## Master
Site ID | Site name | Div | EDM Spill 2020 | EDM Spill 2021 | EDM Spill 2022 | EDM Spill Average | Flow4 check | Flow meter? | Consented flow (l/s) | DWEF (l/s) | Required flow to meeting SCV (l/s) | Max flow measured / estimated (l/s) | % out Of consent or Below SCV | Date of flow measurement | Column2 | Column1 | Out of consent date | Site Spilled This Month? | Ops Compliance Status | Monthly Board Compliance Status | Old Status | Action log/feedback - this is superseded by the Action log tab | Link to pump test | Virtual Drop Test Calculations
14490 | Edington Tinhead (Lower Baynton Road) | N |  |  |  |  | N | N | #N/A |  | #N/A | 45 | #N/A | 4348000% |  |  |  |  | Not currently assessed |  |  |  |  | N
17498 | Huish Episcopi The Hill Detention Tank | W |  |  |  |  | N | Y | #N/A |  | #N/A | 13.9 | #N/A | 4449800% |  |  |  |  | Not currently assessed |  |  |  |  | N
16825 | Clevedon Ladye Bay Sps CSO | W |  |  |  |  | N | N | #N/A |  | #N/A |  | #N/A | [5 empty] | Not currently assessed |  |  |  |  | N
17285 | Cromhall Church Lane SPS | N |  |  |  |  | N | N | #N/A |  | #N/A |  | #N/A | [5 empty] | Not currently assessed |  |  |  |  | N
14142 | Minety Station Road SPS | N |  |  |  |  | N | N | 6.5 |  | 19.0852 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14229 | Wareham West Mill Crescent SPS | S |  |  |  |  | N | N | 16.7 |  | 9.2039 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14235 | Bovington Duncan Crescent SPS | S |  |  |  |  | N | N | 7 |  | 5.8905 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14273 | Wool Railway Cottages SPS | S |  |  |  |  | N | N | 21 |  | 13.2536 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14275 | Corfe Castle Halves Cottages SPS | S |  |  |  |  | N | N | 8 |  | 5.8905 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14368 | Mere Edgebridge SPS | S |  |  |  |  | N | N | 11 |  | 13.2536 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14395 | Hatch Beauchamp . SPS | T |  |  |  |  | N | N | 4 |  | 3.7699 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14405 | West Stafford Dorchester Road SPS | S |  |  |  |  | N | N | 14.1 |  | 5.8905 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14440 | Dilton Marsh Pen Knapp SPS | N |  |  |  |  | N | N | 10 |  | 4.7713 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | Y
14447 | Keevil The Street SPS | N |  |  |  |  | N | N | 37 |  | 17.0235 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14507 | Shirehampton Lamplighters SPS | N |  |  |  |  | N | N | 37 |  | 36.8155 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14581 | Bristol Victoria Road SPS | N |  |  |  |  | N | N | 111 |  | 53.0144 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14624 | Saltford Mead Lane SPS | N |  |  |  |  | N | N | 7 |  | 342.0275 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15043 | Mudeford Mudeford Gardens SPS | S |  |  |  |  | N | N | 90 |  | 29.8206 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15053 | Ferndown Golf Links Road SPS | S |  |  |  |  | N | N | 80 |  | 36.8155 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15091 | Ferndown Aldridge Road SPS | S |  |  |  |  | N | N | 28 |  | 23.5619 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15101 | Patney Patney Weir SPS | N |  |  |  |  | N | N | 2.9 |  | 8.4823 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15139 | Pilning Swanmore Bridge SPS | N |  |  |  |  | N | N | 17 |  | 13.2536 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15166 | Rangeworthy Berrows Mead SPS | N |  |  |  |  | N | N | 8 |  | 13.2536 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15167 | Cromhall Jubilee Lane SPS | N |  |  |  |  | N | N | 12 |  | 5.8905 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15236 | Poole Canford Heath Road SPS | S |  |  |  |  | N | N | 44 |  | 23.5619 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15283 | Wincanton Bayford SPS | W |  |  |  |  | N | N | 5 |  | 3.3134 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  | SAST001251 | 0
15378 | Pawlett Vicarage Lane SPS | W |  |  |  |  | N | N | 3 |  | 5.8905 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  | No Tests | 0
15391 | Westonzoyland Hamrod Lane SPS | W |  |  |  |  | N | N | 5 |  | 5.8905 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15396 | Woolavington Meadow Farm SPS | W |  |  |  |  | N | N | 33 |  | 53.0144 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  | No Tests | 0
15436 | Ruishton Barton Lane SPS | W |  |  |  |  | N | N | 16 |  | 5.8905 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15443 | Taunton New Barn Queensway SPS | W |  |  |  |  | N | N | 21 |  | 13.2536 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15448 | Taunton Longacre Close SPS | W |  |  |  |  | N | N | 7 |  | 3.3134 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15458 | Stoke St Gregory Curload SPS | W |  |  |  |  | N | Y | 2.2 |  | 1.4726 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15460 | Meare Green Stoke St Gregory SPS | W |  |  |  |  | N | Y | 0.4 |  | 3.7699 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15461 | Stoke St Gregory Woodhill SPS | W |  |  |  |  | N | N | 16 |  | 13.2536 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15463 | Bradford On Tone Tone Green SPS | W |  |  |  |  | N | N | 0.5 |  | 3.3134 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  | No Drop Test | 0
15467 | Nailsbourne . SPS | W |  |  |  |  | N | N | 16 |  | 23.5619 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15508 | Wootton Courtenay . SPS | W |  |  |  |  | N | N | 0.7 |  | 3.3134 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15580 | Langford Blackmoor Road SPS | W |  |  |  |  | N | N | 40 |  | 36.8155 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15723 | Tetbury Springfields SPS | N |  |  |  |  | N | N | 4 |  | - | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15792 | Weston-Super-Mare Knightstone Road SPS | W |  |  |  |  | N | N | 443 |  | 36.8155 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
17175 | Puriton Downend Terrace SPS | W |  |  |  |  | N | N | 5 |  | 4.7713 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
19035 | Kingsbury Episcopi . SPS | W |  |  |  |  | N | N | 14 |  | 9.9549 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
19699 | Bovington Lytchett Lane SPS | S |  |  |  |  | N | N | 10 |  | 9.2039 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
19787 | Stour Row . SPS | S |  |  |  |  | N | N | 6 |  | 9.2039 | #N/A | #N/A | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14249 | Bloxworth Fox Pound SPS | S |  |  |  |  | N | Y | #N/A |  | 13.2536 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
14330 | Little Langford SPS | S |  |  |  |  | N | Y | #N/A |  | 13.2536 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
14376 | Moorlinch Right Drove SPS | W |  |  |  |  | N | Y | #N/A |  | 54.7962 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
14408 | Bradford Peverell SPS | S |  |  |  |  | N | Y | #N/A |  | 212.0575 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
14551 | Bradney Bridge SPS | W |  |  |  |  | N | Y | #N/A |  | 132.9041 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
14598 | LOWER WEARE SPS | W |  |  |  |  | N | Y | #N/A |  | 3.7699 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
15064 | Shapwick Stewards Lane SPS | S |  |  |  |  | N | N | #N/A |  | 58.4483 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
15239 | Poole Poole Park SPS | S |  |  |  |  | N | Y | #N/A |  | 13.2536 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
15385 | MERRY BEE SOUTH ROAD SPS | W |  |  |  |  | N | Y | #N/A |  | 46.1814 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
15426 | Newport South SPS | N |  |  |  |  | N | Y | #N/A |  | 7.7902 |  | 100% | [5 empty] | Not currently assessed |  | With Luke S |  |  | N
14095 | Glastonbury Porchestall SPS | W |  |  |  |  | N | Y | 200 |  | 94.2478 | 95.07 | 52.47% | 4552800% |  |  | 4512100% | N | At Risk | At Risk | Monitor |  |  | N
19300 | Stawell Moor Lane SPS | W |  |  |  |  | N | Y | #N/A |  | 5.8905 |  | 100% |  |  |  |  | N | Not currently assessed |  |  |  |  | N
15553 | VICTORIA SQUARE SPS | S |  |  |  |  | 15553 | Y - Treatment | 480 |  | 288.6338 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
15556 | RADIPOLE SPS | S |  |  |  |  | 15556 | Y - Treatment | 2200 |  | 712.7488 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
13373 | Porlock Porlock Weir SPS | W |  |  |  |  | N | N | 7 |  | 5.8905 |  | 100% | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
14197 | Malmesbury Corston SPS | N |  |  |  |  | N | Y | 8 | 7.5 | 7.1275 | 5 | 37.5% | 4551800% |  |  | 4508200% | N | At Risk | At Risk
14040 | Leighterton | N |  |  |  |  | N | N | #N/A |  | 5.3162 |  | 100% | [10 empty] | N
14324 | Wylye Chequers Cottages SPS | S |  |  |  |  | N | N | #N/A |  | 3.3134 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
14435 | Warminster Boreham Road | N |  |  |  |  | N | N | #N/A |  | 23.5619 |  | 100% | [5 empty] | Not currently assessed |  | Virtual drop test? |  |  | Y
14460 | North Bradley Yarnbrook | N |  |  |  |  | N | N | #N/A |  | 19.0852 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
15140 | Tytherington Southlands SPS | N |  |  |  |  | N | N | #N/A |  | 3.7699 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
15141 | Rangeworthy Patch Elm Lane SPS | N |  |  |  |  | N | N | #N/A |  | 3.7699 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
15163 | Cromhall Townwell SPS | N |  |  |  |  | N | N | #N/A |  | 5.8905 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
15473 | Stratton Mill Lane SPS | S |  |  |  |  | N | N | #N/A |  | 5.8905 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
14176 | Kington Langley . SPS | N |  |  |  |  | N | N | 7 |  | 13.2536 |  | 100% | 4448900% |  |  |  |  | Not currently assessed |  | Drop test is out of range for this site. Look at calculations. |  |  | Y
15622 | Clevedon Marine Parade SPS | W |  |  |  |  | N | N | 42 |  | 13.2536 |  | 100% | [5 empty] | Not currently assessed |  | Requires virtual drop test |  |  | Y
17585 | Pymore Thread Mill Lane SPS | S |  |  |  |  | N | Y | #N/A |  | 13.2536 |  | 100%
15683 | [6 empty] | N | Y | #N/A |  | 5.8905 |  | 100%
15810 | Melksham Primrose Drive | N |  |  |  |  | N | Y | 22 |  | 15.0796 |  | 100% | [5 empty] | Not currently assessed |  |  |  |  | N
13389 | Bossington . SPS | W |  |  |  |  | N | N | 13 |  | 13.2536 | 1.85 | 85.77% | 4513300% |  |  |  | N | Not currently assessed |  |  | Review VDT volumes |  | Y
19725 | Kimmeridge SPS | S |  |  |  |  | N | N | #N/A |  | 8.4823 | 1.4 | 83.5% | 4428400% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14157 | Calne Rough Leaze | N |  |  |  |  | N | N | 20 |  | 29.8206 | 3.77 | 81.15% | 4516800% |  |  |  | N | Not currently assessed |  | Under investigation. Flows from VDT are an overestimate meaning the flow is actually less. |  |  | 0
14467 | Holt The Star | N |  |  |  |  | N | Y | 101 |  | 23.5619 | 2134 | -2013% | 4313800% |  |  |  |  | Not currently assessed |  | Under investigation |  |  | 0
15606 | Clevedon The Beach SPS | W |  |  |  |  | N | N | 71 |  | 36.8155 | 20.98 | 70.45% | 4310150% |  |  |  |  | Not currently assessed |  | Requires virtual drop test |  |  | 0
19731 | Harmans Cross Transfer Station SPS | S |  |  |  |  | N | N | 7.5 |  | 9.2039 | 2.6 | 65.33% | 4273650% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14394 | Wellington Mitchells Pool SPS | W |  |  |  |  | N | N | 70 |  | 19.0852 | 32 | 54.29% | 4316850% |  |  |  |  | Not currently assessed |  | Requires virtual drop test |  |  | 0
14221 | Upton Frenchs Farm | S |  |  |  |  | N | N | #N/A |  | 23.5619 | 11 | 53.31% | 4451100% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15541 | Keynsham The Hams SPS | N |  |  |  |  | N | N | 23 |  | 23.5619 | 10.76 | 53.22% | 4346650% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14411 | Sydling St Nicholas . SPS | S |  |  |  |  | N | N | 17 |  | 13.2536 | 9.6 | 43.53% | 4502800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
13033 | Bradford Peverell Giles Cross | S |  |  |  |  | N | N | #N/A |  | 29.8206 | 14.5 | 51.38% | 4409800% |  |  |  |  | Not currently assessed |  |  |  |  | N
15493 | Frampton Muckleford SPS | S |  |  |  |  | N | N | #N/A |  | 5.8905 | 2.9 | 50.77% | 4411600% |  |  |  |  | Not currently assessed |  |  |  |  | N
15389 | Pawlett Main Road SPS | W |  |  |  |  | N | Y | 19.2 |  | 9.2039 | 12.44 | 35.21% | 4554000% |  |  | 4498600% | N | At Risk | At Risk |  |  |  | N
14226 | Church Knowle Glebe Farm SPS | S |  |  |  |  | N | N | 8 |  | 5.8905 | 4.02 | 49.75% | 4516800% |  |  |  | N | Not currently assessed |  | Pump 1 sometimes reaches consent but Pump 2 does not. Monitor |  |  | Y
14263 | Corfe Castle Red Lane SPS | S |  |  |  |  | N | N | 18.3 |  | 13.2536 | 9.47 | 48.25% | 4516800% |  |  |  | N | Not currently assessed |  | Dimensions may be inaccurate |  |  | Y
14266 | Wareham Sandford Lane SPS | S |  |  |  |  | N | Y | 60 | 60 | 23.5619 | 43.94 | 26.77% | 4551800% |  |  | 4509700% | N | At Risk | At Risk |  | Imepllors and wear rings, also not switching duty |  | N
13334 | West Bay SPS | S |  |  |  |  | N | Y-Treatment | 414 |  | 147.2622 | 216.97 | 47.59% | 4489100% |  |  |  |  | Not currently assessed |  |  |  |  | N
15206 | Blandford Langton Road (Blandford No. 1) | S |  |  |  |  | N | N | 89 |  | 72.1585 | 47.2 | 46.97% | 4349100% |  |  |  |  | Not currently assessed |  | Under investigation |  | CCTV122541 | Y
14287 | Hinton St. George SPS | W |  |  |  |  | N | Y | 7 |  | 5.8905 | 4.4 | 37.14% | 4341000% |  |  |  |  | Not currently assessed |  | Under investigation |  | CCTV122552 | Y
15244 | Poole Elgin Road | S |  |  |  |  | 15244 | Y | 650 | 420 | 376.9911 | 541.66 | 16.67% | 4551900% |  |  | 4502700% | N | At Risk | At Risk | Scheme |  |  | N
15235 | SHORE ROAD POOLE | S |  |  |  |  | N | Y | 90 |  | 74.2349 | 75 | 16.67% | 4551800% |  |  | 4495000% | N | At Risk | At Risk | Under investigation. |  |  | N
15402 | Middlezoy Nethermoor Road SPS | W |  |  |  |  | N | Y | 11 |  | 29.8206 | 9.26 | 15.82% | 4554000% |  |  |  | N | At Risk | At Risk |  |  |  | N
14450 | Coulston | N |  |  |  |  | N | N | 3.4 |  | 23.5619 | 2 | 41.18% | [5 empty] | Not currently assessed |  | Under investigation |  |  | Y
14116 | GURNEY SLADE SPS | W |  |  |  |  | N | Y | 7 |  | 5.8905 | 5.96 | 14.86% | 4552800% |  |  | 4498700% | N | At Risk | At Risk |  |  |  | 0
14126 | Shroton . SPS | S |  |  |  |  | N | N | 9.6 |  | 5.8905 | 5.86 | 38.96% | 4516800% |  |  |  | N | Not currently assessed |  |  |  |  | Y
14392 | WEST BUCKLAND SPS | W |  |  |  |  | N | N | 10 |  | 5.8905 | 6.2 | 38% | 4341600% |  |  |  |  | Not currently assessed |  | Under investigation |  | CCTV122549 | Y
14386 | Greinton Moor Drive SPS | W |  |  |  |  | N | Y | 34 |  | 29.8 | 28.95 | 14.85% | 4554000% |  |  | 4494200% | N | At Risk | At Risk | Monitor |  |  | N
14439 | Warminster Calveswater | N |  |  |  |  | N | N | 95 |  | 74.2349 | 60 | 36.84% | 4316650% |  |  |  |  | Not currently assessed |  | Scheme |  |  | Y
14302 | Idmiston | S |  |  |  |  | N | N | 14.5 |  | 36.8155 | 9.2 | 36.55% | 4313600% |  |  |  |  | Not currently assessed |  | Under investigation |  | CCTV121660 | Y
14127 | Gillingham Brickyard Lane SPS | S |  |  |  |  | N | N | 65 |  | 18.0396 | 42 | 35.38% | 4276750% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14320 | Stapleford Pelican Inn SPS | S |  |  |  |  | N | Y | #N/A |  | 9.2039 | 5.98 | 35.03% | 4495600% |  |  |  | Y | Not currently assessed |  |  |  |  | N
15370 | Westonzoyland Lakewall Road SPS | W |  |  |  |  | N | N | 9 |  | 5.8905 | 3.7 | 58.89% | 4536100% |  |  |  |  | Not currently assessed |  | Requires virtual drop test |  |  | N
15052 | Verwood Ebblake SPS | S |  |  |  |  | N | N | 5 |  | 3.7699 | 3.3 | 34% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14304 | Allington Old Inn SPS | S |  |  |  |  | N | N | 6.8 |  | 3.3134 | 4.55 | 33.09% | 4516800% |  |  |  | N | Not currently assessed |  | Under investigation |  | CCTV123657 | Y
14075 | Glastonbury North Load Bridge SPS | W |  |  |  |  | N | N | 3 |  | 5.8905 | 2.02 | 32.67% | 4453500% |  |  |  | N | Not currently assessed |  | Flowmeter not recording during high level |  |  | 0
14317 | Hurdcott . SPS | S |  |  |  |  | N | N | 60 |  | 36.8155 | 40.63 | 32.28% | 4516800% |  |  |  | N | Not currently assessed |  | Under investigation |  |  | Y
15381 | Wembdon Common SPS | W |  |  |  |  | N | N | 52 |  | 29.8206 | 36.8 | 29.23% | 4516800% |  |  |  | N | Not currently assessed |  | Dimensions from John Harper |  |  | Y
15569 | Portbury Drove SPS | W |  |  |  |  | N | N | 92.3 |  | 94.2478 | 66.2 | 28.28% | 4364750% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15447 | Taunton Mountway Bishops Hull SPS | W |  |  |  |  | N | N | 120 |  | 13.2536 | 88.22 | 26.48% | 4118450% |  |  |  |  | Not currently assessed |  | Requires on site pump test (no historic drop test) |  |  | 0
14114 | Glastonbury Edgarley Millfield School SPS | W |  |  |  |  | N | Y | 8 |  | 5.8905 | 7.01 | 12.38% | 4553900% |  |  | 4501400% | N | At Risk | At Risk |  |  |  | Y
14107 | Witham Friary . SPS | W |  |  |  |  | N | N | 5 |  | 3.3134 | 3.7 | 26% | 4344950% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14333 | East Knoyle Shaftesbury Road SPS | S |  |  |  |  | N | Y | #N/A |  | 3.3134 | 2.5 | 24.55% | 4493500% |  |  |  |  | Not currently assessed |  | Flowmeter broken - raise IT ticket |  |  | N
14340 | Fovant Church Lane | S |  |  |  |  | N | N | #N/A |  | 15.0796 | 11.5 | 23.74% | 4471700% |  |  |  |  | Not currently assessed |  |  |  |  | N
15686 | Compton Dundon Ham Lane | W |  |  |  |  | N | Y | #N/A |  | 5.8905 | 4.91 | 16.65% | 4495100% |  |  |  | N | Not currently assessed |  | Monitor. Can only reach consent with Pump 2 running |  |  | N
15125 | Worton Mill Road | N |  |  |  |  | N | N | 11 |  | 8.4823 | 8.4 | 23.64% | 4317500% |  |  |  |  | Not currently assessed |  | Under investigation |  |  | 0
15469 | Leigh Frampton Farm SPS | S |  |  |  |  | N | N | 14 |  | 9.2039 | 10.9 | 22.14% | 4340250% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14147 | Chippenham Westmead SPS | N |  |  |  |  | N | Y | 155 | 50 | 53.0144 | 136.4 | 12% | 4551800% |  |  | 4543400% | N | At Risk | At Risk |  |  |  | 0
14200 | Lea Lea North SPS | N |  |  |  |  | N | N | 11.2 |  | 5.8905 | 8.95 | 20.09% | 4516800% |  |  |  | Y | Not currently assessed |  |  |  |  | Y
14085 | Coxley Coxley Ripple SPS | W |  |  |  |  | N | N | 6 |  | 4.7713 | 4.8 | 20% | 4369350% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15465 | North Curry Stoke Road SPS | W |  |  |  |  | N | N | 9 |  | 9.2039 | 7.21 | 19.89% | 4516800% |  |  |  | N | Not currently assessed |  | Observed decrease in flows on 15/05/2022. Start and stop levels were not changed. |  |  | Y
15388 | Othery Rye Lane/ Summerhedge Road SPS | W |  |  |  |  | N | Y | 13.5 |  | 29.8206 | 12.14 | 10.07% | 4554000% |  |  |  | N | At Risk | At Risk |  |  |  | N
14428 | Corston Newton St. Loe | N |  |  |  |  | N | N | 23.5 |  | 5.8905 | 18.9 | 19.57% | 4364900% |  |  |  |  | Not currently assessed |  | Under investigation |  |  | 0
15400 | Bridgwater West Quay SPS | W |  |  |  |  | 15400 | Y | 206 |  | 94.2478 | 189.48 | 8.019% | 4544000% |  |  | 4469500% | N | At Risk | At Risk |  |  |  | N
15082 | Wimborne Brook Road No 1 SPS | S |  |  |  |  | N | N | 130 |  | 72.1585 | 107.45 | 17.35% | 4361350% |  |  | 4467500% |  | Not currently assessed |  |  |  |  | Y
15440 | North Curry Main SPS | W |  |  |  |  | N | N | 8.3 |  | 3.7699 | 6.9 | 16.87% | 4355750% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14430 | Chew Magna Dumpers Lane | N |  |  |  |  | N | Y | 94 | 75 | 74.2349 | 87.73 | 6.67% | 4551900% |  |  |  |  | At Risk | At Risk |  |  |  | 0
14420 | Minehead Quay West | W |  |  |  |  | 14420 | Y | 14 | 13.5 | 13.2536 | 13.12 | 6.286% | 4548100% |  |  |  | N | At Risk | At Risk | Pumps would produce PFF in high level but the site never goes high |  |  | N
15673 | Portland Southwell SPS | S |  |  |  |  | N | N | 160 |  | 94.2478 | 135 | 15.62% | 4322150% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14431 | Bishop Sutton . SPS | N |  |  |  |  | N | Y | 19.6 | 15.5 | 13.2536 | 19 | 3.061% | 4551900% |  |  |  | N | At Risk | At Risk | Monitor |  |  | N
15314 | Upton near Langport | W |  |  |  |  | N | Y | 5 |  | 19.0852 | 4.91 | 1.8% | 4554000% |  |  |  | N | At Risk | At Risk |  |  | CCTV122551 | N
15715 | Bridgwater Horsey Bath Road SPS | W |  |  |  |  | N | Y | 54 |  | 5.8905 | 53.22 | 1.444% | 4548100% |  |  |  | N | At Risk | At Risk |  |  |  | N
15542 | Keynsham Keynsham High Level SPS | N |  |  |  |  | N | N | 112 |  | 60.3186 | 95.02 | 15.16% | 4516800% |  |  |  | Y | Not currently assessed |  |  |  |  | Y
15536 | Wellow Mill Hill SPS | N |  |  |  |  | N | N | 5 |  | 5.8905 | 4.25 | 15% | 4516800% |  |  |  | N | Not currently assessed |  | Start/stop levels were changed and I calculated new ones. Still the flow under consent |  |  | Y
14466 | Semington Brook | N |  |  |  |  | N | N | 18 |  | 19.0852 | 15.3 | 15% | 4399300% |  |  |  |  | Not currently assessed |  | Under investigation |  |  | Y
15237 | POOLE MAGNA ROAD SPS | S |  |  |  |  | N | N | 100 | 80 | 147.2622 | 100 | 0% | 4516800% |  |  |  | N | Not currently assessed |  | Under investigation. Flowmeter out of range |  |  | 0
15494 | Abbotsbury Church Street SPS | S |  |  |  |  | N | N | 9.3 |  | 5.8905 | 8 | 13.98% | 4342350% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15304 | West Chinnock Garage SPS | W |  |  |  |  | N | Y | 8.8 | 8.8 | 13.2536 | 8.75 | 0.5682% | 4552800% |  |  |  | N | At Risk | At Risk |  |  |  | 0
15088 | Alderholt Sandleheath Road | S |  |  |  |  | N | N | #N/A |  | 24.7548 | 21.7 | 12.34% | 4451100% |  |  |  |  | Not currently assessed |  | Requires virtual drop test |  |  | N
15158 | OLVESTON THE COMMON SPS | N |  |  |  |  | N | Y | 21 |  | 13.2536 | 21 | 0% | 4551800% |  |  | 4534400% | N | DWEF Compliant | Compliant |  |  |  | N
10312 | Iron Acton Hoovers Lane SPS | N |  |  |  |  | N | Y | 400 |  | 19.0852 | 400 | 0% | 4551300% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | N
14265 | Upton Moorlands Way | S |  |  |  |  | N | Y | 45 | 43 | 58.4483 | 45 | 0% | 4551800% |  |  |  | N | At Risk | At Risk | Monitor |  |  | N
14020 | Lower Stanton Drew . SPS | N |  |  |  |  | N | N | 2.3 |  | 5.8905 | 2.06 | 10.43% | 4516800% |  |  |  | N | Not currently assessed |  | Pump 1 - 1.97, Pump 2.30 |  |  | Y
15233 | Poole Wilderton Road | S |  |  |  |  | N | Y | 350 | 270 | 212.0575 | 350 | 0% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
14328 | Hanging Langford . SPS | S |  |  |  |  | N | Y | 12 |  | 9.2039 | 12 | 0% | 4549000% |  |  | 4495500% | N | DWEF Compliant | Compliant | Monitor |  |  | N
14414 | Charminster North Street SPS | S |  |  |  |  | N | Y | 45 |  | 36.8155 | 45 | 0% | 4548600% |  |  | 4466200% | N | DWEF Compliant | Compliant |  | 0 |  | N
14323 | AMESBURY FLOWER LANE SPS | S |  |  |  |  | N | Y | 120 |  | 53.0144 | 120 | 0% | 4534200% |  |  |  |  | Not currently assessed |  | New flowmeter is being fitted. |  |  | 0
13153 | Holton Heath Holton Heath SPS SPS | S |  |  |  |  | N | Y | 20 | 17.5 | 29.8206 | 20 | 0% | 4543400% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | 0
14222 | East Knighton Blacknoll SPS | S |  |  |  |  | N | Y | 11 |  | 15.0796 | 11 | 0% | 4516800% |  |  |  | Y | Not currently assessed |  |  |  |  | Y
19817 | Sandford Orcas . SPS | S |  |  |  |  | N | N | 6 |  | 5.8905 | 5.4 | 10% | 4448900% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14326 | Stoford SPS | S |  |  |  |  | N | N | #N/A |  | 9.2039 | 8.3 | 9.821% | 4413900% |  |  |  |  | Not currently assessed |  |  |  |  | N
15772 | Peasedown St John Wellow Lane SPS | N |  |  |  |  | N | N | 70 |  | 36.8155 | 63.4 | 9.429% | 4451100% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15481 | Bradpole Lee Lane SPS | S |  |  |  |  | N | N | 33 |  | 23.5619 | 30 | 9.091% | 4316750% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S |  |  |  |  | N | Y | 370 |  | 147.2622 | 370 | 0% | 4549300% |  |  | 4498700% | N | DWEF Compliant | Compliant |  |  |  | N
15333 | Penselwood Penn Mill SPS | S |  |  |  |  | N | N | 14 |  | 5.8905 | 12.78 | 8.714% | 4516800% |  |  |  | N | Not currently assessed |  |  |  |  | Y
14397 | Beer Hackett SPS | S |  |  |  |  | N | Y | 29 |  | 23.5619 | 29 | 0% | 4548200% |  |  |  | N | DWEF Compliant | Compliant |  |  | CCTV122552 | Y
14185 | MALMESBURY ST JOHNS | N |  |  |  |  | N | Y | 60 | 60 | 42.9416 | 60 | 0% | 4551900% |  |  |  | N | DWEF Compliant | Compliant | Out of consent |  |  | N
15047 | Ferndown Redwood Drive SPS | S |  |  |  |  | N | N | 6.5 |  | 5.8905 | 6 | 7.692% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S |  |  |  |  | 15273 | Y | 345 |  | 212.0575 | 345 | 0% | 4548900% |  |  | 4469600% | N | Compliant | Compliant |  |  |  | N
14125 | Gillingham Buckingham Road SPS | S |  |  |  |  | N | N | 149 |  | 36.8155 | 138 | 7.383% | 4276750% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15383 | Poole East Quay Perry Gardens | S |  |  |  |  | 15383 | Y | 202 | 125 | 212 | 202 | 0% | 4549400% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | N
15278 | BENNETTS ORCHARD SPS | W |  |  |  |  | N | Y | 7.8 |  | 19.0852 | 7.81 | -0.1282% | 4552800% |  |  |  | N | Compliant | Compliant |  |  |  | N
14082 | Street Main SPS | W |  |  |  |  | N | Y | 190 |  | 119.2823 | 191.01 | -0.5316% | 4552800% |  |  |  | N | Compliant | Compliant |  |  |  | N
14084 | Glastonbury Actis SPS | W |  |  |  |  | N | N | 21.9 |  | 13.2536 | 20.4 | 6.849% | 4359550% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15311 | Yeovil Mudford SPS | W |  |  |  |  | N | Y | 9.3 |  | 13.2536 | 9.37 | -0.7527% | 4552800% |  |  | 4500900% | N | Compliant | Compliant |  |  |  | N
15393 | Bridgwater Taunton Road | W |  |  |  |  | 15393 | Y | 70 | 60 | 58.4483 | 60.5 | -0.8333% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
15060 | West Moors Pennington Copse | S |  |  |  |  | N | N | 50 |  | 23.5619 | 46.9 | 6.2% | 4287700% |  |  |  |  | Not currently assessed |  |  |  | \\wxfpsnasoc01\SAST\Sewer Surveys HQ CCTV\CCTV120668\CCTV120668\CCTV120668\Ferndown, Bournemouth SPS Survey_26 05 2017\Pennington Copse SPS | Y
15078 | Ferndown A31 Tricketts Cross SPS | S |  |  |  |  | N | Y | 218 |  | 212.0575 | 220 | -0.9174% | 4549100% |  |  |  | N | Compliant | Compliant |  |  |  | N
14384 | Bridgwater, Chilton St SPS | W |  |  |  |  | 14384 | Y | 242 | 135 | 147.2622 | 244.7 | -1.116% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
15446 | Hillcommon Hill Common SPS | W |  |  |  |  | N | N | 8.6 |  | 5.8905 | 8.15 | 5.233% | 4516800% |  |  |  | N | Not currently assessed |  |  |  |  | Y
14047 | Coate Spaniel's Bridge | N |  |  |  |  | N | N | 7.4 |  | 5.8905 | 7.06 | 4.595% | 4516800% |  |  |  | Y | Not currently assessed |  | Under investigation |  |  | Y
14270 | Bovington Terminal SPS | S |  |  |  |  | N | N | 55 |  | 58.4483 | 52.49 | 4.564% | 4516800% |  |  |  | N | Not currently assessed |  | Dimensions may be inaccurate |  |  | Y
14501 | Bristol Whitby Road St Annes SPS | N |  |  |  |  | N | N | 92.1 |  | 94.2478 | 88 | 4.452% | 4316650% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14174 | Box Mill Lane SPS | N |  |  |  |  | N | N | 27.3 |  | 17.0235 | 24.27 | 11.1% | 4529100% |  |  | 4505400% | Y | Out of Consent | Out of Consent |  |  |  | 0
14046 | Pewsey Swan SPS | N |  |  |  |  | N | N | 53 |  | 17.0235 | 51 | 3.774% | 4287750% |  |  |  |  | Not currently assessed |  | Under investigation |  |  | Y
14550 | Lacock Nethercote Hill SPS | N |  |  |  |  | N | N | 13.5 |  | 13.2536 | 13 | 3.704% | 4342750% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14139 | Christian Malford Swalletts Gate SPS | N |  |  |  |  | N | N | 10 |  | 5.8905 | 9.7 | 3% | 4342350% |  |  |  |  | Not currently assessed |  |  |  |  | Y
13337 | West Lulworth Hambury Farm SPS | S |  |  |  |  | N | N | 15.9 |  | 29.8206 | 15.53 | 2.327% | 4516800% |  |  |  | Y | Not currently assessed |  | Virtual drop test? |  |  | Y
14380 | North Newton Church Road SPS | W |  |  |  |  | N | N | 13.2 |  | 19.0852 | 13 | 1.515% | 4212050% |  |  |  |  | Not currently assessed |  | Under investigation |  |  | Y
14621 | PORTISHEAD TOWN HARBOUR | W |  |  |  |  | N | Y | 260 |  | 331.3399 | 263 | -1.154% | 4548000% |  |  |  | N | Compliant | Compliant |  |  |  | N
15327 | Ilminster Lord Nelson SPS | W |  |  |  |  | N | N | 20 |  | 13.2536 | 19.8 | 1% | 4364550% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14391 | Stoke St Gregory No 1 Lane End | W |  |  |  |  | N | Y | 27 | 12.6 | 5.8905 | 27.35 | -1.296% | 4552800% |  |  |  | N | Compliant | Compliant | Separate flow meters on storm and foul rising mains - PFF should be both flow meters summed. Not gone into HL recently. No evidence that we weren't doing PFF |  | CCTV122550 | Y
15519 | WATCHET MARKET STREET TUNNEL | W |  |  |  |  | N | Y-Treatment | 120 |  | 53.0144 | 119.21 | 0.6583% | 4488200% |  |  |  | Y | Not currently assessed |  |  |  |  | N
15207 | SHAFTESBURY LONG CROSS SPS | S |  |  |  |  | N | Y | 15 |  | 9.2039 | 15.2 | -1.333% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | 0
14016 | BRISTOL ASHTON AVENUE SPS | N |  |  |  |  | N | Y | 2050 | 510 | 2697.6071 | 2082.15 | -1.568% | 4551900% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | N
15415 | Bridgwater, Colley Lane SPS | W |  |  |  |  | 15415 | Y | 123 | 86 | 212.0575 | 125.41 | -1.959% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
14055 | Marden High Street SPS | N |  |  |  |  | N | Y | 8 |  | 8.4823 | 8 | 0% | 4000150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14151 | Dauntsey The Green SPS | N |  |  |  |  | N | N | 5.6 |  | 3.7699 | 5.6 | 0% | 3945550% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14462 | Broughton Gifford Curtis Orchard SPS | N |  |  |  |  | N | N | 3 |  | 5.8905 | 3 | 0% | 4360850% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14468 | Melksham Semington Road SPS | N |  |  |  |  | N | N | 7 |  | 9.2039 | 7 | 0% | 4360850% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14502 | Bristol Whitby Road B Co-Op Depot Arnos Vale SPS | N |  |  |  |  | N | N | 30 |  | 23.5619 | 30 | 0% | 4023950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14580 | Bristol Ullswater Close SPS | N |  |  |  |  | N | N | 12 |  | 13.2536 | 12 | 0% | 3925850% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14620 | Pewsey Salisbury Road SPS | N |  |  |  |  | N | N | 11.3 |  | 13.2536 | 11.3 | 0% | 4215650% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14375 | Pedwell . SPS | W |  |  |  |  | N | N | 16 |  | 23.5619 | 16 | 0% | 4063350% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15048 | Verwood Acacia Avenue SPS | S |  |  |  |  | N | N | 8 |  | 3.3134 | 8 | 0% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15201 | Durweston Water Lane SPS | S |  |  |  |  | N | N | 7 |  | 5.8905 | 7 | 0% | 3925850% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15203 | Shillingstone Haywards Bridge SPS | S |  |  |  |  | N | N | 8.5 |  | 23.5619 | 8.5 | 0% | 3929450% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15205 | Blandford St Mary Bournemouth Road SPS | S |  |  |  |  | N | N | 12 |  | 5.8905 | 12 | 0% | 4348950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15230 | Poole Kennart Road SPS | S |  |  |  |  | N | N | 12 |  | 5.8905 | 12 | 0% | 4061850% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15231 | Poole Sandbanks Pavilion SPS | S |  |  |  |  | N | N | 18 |  | 46.1814 | 18 | 0% | 4289150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14632 | Taunton Maidenbrook SPS | W |  |  |  |  | N | N | 82.1 |  | 53.0144 | 82.1 | 0% | 4215650% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15486 | West Bexington . SPS | S |  |  |  |  | N | N | 1.5 |  | 1.4726 | 1.5 | 0% | 4215350% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15559 | Portland Pennsylvania Road SPS | S |  |  |  |  | N | N | 5 |  | 5.8905 | 5 | 0% | 4322150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15331 | Shepton Beauchamp . SPS | W |  |  |  |  | N | N | 12 |  | 13.2536 | 12 | 0% | 4314350% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15316 | Barton St David Tootal Bridge SPS | W |  |  |  |  | N | Y | 2.4 |  | 7.1275 | 2.45 | -2.083% | 4552800% |  |  |  | N | Compliant | Compliant |  |  |  | N
15002 | Boscombe No 1 SPS | S |  |  |  |  | N | Y | 45 |  | 23.5619 | 46 | -2.222% | 4548900% |  |  |  | N | Compliant | Compliant |  |  |  | N
15257 | Poole Bridge Poole Quay | S |  |  |  |  | 15257 | Y | 15 |  | 13.2536 | 15.4 | -2.667% | 4548900% |  |  | 4507200% | N | Compliant | Compliant | Monitor |  |  | N
14220 | LYT MATVRS BULBURY LANE SPS | S |  |  |  |  | N | Y | 26 |  | 23.5619 | 26.86 | -3.308% | 4549300% |  |  |  | N | Compliant | Compliant |  |  |  | N
14259 | Wareham South East SPS | S |  |  |  |  | N | Y | 54 |  | 82.835 | 56 | -3.704% | 4549300% |  |  |  | N | Compliant | Compliant |  |  |  | N
15246 | CANFORD MAIN SPS | S |  |  |  |  | N | Y | 80 | 59 | 23.5619 | 83 | -3.75% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
14092 | Glastonbury Wells Road SPS | W |  |  |  |  | N | N | 12.8 |  | 19.0852 | 12.9 | -0.7812% | 4364250% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14374 | Highbridge Newton SPS | W |  |  |  |  | 14374 | Y - Treatment | 300 |  | - | 298.37 | 0.5433% | 4494200% |  |  | 4494200% | N | At Risk | At Risk |  |  |  | N
15459 | Rumwell . SPS | W |  |  |  |  | N | N | 6.93 |  | 5.8905 | 7 | -1.01% | 4118450% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14113 | TRUDOXHILL SPS | W |  |  |  |  | N | Y | 6 |  | 9.2039 | 6.23 | -3.833% | 4552800% |  |  |  | N | Compliant | Compliant |  |  |  | N
15190 | Milborne St Andrew Manor Farm SPS | S |  |  |  |  | N | Y | 47 |  | 23.5619 | 49 | -4.255% | 4548200% |  |  |  | N | Compliant | Compliant |  |  |  | N
14301 | Stalbridge . SPS | S |  |  |  |  | N | N | 61 |  | 36.8155 | 61.84 | -1.377% | 4172950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14145 | Malmesbury Tanners Bridge | N |  |  |  |  | N | Y | 18 | 17 | 8.4823 | 19.05 | -5.833% | 4551900% |  |  | 4534600% | N | DWEF Compliant | Compliant |  |  |  | Y
15317 | NORTON SUB HAMDON SPS | W |  |  |  |  | N | Y | 15.4 |  | 13.2536 | 16.17 | -5% | 4554000% |  |  | 4509700% | Y | At Risk | Compliant |  |  |  | N
15511 | Monksilver B3188 SPS | W |  |  |  |  | N | Y | 2.5 |  | 2.7238 | 2.91 | -16.4% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
15457 | Wellington Westford SPS | W |  |  |  |  | N | N | 13.8 |  | 5.8905 | 14 | -1.449% | 4311950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14372 | West Huntspill Sloway Lane | W |  |  |  |  | 14372 | Y | 130 | 76 | 132.9041 | 138.96 | -6.892% | 4548200% |  |  | 4512100% | N | Compliant | Compliant |  |  |  | N
13273 | Shipton Gorge Off Markets Lane SPS | S |  |  |  |  | N | Y | 6.3 |  | 7.1275 | 6.75 | -7.143% | 4546800% |  |  | 4509700% | N | Compliant | Compliant |  |  |  | 0
14415 | LITTON CHENEY CHICKSBRIDGE SPS | S |  |  |  |  | N | Y | 5.3 |  | 4.7713 | 5.68 | -7.17% | 4548100% |  |  |  | N | Compliant | Compliant |  |  |  | N
14102 | Kilmersdon . SPS | W |  |  |  |  | N | Y | 5 |  | 9.2039 | 5.2 | -4% | #N/A |  |  |  |  | Not currently assessed |  |  |  |  | 0
15090 | West Parley Church Lane | S |  |  |  |  | N | Y | 118 |  | 72.1585 | 126.54 | -7.237% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | Y
14097 | Baltonsborough Baltonsborough Main SPS | W |  |  |  |  | N | Y | 17 |  | 19.0852 | 18.31 | -7.706% | 4554100% |  |  |  | N | Compliant | Compliant |  |  |  | Y
15630 | Chickerell Lower Way | S |  |  |  |  | N | N | 15.5 |  | 13.2536 | 15.8 | -1.935% | 4407500% |  |  |  |  | Not currently assessed |  | Under investigation |  |  | 0
14346 | Hindon The Dene SPS | S |  |  |  |  | N | Y | 13 |  | 5.8905 | 14 | -7.692% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
15535 | Peasedown St John New Buildings / Whitebrook Lane SPS | N |  |  |  |  | N | N | 3.9 |  | 3.3134 | 4 | -2.564% | 4120750% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15243 | Bridgwater, East Quay SPS | W |  |  |  |  | 15243 | Y | 179 |  | 184.7256 | 193.28 | -7.978% | 4548200% |  |  |  | N | Compliant | Compliant |  |  |  | N
14291 | West Camel . SPS | W |  |  |  |  | N | Y | 3.5 |  | 3.3134 | 3.7 | -5.714% | 4534200% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14074 | Shepton Mallet Fosse Lane Charlton SPS | W |  |  |  |  | N | N | 16.5 |  | 8.4823 | 17 | -3.03% | 4167550% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15334 | CHARLTON ADAM | W |  |  |  |  | N | Y | 21 |  | 13.2536 | 22.69 | -8.048% | 4554000% |  |  |  | N | Compliant | Compliant |  |  | CCTV122871 | N
15290 | Henstridge Marsh Lane (Henstridge No 2) SPS | W |  |  |  |  | N | Y | 23 |  | 13.2536 | 24.51 | -6.565% | 4516800% |  |  |  |  | Not currently assessed |  | Requires virtual drop test |  |  | Y
15277 | Poole Wood Lane SPS | S |  |  |  |  | N | N | 14.5 |  | 13.2536 | 15 | -3.448% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15007 | Bournemouth Iford Lane Tuckton | S |  |  |  |  | 15007 | Y | 65 |  | 94.2478 | 70.62 | -8.646% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
14260 | Lytchett Matravers Glebe Road SPS | S |  |  |  |  | N | N | 7 |  | 15.0796 | 7.3 | -4.286% | 4411800% |  |  |  |  | Not currently assessed |  | Raised a job regarding data not coming in |  |  | Y
14243 | Morden Cock And Bottle SPS | S |  |  |  |  | N | N | 13.7 |  | 13.2536 | 14.3 | -4.38% | 4451600% |  |  |  |  | Not currently assessed |  | No Pump RS coming through |  |  | Y
13014 | AXBRIDGE OLD | W |  |  |  |  | N | Y | 53.5 |  | 36.8155 | 58.19 | -8.766% | 4547900% |  |  |  | N | Compliant | Compliant |  |  | CCTV122945 | Y
15129 | Potterne Wick SPS | N |  |  |  |  | N | N | 6.4 |  | 9.2039 | 6.7 | -4.687% | 4320950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14385 | Bridgwater, Bristol Road SPS | W |  |  |  |  | 14385 | Y | 160 |  | 132.9041 | 175.34 | -9.588% | 4548200% |  |  |  | N | Compliant | Compliant |  |  |  | N
14648 | CHILTON POLDEN MAIN SPS | W |  |  |  |  | N | Y | 36 |  | 29.8206 | 39.59 | -9.972% | 4552700% |  |  |  | N | Compliant | Compliant |  |  |  | N
15544 | Temple Cloud Temple Bridge SPS | N |  |  |  |  | N | Y | 32 | 32 | 13.2536 | 35.35 | -10.47% | 4551800% |  |  | 4534400% | N | DWEF Compliant | Compliant |  |  |  | Y
15680 | Portishead Black Nore (Nautical School) SPS | W |  |  |  |  | N | Y | 26 |  | 29.8206 | 27 | -3.846% | 4556900% |  |  |  |  | DWEF Compliant | Compliant |  |  |  | 0
15527 | Dunkerton Brooklands SPS | N |  |  |  |  | N | N | 3.8 |  | 5.8905 | 4 | -5.263% | 4120750% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15309 | Charlton Mackerell Rookery Farm | W |  |  |  |  | N | Y | 26 |  | 36.8155 | 28.04 | -7.846% | 4554000% |  |  |  | Y | Compliant | Compliant
15299 | Kingsdon . SPS | W |  |  |  |  | N | Y | 4.4 |  | 8.4823 | 4.8 | -9.091% | 4338350% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15645 | PILL AVON ROAD SPS | W |  |  |  |  | N | Y | 80 |  | 53.0144 | 89.05 | -11.31% | 4554100% |  |  |  | N | Compliant | Compliant |  |  |  | N
14457 | Bulkington Wickleaze SPS | N |  |  |  |  | N | N | 3.3 |  | 23.5619 | 3.5 | -6.061% | 4356550% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15063 | Sturminster Marshall Newton Road SPS | S |  |  |  |  | N | Y | #N/A |  | 42.7 | 45.3 | -6.089% | 4450200% |  |  |  | N | Not currently assessed |  |  |  |  | N
15117 | Devizes Dunkirk Hill | N |  |  |  |  | N | N | 14.6 |  | 19.0852 | 15.5 | -6.164% | 4410500% |  |  |  |  | Not currently assessed |  | Under investigation |  |  | 0
14112 | WANSTROW SPS | W |  |  |  |  | N | Y | 7 |  | 15.0796 | 10.38 | -48.29% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14120 | Street Middle Brooks Road SPS | W |  |  |  |  | N | N | 6 |  | 5.8905 | 6.4 | -6.667% | 4369150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14528 | CARLINGCOTT STONEAGE SPS | N |  |  |  |  | N | Y | 50 | 25.5 | 36.8155 | 55.88 | -11.76% | 4551900% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | N
14426 | Paulton Goosard Bridge SPS | N |  |  |  |  | N | Y | 50 | 42 | 29.8206 | 55.98 | -11.96% | 4551900% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | N
15282 | Bradford Abbas Mill Lane SPS | S |  |  |  |  | N | N | 14.3 |  | 17.0235 | 15.3 | -6.993% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15339 | Templecombe Slades Hill SPS | W |  |  |  |  | N | N | 5.7 |  | 5.8905 | 6.1 | -7.018% | 4345350% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14342 | Teffont Evias | S |  |  |  |  | N | Y | #N/A |  | 7 | 7.5 | -7.143% | 4495300% |  |  |  | Y? | Not currently assessed |  | Under investigation. Is the consent 9 l/s? Not gone into high level recently |  |  | N
14196 | Malmesbury Noahs Ark SPS | N |  |  |  |  | N | Y | 39 | 39 | 53.0144 | 43.96 | -12.72% | 4551900% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | 0
14152 | Calne Broads Green | N |  |  |  |  | N | N | 7.6 |  | 9.2039 | 8.18 | -7.632% | 4516800% |  |  |  | Y | Not currently assessed |  | Under investigation |  |  | Y
14583 | Bristol West Town Road SPS | N |  |  |  |  | N | N | 40 |  | 17.0235 | 43.17 | -7.925% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14244 | Swanage Durlston Road SPS | S |  |  |  |  | N | N | 11 |  | 9.2039 | 11.9 | -8.182% | 4273650% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14294 | Donyatt . SPS | W |  |  |  |  | N | N | 6 |  | 13.2536 | 6.5 | -8.333% | 4448900% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15111 | All Cannings . SPS | N |  |  |  |  | N | Y | 8.5 | 8.5 | 5.8905 | 9.61 | -13.06% | 4551900% |  |  | 4534400% | N | DWEF Compliant | Compliant |  |  |  | 0
14232 | Church Knowle Animal Sanctuary SPS | S |  |  |  |  | N | N | 7 |  | 3.7699 | 7.6 | -8.571% | 4516800% |  |  |  |  | Not currently assessed |  | Pump 1 = 4.5, Pump 2 = 5.17 |  |  | Y
14404 | Beaminster Southgate SPS | S |  |  |  |  | N | Y | 31 |  | 58.4483 | 35.07 | -13.13% | 4548100% |  |  | 4509700% | Y | Compliant | Compliant |  |  |  | N
15516 | Bilbrook . SPS | W |  |  |  |  | N | Y | 4 |  | 8.4823 | 4.51 | -12.75% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14495 | Clevedon Main | W |  |  |  |  | 14495 | Y | 335 | 150 | 296.9394 | 381.53 | -13.89% | 4548200% |  |  |  | N | Compliant | Compliant |  |  |  | N
15079 | Wimborne Poole Road SPS | S |  |  |  |  | N | N | 55 |  | 53.0144 | 60 | -9.091% | 4328550% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15648 | Portland Portland Bill SPS | S |  |  |  |  | N | N | 5.5 |  | 3.7699 | 6 | -9.091% | 4448900% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14272 | Briantspuddle . SPS | S |  |  |  |  | N | N | 6 |  | 9.2039 | 6.55 | -9.167% | 4516800% |  |  |  |  | Not currently assessed |  | P1 to be stripped down |  |  | Y
14371 | FROGLAND CHEDDAR | W |  |  |  |  | N | Y | 48 |  | 36.8155 | 54.92 | -14.42% | 4554100% |  |  |  | N | Compliant | Compliant |  |  | CCTV121655 | N
13074 | COMBWICH QUAY ROAD SPS | W |  |  |  |  | N | Y | 4.9 |  | 9.2039 | 6.2 | -26.53% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | 0
15435 | Bathpool Hyde Lane SPS | W |  |  |  |  | N | Y | 51 |  | 29.8206 | 65.51 | -28.45% | 4554000% |  |  |  | N | Compliant | Compliant | Requires virtual drop test |  |  | Y
14216 | Stoborough Kings Arms | S |  |  |  |  | 14216 | Y | 15.3 | 14.7 | 13.2536 | 18.08 | -18.17% | 4549200% |  |  |  | N | Compliant | Compliant |  |  |  | N
15627 | Ilton Frost Lane SPS | W |  |  |  |  | N | N | 5.6 |  | 8.4823 | 6.2 | -10.71% | 4340450% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14285 | MISTERTON | W |  |  |  |  | N | N | 19.8 |  | 13.2536 | 22 | -11.11% | 4401800% |  |  |  |  | Not currently assessed |  | Under investigation |  | CCTV121646 | 0
15322 | Pitney . SPS | W |  |  |  |  | N | Y | 5.3 |  | 13.2536 | 6.27 | -18.3% | 4548200% |  |  | 4505800% | N | Compliant | Compliant |  |  |  | N
14202 | Hankerton Bridge SPS | N |  |  |  |  | N | Y | 42 | 42 | 23.5619 | 50 | -19.05% | 4551900% |  |  | 4531300% | N | DWEF Compliant | Compliant |  |  |  | N
15019 | BOURNEMOUTH NO.1 SPS | S |  |  |  |  | N | Y | 750 | 300 | 162.3565 | 904 | -20.53% | 4548900% |  |  |  | N | Compliant | Compliant |  |  |  | N
15577 | Sandford Sandmead Lane SPS | W |  |  |  |  | N | Y | 54 |  | 36.8155 | 71.29 | -32.02% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14274 | East Chaldon . SPS | S |  |  |  |  | N | N | 4 |  | 3.7699 | 4.54 | -13.5% | 4516800% |  |  |  |  | Not currently assessed |  | Monitor. |  |  | Y
14096 | Coxley Mill Lane SPS | W |  |  |  |  | N | Y | 10.8 |  | 13.2536 | 13.09 | -21.2% | 4554100% |  |  |  | N | Compliant | Compliant |  |  | CCTV122987 | Y
14459 | Southwick Chantry Gardens SPS | N |  |  |  |  | N | N | 22 |  | 13.2536 | 25 | -13.64% | 4298650% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15496 | Leigh Bridge Farm SPS | S |  |  |  |  | N | N | 11.8 |  | 5.8905 | 13.5 | -14.41% | 4339650% |  |  | 4502700% |  | Not currently assessed |  |  |  |  | 0
14069 | Street Houndwood Drove SPS | W |  |  |  |  | N | N | 31.4 |  | 13.2536 | 36 | -14.65% | 4364150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15297 | Drayton Ducks Lane SPS | W |  |  |  |  | N | N | 45 |  | 36.8155 | 51.6 | -14.67% | 4341150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15573 | Bleadon Purn SPS | W |  |  |  |  | N | Y | 17 |  | 5.8905 | 19.61 | -15.35% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14132 | Bransgore Wiltshire Gardens SPS | S |  |  |  |  | N | N | 115 |  | 53.0144 | 132.52 | -15.23% | 4301150% |  |  | 4502700% |  | Not currently assessed |  |  |  |  | 0
14295 | YEOVILTON WEIR | W |  |  |  |  | N | Y | 5 |  | 5.8905 | 6 | -20% | 4554000% |  |  |  | N | Compliant | Compliant |  |  | CCTV122542 | N
14252 | Studland Combe | S |  |  |  |  | 14252 | Y | 16.2 | 16 | 13.2536 | 19.85 | -22.53% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
14248 | East Burton Cross Roads SPS | S |  |  |  |  | N | Y | 22 |  | 13.2536 | 26.96 | -22.55% | 4549300% |  |  |  | N | Compliant | Compliant |  |  |  | N
15042 | Burton Stony Lane SPS | S |  |  |  |  | N | N | 35 |  | 58.4483 | 41.09 | -17.4% | 4516800% |  |  |  |  | Not currently assessed |  | VDT may not be accurate as volume is hard to calculate area |  |  | Y
13093 | DONIFORD SPS | W |  |  |  |  | N | Y | 60 |  | 58.4483 | 73.98 | -23.3% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14058 | Horton Horton Farm SPS | N |  |  |  |  | N | Y | 5.6 | 5.6 | 7.1275 | 6.88 | -22.86% | 4551900% |  |  |  | N | DWEF Compliant | Compliant | No RS coming through |  |  | Y
15080 | Ferndown Dugdell Close SPS | S |  |  |  |  | N | N | 173 |  | 72.1585 | 204 | -17.92% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15270 | Poole Creekmore Lane | S |  |  |  |  | 15270 | Y | 120 |  | 119.2823 | 149 | -24.17% | 4549500% |  |  |  | N | Compliant | Compliant |  |  |  | N
15075 | Corfe Mullen Pardys Hill SPS | S |  |  |  |  | N | Y | 42 |  | 36.8155 | 52.64 | -25.33% | 4548600% |  |  |  | N | At Risk | At Risk |  |  |  | N
14427 | Hallatrow . SPS | N |  |  |  |  | N | N | 52 |  | 29.8206 | 62 | -19.23% | 4305250% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15320 | Long Sutton Knole | W |  |  |  |  | N | Y | 2.8 |  | 1.4726 | 3.35 | -19.64% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
15189 | Aust Village | N |  |  |  |  | N | N | 3.1 |  | 5.8905 | 3.7 | -19.35% | 4452600% |  |  |  | N | Not currently assessed |  |  |  |  | 0
15548 | Keynsham Keynsham Low Level SPS | N |  |  |  |  | N | N | 10 |  | 5.8905 | 11.96 | -19.6% | 4346650% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15572 | LOCKING VILLAGE SPS | W |  |  |  |  | N | Y | 46 |  | 13.2536 | 59.2 | -28.7% | 4554000% |  |  |  | N | Compliant | Compliant |  | NB sum these flows for each meter |  | N
13265 | Shapwick Somerset SPS | W |  |  |  |  | N | Y | 7 |  | 5.8905 | 8.65 | -23.57% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
15449 | Meare Green Wrantage SPS | W |  |  |  |  | N | Y | 1 |  | 5.8905 | 1.28 | -28% | 4548700% |  |  |  | N | Compliant | Compliant |  |  |  | N
15106 | Poulshot Townsend SPS | N |  |  |  |  | N | N | 17 |  | 19.0852 | 20.4 | -20% | 4365050% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14452 | Freshford New Inn SPS | N |  |  |  |  | N | N | 5 |  | 8.4823 | 6 | -20% | 4345150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15051 | Corfe Mullen Rushcombe Bottom SPS | S |  |  |  |  | N | N | 25 |  | 23.5619 | 30 | -20% | 4211050% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14255 | STOBOROUGH RIDGE SPS | S |  |  |  |  | N | Y | 5 |  | 5.8905 | 6.42 | -28.4% | 4549300% |  |  |  | N | Compliant | Compliant |  |  |  | N
15434 | Newport North SPS | N |  |  |  |  | N | Y | #N/A |  | 5.8905 | 7.14 | -21.21% | 4494000% |  |  |  | N | Not currently assessed |  | With Luke S |  |  | N
14410 | Burton Bradstock Burton Southover SPS | S |  |  |  |  | N | N | 12 |  | 5.8905 | 14.6 | -21.67% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14337 | Alderbury Home Farm | S |  |  |  |  | N | Y | 22.8 | 27.12 | 23.5619 | 29.28 | -28.42% | 4548900% |  |  |  | N | Compliant | Compliant |  |  |  | N
14099 | Street Walton Globe SPS | W |  |  |  |  | N | N | 5 |  | 9.2039 | 6.1 | -22% | 4368950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14413 | Chideock Seatown | S |  |  |  |  | 14413 | Y | 9.7 |  | 9.2039 | 12.47 | -28.56% | 4548800% |  |  |  | N | At Risk | Out of Consent |  |  |  | N
14456 | Bratton Trowbridge Road | N |  |  |  |  | N | N | 18 |  | 17.0235 | 22 | -22.22% | 4399300% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14358 | South Newton Bell Inn SPS | S |  |  |  |  | N | Y | #N/A |  | 13.2536 | 16.22 | -22.38% | 4495500% |  |  |  |  | Not currently assessed |  |  |  |  | N
15183 | Bagstone SPS | N |  |  |  |  | N | Y | #N/A |  | 8.4823 | 10.4 | -22.61% | 4450300% |  |  |  |  | Not currently assessed |  | Flowmeter stopped working 29th October - IT ticket |  |  | N
15441 | Cheddon Fitzpaine Cheddon Farm SPS | W |  |  |  |  | N | Y | #N/A |  | 5.8905 | 7.49 | -27.15% | 4494200% |  |  |  | N | Not currently assessed |  | OK |  |  | N
14067 | Bitton . SPS | N |  |  |  |  | N | Y | 14.85 | 14.85 | 28.51 | 19.29 | -29.9% | 4551900% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | Y
15497 | MARTINSTOWN SPS | S |  |  |  |  | N | Y | 10 | 10.7 | 9.5008 | 13.06 | -30.6% | 4548500% |  |  |  | N | Compliant | Compliant |  |  |  | 0
15551 | Fisherbridge SPS, Weymouth | S |  |  |  |  | 15551 | Y | #N/A |  | 94.2478 | 116.7 | -23.82% | 4455800% |  |  |  |  | Not currently assessed | Compliant |  |  |  | N
15621 | Clevedon Ladye Bay SPS | W |  |  |  |  | N | Y | 35.5 |  | 23.5619 | 44.98 | -26.7% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | Y
18710 | Bristol Royal Edward Dock | N |  |  |  |  | N | Y | #N/A |  | 72.1585 | 90 | -24.73% | [5 empty] | Not currently assessed |  | Scheme |  |  | N
14289 | Ilchester Ilchester Main SPS | W |  |  |  |  | N | Y | 45 |  | 23.5619 | 60.57 | -34.6% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
15084 | Verwood Potterne Way SPS | S |  |  |  |  | N | Y | 108 |  | 5.8905 | 142.83 | -32.25% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | 0
15644 | Sutton Waldron . SPS | S |  |  |  |  | N | N | 6 |  | 5.8905 | 7.5 | -25% | 4347250% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14585 | Edington Broadmead Lane (Som) SPS | W |  |  |  |  | N | Y | 14 |  | 23.5619 | 18 | -28.57% | 4290950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14311 | Tilshead, Camp Road SPS | S |  |  |  |  | N | Y | 12 |  | 5.8905 | 15.88 | -32.33% | 4549500% |  |  |  | N | DWEF Compliant | Compliant |  |  | CCTV122543 | Y
14286 | Lopen SPS | W |  |  |  |  | N | Y | 11 |  | 9.2039 | 14.21 | -29.18% | 4516800% |  |  |  |  | Not currently assessed |  | Under investigation |  | CCTV122552 | Y
15196 | Sturminster Newton The Bridge SPS | S |  |  |  |  | N | N | 13.7 |  | 13.2536 | 17.4 | -27.01% | 4172950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14050 | Collingbourne Ducis SPS | N |  |  |  |  | N | Y | 20 | 20 | 17.0235 | 26.5 | -32.5% | 4551800% |  |  |  | N | DWEF Compliant | Compliant | Out of consent |  |  | N
14379 | Fiddington SPS | W |  |  |  |  | N | Y | 5.3 |  | 5.8905 | 5.4 | -1.887% | 4554000% |  |  |  | N | Compliant | Compliant |  |  | CCTV122549 | Y
13283 | Spaxton . SPS | W |  |  |  |  | N | N | 11.5 |  | 15.0796 | 14.68 | -27.65% | 4135950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14256 | Affpuddle . SPS | S |  |  |  |  | N | N | 6 |  | 8.4823 | 7.67 | -27.83% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14362 | Chilmark . SPS | S |  |  |  |  | N | Y | 4.9 |  |  | 6.53 | -33.27% | 4549000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14057 | Great Cheverell Cheverell Green SPS | N |  |  |  |  | N | Y | 6 | 7.5 | 13.2536 | 8 | -33.33% | 4551900% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | Y
15057 | Ferndown Thames Close SPS | S |  |  |  |  | N | N | 14 |  | 13.2536 | 18 | -28.57% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15164 | Tytherington Stidcott SPS | N |  |  |  |  | N | N | #N/A |  | 18.0396 | 23.2 | -28.61% | 4411800% |  |  |  |  | Not currently assessed |  |  |  |  | N
14083 | West Pennard Havyatt SPS | W |  |  |  |  | N | Y | 8.1 |  | 9.2039 | 10.96 | -35.31% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | 0
14108 | Mells SPS | W |  |  |  |  | N | Y | 11 |  | 5.8905 | 14.81 | -34.64% | 4549600% |  |  |  | N | Compliant | Compliant |  |  | CCTV122546 | N
15505 | Symondsbury West Road Foundry SPS | S |  |  |  |  | N | Y | 6 | 6 | 53.0144 | 8.22 | -37% | 4548900% |  |  |  | N | Compliant | Compliant |  |  |  | N
14402 | Osmington Pontins SPS | S |  |  |  |  | N | N | 11 |  | 17.0235 | 14.4 | -30.91% | 4364050% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15083 | St Leonards Forest Edge Drive SPS | S |  |  |  |  | N | N | 10 |  | 13.2536 | 13.11 | -31.1% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15200 | Marnhull Sodom Lane SPS | S |  |  |  |  | N | N | 19 |  | 29.8206 | 24.91 | -31.11% | 4172950% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14407 | Stratton Bridge SPS | S |  |  |  |  | N | Y | #N/A |  | 5.8905 | 7.73 | -31.23% | 4494500% |  |  |  |  | Not currently assessed |  |  |  |  | N
14378 | Bridgwater Blake Gardens | W |  |  |  |  | 14378 | Y | 90 |  | 184.7256 | 125 | -38.89% | 4543800% |  |  |  | N | Compliant | Compliant |  |  |  | N
14179 | BIDDESTONE MANOR COT | N |  |  |  |  | N | Y | 7 |  | 5.8905 | 9.78 | -39.71% | 4551800% |  |  | 4538200% | N | DWEF Compliant | Compliant | Out of consent |  |  | N
15555 | Hillcrest Road PS, Wyke, Weymouth | S |  |  |  |  | 15555 | Y | 150 |  | 119.2823 | 210 | -40% | 4548100% |  |  |  | N | Compliant | Compliant |  |  |  | N
15275 | Poole Hewitt Road SPS | S |  |  |  |  | N | N | 15.8 |  | 8.4823 | 21 | -32.91% | 4311650% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14588 | West Lulworth Lulworth Outfall Ps SPS | S |  |  |  |  | N | N | 10.5 |  | 8.4823 | 14.02 | -33.52% | 4516800% |  |  |  |  | Not currently assessed |  | Monitor as Pump 2 flow has decreased recently. |  |  | Y
15495 | Netherbury Beaminster SPS | S |  |  |  |  | N | Y | 3.8 |  | 3.5838 | 5.43 | -42.89% | 4548200% |  |  |  | N | Compliant | Compliant |  |  |  | N
15450 | Norton Fitzwarren Langford Lane | W |  |  |  |  | N | Y | 1.7 |  | 1.4726 | 2.28 | -34.12% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14399 | Osmington Mills SPS | S |  |  |  |  | N | N | #N/A |  | 5.89 | 8 | -35.82% | 4462300% |  |  |  |  | Not currently assessed |  |  |  |  | N
14110 | Stoke St Michael Stoke Hill SPS | W |  |  |  |  | N | Y | 11.3 |  | 5.8905 | 15.96 | -41.24% | 4554000% |  |  |  | N | Compliant | Compliant |  | Faulty meter, now fixed |  | Y
14555 | Isle Abbotts Two Bridges SPS | W |  |  |  |  | N | Y | #N/A |  | 6 | 8.1 | -35% | 4495400% |  |  |  |  | Not currently assessed |  | Monitor. |  |  | N
14070 | Godney | W |  |  |  |  | N | Y | #N/A |  | 3.7699 | 5.21 | -38.2% | 4493900% |  |  |  | Y | Not currently assessed |  | Find consent and add to Qlikview. Hasn't gone into high level recently. |  |  | N
15252 | Poole Egmont Road SPS | S |  |  |  |  | N | N | 10.6 |  | 5.8905 | 14.96 | -41.13% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15188 | Yate North Road SPS | N |  |  |  |  | N | N | 20 |  | 15.0796 | 28.27 | -41.35% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15070 | Wimborne Hayes Lane Colehill SPS | S |  |  |  |  | N | Y | 100 |  | 94.2478 |  | 100% | [10 empty] | 0
14444 | Wingfield Church Lane SPS | N |  |  |  |  | N | N | 2.9 |  | 4.7713 | 4.14 | -42.76% | 4298650% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14531 | Midford Tucking Mill SPS | N |  |  |  |  | N | N | 6 |  | 9.2039 | 8.57 | -42.83% | 4283850% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14519 | Somerton Barpool Lane (Compton Dundon No.3 on Prism) | W |  |  |  |  | N | Y | #N/A |  | 5.8905 | 8.44 | -43.28% | 4495000% |  |  |  | Y | Not currently assessed |  |  |  |  | N
15298 | Limington Main SPS | W |  |  |  |  | N | N | 4 |  | 3.7699 | 5.74 | -43.5% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14458 | North Bradley Churchlands SPS | N |  |  |  |  | N | N | 6 |  | 8.4823 | 8.62 | -43.67% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14188 | LWR STANTON ST QUINTIN SPS | N |  |  |  |  | N | Y | 27.7 | 20 | 29.8206 | 41.41 | -49.49% | 4551900% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | Y
16057 | Bath Technology House SPS | N |  |  |  |  | N | Y | 11 | 6 | 36.8155 | 16.5 | -50% | 4551900% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | 0
15371 | Cross East SPS | W |  |  |  |  | N | Y | 5.5 |  | 5.8905 | 8.31 | -51.09% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14288 | Marston Magna Church Lane SPS | W |  |  |  |  | N | Y | 4 |  | 5.8905 | 6.13 | -53.25% | 4534000% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15325 | Keinton Mandeville . SPS | W |  |  |  |  | N | Y | 19.8 |  | 13.2536 | 30.9 | -56.06% | 4448900% |  |  |  |  | Not currently assessed |  | Requires virtual drop test |  |  | Y
14293 | Queen Camel Englands Mead Green Lane SPS | W |  |  |  |  | N | Y | 9.3 |  | 9.2039 | 15.4 | -65.59% | 4448900% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14227 | Studland Wadmore Lane | S |  |  |  |  | N | Y | 11 |  | 13.2536 | 17.54 | -59.45% | 4548800% |  |  |  | N | Compliant | Compliant |  |  | CCTV121779 | N
14049 | Pewsey Wilcot Lodge SPS | N |  |  |  |  | N | N | 4 |  | 5.8905 | 6 | -50% | 4287750% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14059 | Rowde Tower View SPS | N |  |  |  |  | N | N | 7.7 |  | 8.4823 | 11.6 | -50.65% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14219 | Upton Sandy Lane | S |  |  |  |  | 14219 | Y | 6.4 |  | 5.8905 | 10.6 | -65.62% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
16050 | Bath Ea Depot SPS | N |  |  |  |  | N | Y | 29.9 | 29.9 | 23.5619 | 50 | -67.22% | 4551400% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | 0
14423 | Blue Anchor Pill Bridge | W |  |  |  |  | 14423 | Y | 18 |  | 36.8155 | 30.13 | -67.39% | 4547900% |  |  |  | N | Compliant | Compliant |  |  |  | N
15507 | Bridport West Bay Sluices | S |  |  |  |  | 15507 | Y | 9.3 |  | 5.8905 | 15.78 | -69.68% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | N
14162 | Malmesbury Burton Hill SPS | N |  |  |  |  | N | N | 8 |  | 5.8905 | 12.23 | -52.88% | 4516800% |  |  |  |  | Not currently assessed |  | Pump 2 closer to consent than Pump 1 |  |  | Y
15071 | St Leonards Craigside Road SPS | S |  |  |  |  | N | N | 73 |  | 53.0144 | 113 | -54.79% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
19978 | Rooksbridge Bristol Road SPS | W |  |  |  |  | N | Y | 8.5 | 8.5 | 9.2039 | 14.83 | -74.47% | 4548100% |  |  |  | N | Compliant | Compliant |  |  |  | N
14429 | Chew Stoke Bilbie Road SPS | N |  |  |  |  | N | N | 12.3 |  | 13.2536 | 19.3 | -56.91% | 4332750% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15468 | BRADFORD ON TONE HOCKHOLLER SPS | W |  |  |  |  | N | Y | 6 |  | 5.8905 | 10.74 | -79% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
15523 | Camerton Sunnyvale SPS | N |  |  |  |  | N | N | 3.8 |  | 5.8905 | 6 | -57.89% | 4120750% |  |  |  |  | Not currently assessed |  |  |  |  | 0
17268 | Kingswood Station Road Storm Tank SPS | N |  |  |  |  | N | N | 30 |  | 13.2536 | 47.5 | -58.33% | 4449000% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15454 | Creech St Michael North End SPS | W |  |  |  |  | N | Y | 26 |  | 23.5619 | 47.84 | -84% | 4547900% |  |  |  | N | Compliant | Compliant |  |  |  | 0
19056 | Weymouth Castle Cove Old Castle Road Wyke Regis SPS | S |  |  |  |  | N | N | 30 |  | 29.8206 | 50 | -66.67% | 4322150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14276 | Corfe Castle Studland Road SPS | S |  |  |  |  | N | Y | 17 |  | 21.2647 | 31.33 | -84.29% | 4548100% |  |  |  | N | Compliant | Compliant |  |  |  | N
14093 | West Pennard Page Lane SPS | W |  |  |  |  | N | N | 5 |  | 3.7699 | 8.4 | -68% | 4335750% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14474 | Melksham Semington Roundabout SPS | N |  |  |  |  | N | N | 19 |  | 5.8905 | 32 | -68.42% | 4360850% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15073 | Wimborne Pilford Heath SPS | S |  |  |  |  | N | N | 47 |  | 58.4483 | 80 | -70.21% | 4213650% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14563 | Frome Courts Barton Marston Lane SPS | W |  |  |  |  | N | N | 8 |  | 5.8905 | 13.83 | -72.88% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
18718 | Chapmanslade Divers Bridge SPS | W |  |  |  |  | N | N | 5.2 |  | 13.2536 | 9 | -73.08% | 4352150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15100 | North Newnton . SPS | N |  |  |  |  | N | Y | 10 | 10 | 8.4823 | 18.54 | -85.4% | 4551900% |  |  | 4499300% | N | DWEF Compliant | Compliant |  |  |  | N
14389 | Taunton Priory Storm Tanks SPS | T |  |  |  |  | N | N | 360 |  | 288.6338 | 624.93 | -73.59% | 4118450% |  |  |  |  | Not currently assessed |  |  |  |  | N
15500 | Bradpole Fishweir Foul SPS | S |  |  |  |  | N | N | 7 |  | 5.8905 | 12.64 | -80.57% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14425 | Clutton Greenbrook | N |  |  |  |  | N | N | 30.9 |  | 23.5619 | 57.1 | -84.79% | 4410500% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14388 | Berkeley Park View Road SPS | N |  |  |  |  | N | N | 40 |  | 60.3186 | 74.2 | -85.5% | 4333550% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14283 | Barton St David . SPS | W |  |  |  |  | N | Y | 5.5 |  | 17.0235 | 9.97 | -81.27% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
17162 | Charlton Down SPS | S |  |  |  |  | N | N | #N/A |  | 6 | 10.4 | -73.33% | 4515400% |  |  |  |  | Compliant | Compliant
14199 | Upper Minety Flisteridge SPS | N |  |  |  |  | N | N | 12.5 |  | 19.0852 | 24.1 | -92.8% | 4327850% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14469 | Great Hinton . SPS | N |  |  |  |  | N | N | 1.6 |  | 5.8905 | 3.1 | -93.75% | 4343550% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15072 | Ferndown Ameysford Road SPS | S |  |  |  |  | N | N | 50 |  | 36.8155 | 97 | -94% | 4310150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15574 | Sandford Batch . SPS | W |  |  |  |  | N | N | 9.8 |  | 13.2536 | 19.2 | -95.92% | 4448900% |  |  |  |  | Not currently assessed |  | Requires virtual drop test |  |  | Y
15318 | Stoford Hillside Main SPS | W |  |  |  |  | N | Y | 12 |  | 13.2536 | 24.55 | -104.6% | 4554000% |  |  |  | Y | Compliant | Compliant |  |  |  | Y
15306 | Lower Somerton SPS | W |  |  |  |  | N | Y | 19.8 |  | 23.5619 | 34.75 | -75.51% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | Y
14475 | Broughton Gifford The Green SPS | N |  |  |  |  | N | Y | 12.2 | 12.2 | 13.2536 | 25.49 | -108.9% | 4551900% |  |  |  | N | DWEF Compliant | Compliant |  |  |  | N
15439 | Henlade . SPS | W |  |  |  |  | N | Y | 4.8 |  | 5.8905 | 10.2 | -112.5% | 4548200% |  |  |  | N | Compliant | Compliant |  |  |  | N
15284 | WAGG DROVE SPS | W |  |  |  |  | N | Y | 3 | 3 | 13.2536 | 5.97 | -99% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14087 | West Lydford . SPS | W |  |  |  |  | N | Y | #N/A |  | 5.8905 | 13.02 | -121% | 4494200% |  |  |  | Y | Not currently assessed |  |  |  |  | N
14161 | Compton Bassett The Pond SPS | N |  |  |  |  | N | Y | 6 |  | 9.2039 | 13.1 | -118.3% | 4335450% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15240 | Poole Branksome Chine SPS | S |  |  |  |  | N | N | 58 |  | 53.0144 | 127 | -119% | 4289150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14240 | Bovington Morris Road SPS | S |  |  |  |  | N | N | 2 |  | 5.8905 | 4.42 | -121% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15397 | STAWELL FORD LANE | W |  |  |  |  | N | Y | 3 |  | 5.8905 | 6.35 | -111.7% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
15115 | Chirton Small Street SPS | N |  |  |  |  | N | N | 8 |  | 8.4823 | 17.7 | -121.2% | 4357550% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15253 | Poole Fairview Road SPS | S |  |  |  |  | N | N | 13.3 |  | 5.8905 | 30 | -125.6% | 4289150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
14416 | MINEHEAD MART ROAD SPS | T |  |  |  |  | 14416 | N | #N/A |  | 212.0575 | 481 | -126.8% | 4456900% |  |  |  |  | Not currently assessed |  |  |  |  | N
15561 | Weymouth Ferrybridge Portland Road SPS | S |  |  |  |  | N | N | 20 |  | 53.0144 | 45.4 | -127% | 4448900% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15726 | Portishead Lake Grounds SPS | W |  |  |  |  | N | Y | 8 |  | 13.2536 | 20.73 | -159.1% | 4554100% |  |  |  | N | Compliant | Compliant |  |  |  | 0
15537 | Shoscombe Single Hill SPS | N |  |  |  |  | N | N | 2 |  | 5.8905 | 5.17 | -158.5% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14542 | COAT CRIPPLE STREET SPS | W |  |  |  |  | N | Y | 2.2 |  | 5.8905 | 5.79 | -163.2% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
15068 | St Leonards Wayside Road No 1 SPS | S |  |  |  |  | N | Y | 40 |  | 53.0144 | 111.48 | -178.7% | 4548800% |  |  |  | N | Compliant | Compliant |  |  |  | 0
15552 | Weymouth Knightsdale Newstead Road SPS | S |  |  |  |  | N | N | 87 |  | 477.1294 | 237.4 | -172.9% | 4447400% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14076 | Evercreech Stoney Stratton SPS | W |  |  |  |  | N | N | 6 |  | 5.8905 | 16.6 | -176.7% | 4516800% |  |  |  |  | Not currently assessed |  | Pump 1 - 4.84, Pump 2 - 5. 68 |  |  | Y
15718 | Bishops Hull Shutemead | W |  |  |  |  | N | N | #N/A |  | 5.8905 | 16.6 | -181.8% | [10 empty] | N
14122 | SPETISBURY NO.3 SPS | S |  |  |  |  | N | Y | #N/A |  | 72.1585 | 205.44 | -184.7% | 4494200% |  |  |  | Y | Not currently assessed |  |  |  |  | N
14432 | Compton Dando Turnbridge SPS | N |  |  |  |  | N | N | 3.1 |  | 8.4823 | 9.32 | -200.6% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15313 | HUISH EPISCOPI PIBSBURY | W |  |  |  |  | N | Y | 1.4 |  | 2.8863 | 4.91 | -250.7% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14354 | Barford St Martin . SPS | S |  |  |  |  | N | N | 5 |  | 5.8905 | 15.66 | -213.2% | 4516800% |  |  |  |  | Not currently assessed |  | Requires virtual drop test |  |  | Y
14072 | Wookey Bleadney Mill SPS & CSO | W |  |  |  |  | N | Y | 3.5 |  | 3.7699 | 12.82 | -266.3% | 4516800% |  |  |  |  | Not currently assessed |  |  |  | CCTV122361 | Y
14064 | Kingswood Willsbridge SPS | N |  |  |  |  | N | N | 30 |  | 60.3186 | 101 | -236.7% | 4315150% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15123 | Seend Bell Inn | N |  |  |  |  | N | N | 4 |  | 8.4823 | 14.6 | -265% | 4410500% |  |  |  |  | Not currently assessed |  |  |  |  | 0
15394 | SUTTON MALLET | W |  |  |  |  | N | Y | 5 | 5 | 8.4823 | 17.7 | -254% | 4548300% |  |  |  | N | Compliant | Compliant |  |  |  | N
14261 | Studland Watery Lane SPS | S |  |  |  |  | N | Y | 2.5 |  | 5.8905 | 10.07 | -302.8% | 4549500% |  |  |  | N | Compliant | Compliant |  |  |  | N
17027 | South Cadbury . SPS | W |  |  |  |  | N | N | 6 |  | 7.1275 | 25.42 | -323.7% | 4516800% |  |  |  |  | Not currently assessed |  | P1 is well below consent. Flow recorded is likely higher than reality as the volume is overestimate |  |  | Y
15315 | Huish Episcopi Wagg Bridge SPS | W |  |  |  |  | N | Y | 0.25 |  | 5.8905 | 0.86 | -244% | 4554000% |  |  |  | N | Compliant | Compliant |  |  |  | N
14264 | East Knighton . SPS | S |  |  |  |  | N | N | 1 |  | 5.8905 | 4.36 | -336% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
15074 | West Moors the Forest | S |  |  |  |  | N | Y | #N/A |  | 23.5619 | 120.16 | -410% | 4494200% |  |  |  |  | Not currently assessed |  | Virtual drop test? |  |  | N
14158 | Hullavington Raf Station SPS | N |  |  |  |  | N | N | 4.8 |  | 5.8905 | 28.26 | -488.8% | 4516800% |  |  |  |  | Not currently assessed |  |  |  |  | Y
14562 | Glastonbury Wirral Park SPS | W |  |  |  |  | N | N | 3 |  | 5.8905 | 20 | -566.7% | 4148750% |  |  |  |  | Not currently assessed |  |  |  |  | 0
Note on K1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Fill the DWEF using following steps. 1. Find the recent high level or spill event. 2. Estimate pump run flow. Calculate margin = consent - estimated flow. 3. Check pump flow before starting of spill or when it was in low level before it. 4. Add margin + dry weather flow (DWF) = DWEF.
Note on M1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For filling this column. 1. If spill or high level, fill normally max flow. 2. if dry weather than fill flow using this metric: Adjusted consent: (DWF/DWEF)*Consented flow. DWF: current measured flow during dry weather DWEF: dry weather flow threshold to meet consent in wet weather. Consented flow: consented flow from consented flow column.
Note on R1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Date from which site has been known to be out consent
Note on M62: Suhaib Rehman: Adjusted w.r.t DWEF. (DWF/DWEF)*consent flow
Note on J72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ignore this site for virtual drop test, permit PFF not realistic
Note on J75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not consented but "whats needed"
Note on B76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Review VDT Reply: Dont't include in report
Note on M76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Runstops don't seem to match up
Note on M95: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only able to meet consent with 3 pumps running at once
Note on M96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Site consent changed from 60?. Will be at risk w.r.t new consent but since the level is not high, I'll put as dwef compliant w.r.t scv.
Note on L102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rg Corrected
Note on M122: Suhaib Rehman: (DWF/DWEF)*consent
Note on M131: Suhaib Rehman: Aug 24: (DWF/DWEF)*consent July 24: can kick consent on foul pump 1.
Note on M134: Suhaib Rehman: Calculating from DWEF. This could miss consent by just about 1 l/s. Exclude the starter flow peak.
Note on B135: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Upton SPS
Note on M144: Suhaib Rehman: Flowmeter is dead here. Pumps though seem to be doing good. But no measurable metric.
Note on M145: Suhaib Rehman: is flowmeter working correctly on this site. It looks submerged.
Note on M151: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Flow meter OOS, guestimate from flow tests and FFT meter measured at the WRC
Note on M154: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Drop test not working for this site.
Note on B166: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Long Sutton Bennetts Orchard SPS
Note on M167: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only able to achieve consented flow with pumps 1 and 2 running together.
Note on M170: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Looks like P2 is able to achieve consent but P1 is not
Note on B184: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Portishead SPS
Note on A186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2 flows add together
Note on I186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2 flowmeters - need to add up
Note on M186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Site rarely goes above 50% level Reply: Wet well level was 37.4 at maximum flow. Reply: Add foul and storm together
Note on M219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Do we need to add the Rising Main Storm Flow and Rising Main DWF Flow? Reply: VSD's not spilling, Estmate of flows made from trend
Note on M223: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: P2 achieves consent but P1 just under
Note on I229: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New meter installed at SPS
Note on B234: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Flow is on the treatment works page
Note on M238: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Virtual drop test in DWF shows 31 l/s for both pumps
Note on I242: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inflow rate Reply: Inflow rate is calculated from Pulsar Ultimate controller. Use combined flow meter at Blackheath WRC end (when Bulbury isn't pumping)
Note on M252: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only check during high level
Note on M258: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only able to reach 50 l/s with P1 and P2 running duty assist Reply: In consent when in high level.
Note on J262: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It was N/A before but I found this on my Prism trend. Is it correct?
Note on B276: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cheddar Froglands SPS
Note on M287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: P2 produces 10 l/s, P1 about 5.6 l/s
Note on B307: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Site has two flow meters - add them together
Note on B308: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Shapwick SPS
Note on M309: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: P2 achieves consent but P1 just under
Note on M318: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Site reached high level because no pump ran. Doing more than 92% of consent all the time.
Note on I337: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total Flow Yesterday?
Note on M350: Freya Upton: flow not on my prism
Note on I351: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Job completed so flowmeter should be calinbrated correctly now. Reply: Trend acting weird again since 3/9/22
Note on J360: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consent is 0.42 according to my Prism trend
Note on M379: Suhaib Rehman: Site seems to be running lately
Note on B380: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Minehead blue anchor SPS
Note on B408: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Stoford Main sps
Note on J408: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Decreased from 36 to 12l/s in May22
Note on M410: Suhaib Rehman: Flowmeter is dead here now.
Note on B412: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Huish Episcopi - Wagg Drove
Note on B424: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Coat SPS
Note on B436: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sutton Mallet Stawell

## Definitions
Board Report
| If site not spilt but is running below DWEF, then at risk | At Risk
| If site spilt, below consent then Out of Consent | Out Of Consent
| Everything else - Compliant | Compliant
Ops Reporting
| Within 8% of Consented figure during spill | At Risk
| Below DWEF Figure during dry weather | At Risk
| Below 8% of consented figure during spill | Out Of Consent
| Above Consented figure during spill | Compliant
| Above DWEF figure during dry weather | DWEF Compliant
Overall compliance
92% compliance when spilling more than 95% of the time.
| Suhaib | South
| Freya | West
| Kieran | North

## Action log
Site ID | Site name | Division | Consented flow (l/s) | Max Flow Measured (l/s) | % Out | Type of report, e.g. monthly flow compliance | Current Ops status (Out of consent, at risk of being out of consent, monitor) | Current Board Status | Date of report/action | Flow on reporting date (P1) | Flow on reporting date (P2) | Flow on reporting date (P3) | Action | Actionee | Latest target date to return to compliant | WAM job no.
15207 | SHAFTESBURY LONG CROSS SPS | S |  |  |  | Dec 23 Report |  | Out of Consent | 4539900% |  |  |  | New impellors installed 10/3/24, Look to test grundfos SH pump with Luke Sturgeon
14152 | Calne Broads Green | N |  |  |  | Dump From Old Master |  |  | 4535200% |  |  |  | LS to Retest | LS
14197 | Malmesbury Corston SPS | N | 8 | 4.5 | 36.14% | April 24 Report |  |  | 4548400% |  |  |  | HLA update required. RG
14197 | Malmesbury Corston SPS | N | 8 | 4.5 | 36.14% | April 24 Report |  |  | 4539300% |  |  |  | Impellors fitted, HLA update required.
14197 | Malmesbury Corston SPS | N | 8 | 4.5 | 36.14% | Dec 23 Report |  |  | 4535100% |  |  |  | Impellors ordered, RG to follow up with HLA team, | LS/RG
15111 | All Cannings . SPS | N | 8.5 | 7.5 |  |  |  |  | 4535100% |  |  |  | Watch for improvments.
15158 | OLVESTON THE COMMON SPS | N | 21 | [5 empty] | 2024-07-18 |  |  |  | DD to arange CCTV of main, LS to arrange Pigging after CCTV
15158 | OLVESTON THE COMMON SPS | N | 21 | [5 empty] | 2024-06-12 |  |  |  | Inspection and FM to be undertaken on the 26th June 2024
15158 | OLVESTON THE COMMON SPS | N | 21 | [5 empty] | 4539300% |  |  |  | Inspection to be updertaken when new flowmeter is installed, Sometime in April, to look for restirctions/Second NRV???? EDM signal coming in? Ed?
15158 | OLVESTON THE COMMON SPS | N | 21 | [5 empty] | 4535100% |  |  |  | RM inspection, TE to borrow camera and inspect first section of RM, est 2/4/24
14179 | BIDDESTONE MANOR COT | N | 7 | 6.6 |  |  |  |  | 2024-04-11 |  |  |  | New impellors fitted
14179 | BIDDESTONE MANOR COT | N | 7 | 5 |  |  |  |  | 4535100% |  |  |  | TE ordered new impellors,
14202 | Hankerton Bridge SPS | N | 42 | [5 empty] | 4535100% |  |  |  | TE to schedule AV jobs and crack bypass valve for an hour. TE to order new wear rings
15100 | North Newnton . SPS | N | 10 | 5.61 | 43.9% | Oct 23 Report |  |  | 4535100% | With HLA team |  |  | Sealing work upstream, TE to get pump backup control looked at, P2 airlocked?
14116 | GURNEY SLADE SPS | W | 7 | 5.34 | 23.71% |  |  |  | 4534900% |  |  |  | LS and AP to reattend and test, with new parts for Pump 1. | A
15322 | Pitney . SPS | W | 5.3 | 4.2 | 20.75% |  |  |  | 4534900% |  |  |  | Pressure to be moniotored at AV to see if that tells us something about restriction in main. JH to raise job for altering pump tops speed, AP raising job for Pressure monitoring at the air valve
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.44 | 15.29% |  |  |  | 4534900% |  |  |  | AP to install higher rated pressuret ransducers, AP to write Son for problems at site
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 11.93 | 11.63% |  |  |  | 4539800% |  |  |  | RG - Seperate meeting to discuss way forward, are pumps trimmed correctly?
14379 | Fiddington SPS | W | 5.3 | 5 | 0.566% |  |  |  | 4534900% | P1 did not run during HL | 5.27 |  | Job Raised for p2
15573 | Bleadon Purn SPS | W | [6 empty] | 4540900% |  |  |  | New impellors arrived, Jobs raised. Ash emailing Wholesale service desk about Caravan park….
15573 | Bleadon Purn SPS | W | [6 empty] | 4534900% |  |  |  | New impeollors arriving soons, Jobs raised.
14147 | Chippenham Westmead SPS | N | 155 | 143.61 | 7.348% | Sep 23 Report | Out of Consent |  | 4548900% |  |  |  | Carried forward, pump proposal for simplifying pumps onsite DD and LS
14147 | Chippenham Westmead SPS | N | 155 | 143.61 | 7.348% | Sep 23 Report | Out of Consent |  | 4534600% |  |  |  | Carried forward, pump proposal for simplifying pumps onsite DD and LS
14428 | Corston Newton St Loe | N | 23.5 | 18.9 | 20% | Feb 24 Report |  | Not currently assessed | 4534500% |  |  |  | LS to trial pump and review flows/pressure when Midland Road is pumping at the higher head
14414 | Charminster North Street SPS | S | 45 | 40 | 11.11% | Jan 24 Report |  |  | 4539900% |  |  |  | AV's need doing in field,need access agreeing with landowner, MOT team to attend and retest late May
13153 | Holton Heath Holton Heath SPS SPS | S | 20 | 17.96 | 10% |  |  |  | 4539900% |  |  |  | HT new impellors orders, RG to look for original report. LS to test
14323 | Flower SPS | S | 120 | 0 |  |  |  |  | 4539900% |  |  |  | Harry to replace flow meter May 24. New pumps installed 17/4/24 RG to correct GIS
14328 | Hanging Langford . SPS | S | 12 | 10.37 | 13.58% |  |  |  | 25/7//24 |  |  |  | RG to arrange piggin meeting, HT to move Pressure transducer at little langford
14328 | Hanging Langford . SPS | S | 12 | 10.37 | 13.58% |  |  |  | 4539900% |  |  |  | Consider pigging when inflows reduce, May/june
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 338.55 | 8.5% | Oct 23 Report |  |  | 4539900% | Awaiting feedback from Paul M (R&M) - enabling works, ahead of increasing the speed of the pumps in high level. RG to follow up |  |  | Awaiting feedback from Paul M (R&M) - enabling works, ahead of increasing the speed of the pumps in high level. RG to follow up
14311 | Tilshead, Camp Road SPS | S | 12 | 11.1 | 7.5% | May 23 Report | At Risk | At Risk | 4539900% |  |  |  | Suck and blow sucessful, met consent for 5 days, now at 11l/s. HT to arrange pigging/More suck and blow?
14648 | CHILTON POLDEN MAIN SPS | W | 36 | 29.9 | 19% | 19% |  |  | 4539800% |  |  |  | One pump in, second in on 17th April, flow meter to be reranged!
14648 | CHILTON POLDEN MAIN SPS | W | 36 | 29.9 | 19% | 19% |  |  | 4531700% |  |  |  | LS to order pumps. | LS
15389 | Pawlett Main Road SPS | W | 19.2 | [5 empty] | 2024-07-23 |  |  |  | Trial booster pump has been installed to deal with increased flows, site needs to be in high level before the booster pump kicks in, monitor over the next couple of months
15389 | Pawlett Main Road SPS | W | 19.2 | 13.5 |  |  |  |  | 4539800% |  |  |  | Storm Pump installed into chamber 18/4/24
15389 | Pawlett Main Road SPS | W | 19.2 | 13.5 |  |  |  |  | 4531700% |  |  |  | Luke to look at pump selections for dry well pump. Spill boster pump, site limited to 80A feed. Sperate meeting
14265 | Upton Moorlands Way | S | 45 | 44.38 | 1.378% | Apr 23 Report | At Risk | At Risk | 4539900% |  |  |  | HT to get pumps checked and AV maintaince undertaken
14431 | Bishop Sutton . SPS | N | 19.6 | [5 empty] | 4549100% |  |  |  | DD to install inflow check valves and RG to monitor, LS to assess requirements for pigging.
14431 | Bishop Sutton . SPS | N | 19.6 | [5 empty] | 4530900% |  |  |  | Air Valve install with Tim/D&C/Mills awaiting fabrication of special piece, DD to look at p2 and speak with Adam Sparrow - RG to provide Air valve code.
14145 | Malmesbury Tanners Bridge | N | 18 | 8.96 | 50.22% |  |  |  | 2024-01-18 |  |  |  | Follow up with HLA team RG, DD to shim Tanners bridge impellors
14174 | Box Mill Lane SPS | N | 27.3 | 25.06 | 8.205% | Dec 23 Report | Out of Consent | Out of Consent | 4530600% |  |  |  | Wait until pump maintenance in April/May, then maybe new impeollors, or best pumps from LS?
14420 | Minehead Quay West | W | 14 | 7.28 | 48% |  |  |  | 4529500% |  |  |  | Jan24: needs sump in h/l to achive flow
15389 | Pawlett Main Road SPS | W | 19.2 | 11.1 | 42.19% |  |  |  | 4529500% |  |  |  | Jan24: booster pump trial
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 5.9 | 26.25% |  |  |  | 4529500% |  |  |  | Jan24: new pumps have been installed site now meeting consent
14116 | GURNEY SLADE SPS | W | 7 | 5.34 | 23.71% |  |  |  | 4529500% |  |  |  | Jan24: VSD controls flow due sump level and rising main pressure
14648 | CHILTON POLDEN MAIN SPS | W | 36 | 28.9 | 19.72% |  |  |  | 4529500% |  |  |  | Jan24: will need pumps checking
14621 | PORTISHEAD TOWN HARBOUR | W | 260 | 214 | 17.69% |  |  |  | 4529500% |  |  |  | Jan24: flow is set a 250 ON HMI
15320 | Long Sutton Knole | W | 2.8 | 2.356 | 15.86% |  |  |  | 4529500% |  |  |  | Jan24: parts ordered to rebuild pump
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.44 | 15.29% |  |  |  | 4529500% |  |  |  | Jan24: pumps controlled by VSD possible partly bloked riser as pressure rising and tripping pumps
15309 | Charlton Mackerell Rookery Farm | W | 26 | 22.5 | 13.46% |  |  |  | 4529500% |  |  |  | Jan24: LS was looking at pump upgade
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 11.93 | 11.63% |  |  |  | 4529500% |  |  |  | Jan24: pumps into same main as middlezoy ongoing issue monitor
15449 | Meare Green Wrantage SPS | W | 1 | 0.9 | 10% |  |  |  | 4539800% |  |  |  | AMS to suck and blow
15449 | Meare Green Wrantage SPS | W | 1 | 0.9 | 10% |  |  |  | 4529500% |  |  |  | Jan24: raise job for pumps to be checked
15334 | CHARLTON ADAM | W | 21 | 19.21 | 8.524% |  |  |  | 4529500% |  |  |  | Jan24: raise job to check / trim pumps
15400 | Bridgwater West Quay SPS | W | 206 | 191.448 | 7.064% |  |  |  | 4529500% |  |  |  | Jan24: please monitor
15415 | Bridgwater, Colley Lane SPS | W | 123 | 117.56 | 4.423% |  |  |  | 4529500% |  |  |  | Jan24: ok no action needed
14372 | West Huntspill Sloway Lane | W | 130 | 130.77 | -0.5923% |  |  |  | 4529500% |  |  |  | Jan24: pump have trimmed and new hardend impellors ordered
15111 | All Cannings . SPS | N | 8.5 | 6.66 | 21.65% | Dec 23 Report |  |  | 4527500% |  |  |  | New impellor on p1, p2 on order. Monitor for improvements - LS to follow up | LS
15158 | OLVESTON THE COMMON SPS | N | 21 | [5 empty] | 4527500% |  |  |  | LS to feedback
14179 | BIDDESTONE MANOR COT | N | 7 | 6.52 |  |  |  |  | 4527500% |  |  |  | LS to feedback on current proposal | LS
14431 | Bishop Sutton . SPS | N | 19.6 | [5 empty] | 4527500% |  |  |  | Air Valve install with Tim/D&C/Mills awaiting fabrication of special piece, DD to look at p2 and speak with Adam Sparrow
14174 | Box Mill Lane SPS | N | 27.3 | 25.06 | 8.205% | May 23 Report | Out of Consent | Out of Consent | 4527500% |  |  |  | DD to look into pump impellors check with LS for best pump? | DD/LS
14185 | MALMESBURY ST JOHNS | N |  |  |  | Dec 23 Report |  |  | 4527500% |  |  |  | flows dropped off, DD to isolate each main and give a decent flush thru
15090 | West Parley Church Lane | S | [6 empty] | 4527300% |  |  |  | Can do consent but at 3 pumps need to be running. Panel undersized and too old, HT to arrange boxed spare for site
14266 | Wareham Sandford Lane SPS | S | 60 | 43 |  | Oct Report | Compliant | At risk | 4552500% |  |  |  | Imepllors and wear rings, also not switching duty
14266 | Wareham Sandford Lane SPS | S | 60 | 59.04 | 1.6% | Oct Report | Compliant | At risk | 4527200% |  |  |  | Impellors arrived, Installed before end of May.
14266 | Wareham Sandford Lane SPS | S | 60 | 59.04 | 1.6% | Oct Report | Compliant | At risk | 4527200% |  |  |  | HT to order new impellor and wear ring
15389 | Pawlett Main Road SPS | W | 19.2 | 12.77 |  |  |  |  | 4527200% |  |  |  | Speak to Matt kettle, Check pump operation, Paul Elson Impermeable area study??
14116 | GURNEY SLADE SPS | W | 7 | 6.22 | 11.14% | Dec 23 Report |  |  | 4527200% |  |  |  | Review pump operation/pump curve with LS after finding issues with rising main
15207 | SHAFTESBURY LONG CROSS SPS | S |  |  |  | Dec 23 Report |  | Out of Consent | 4527200% |  |  |  | HT to order new impellors for both pumps. Testing hardened Iron ones
14404 | Beaminster Southgate SPS | S | 31 | 27.76 | 10.45% | October report | Out of Consent |  | 4523900% |  |  |  | Cliff to install VSD's, RM replacement being undertaken, Pump 1 to be checked HT
15322 | Pitney . SPS | W | 5.3 | 5.01 | 5.472% | Sept 23 Report |  |  | 4523400% |  |  |  | pumps are run of vsd and will ramp up to meet consent when wet well rises
15311 | Yeovil Mudford SPS | W | 9.3 | 8.77 | 5.699% |  |  |  | 4539800% |  |  |  | JH to get P2 looked at
15311 | Yeovil Mudford SPS | W | 9.3 | 8.77 | 5.699% | Sept 23 Report |  |  | 4523300% |  |  |  | flow meter is not givivg correct readings as to close to pumps this has been confirmed with flow meter test outside of building and pumps are meeting consent
14116 | GURNEY SLADE SPS | W | 7 | 6.22 | 11.14% | Sept 23 Report |  |  | 4523200% |  |  |  | site update completed site is also run off vsd so pumps ramp up as wet well rises
14386 | Greinton Moor Drive SPS | W | 34 | 29.99 | 11.79% | Sept 23 Report |  |  | 4523100% |  |  |  | on HLA list no change
14244 | Durlston Road SPS | S | 11 |  |  | SIA Meeting |  |  | 4536500% |  |  |  | LS to retest | LS
14328 | Hanging Langford . SPS | S | 12 | 10.37 | 13.58% | Oct 23 Report |  |  | 4523100%
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.48 | 12.94% | Sept 23 Report |  |  | 4523000% |  |  |  | pumps are run of vsd and will ramp up to meet consent when wet well rises
15111 | All Cannings . SPS | N | 8.5 | 6.66 | 21.65% | Oct 23 Report |  |  | 4523000% | LS to arrange retest, |  |  | LS to arrange retest,
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 6.03 | 24.62% | Sept 23 Report |  |  | 4522900% |  |  |  | scheme raised pumps are at the workshop ready to be delivered to site
14179 | BIDDESTONE MANOR COT | N | 7 | 6.52 | 6.857% | Oct 23 Report |  |  | 4522900% | Look at historic max flows, PPM history, pass to North / Sean to investigate on site. Flow meter is a clamp-on Flow Pulse. Could put a flow meter/portable flow meter in NRV chamber. Feedback from Luke Sturgeon - pumps achieving 11 and 8 l/s. P1 273 and P2 274 impellers - 8.1 l/s and 7.9 l/s, measured with Katronics flow meter. DD to re-calibrate the Pulsar flow meter w/c 15/11/21. P1 should be doing 10l/s. P2 should be doing 8.5 l/s. DD to look at swapping a pump in from Westerleigh SPS and/or maintaining P1 Flow meter needs calibrating
14095 | Glastonbury Porchestall SPS | W | 200 | 143.07 | 28.46% | Sept 23 Report |  |  | 4522800% |  |  |  | new rising main connection completed 6/10/23 please monitor
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 288.52 | 16.37% | Oct 23 Report |  |  | 4522800% | Both pumps have had impellers replaced - now within 10-12% of PFF, but wet well hasn't gone into high level/spilt. Monitor during high level - site doesn't spill much. |  |  | Both pumps have had impellers replaced - now within 10-12% of PFF, but wet well hasn't gone into high level/spilt. Monitor during high level - site doesn't spill much.
15233 | Poole Wilderton Road | S | 350 | 321.63 | 8.106% | Oct 23 Report |  |  | 4522800% | Hidrostall coming to maintain pumps 15th/16th Nov. P2 currently out. At risk of not being compliant. 3 pumps need to run to achieve PFF - Suhaib to check reporting |  |  | Hidrostall coming to maintain pumps 15th/16th Nov. P2 currently out. At risk of not being compliant. 3 pumps need to run to achieve PFF - Suhaib to check reporting
14145 | Malmesbury Tanners Bridge | N | 18 | 8.96 | 50.22% | Oct 23 Report |  |  | 4522800% | HLA for this and Noahs Ark , source protection zone as well, can't have it bursting. |  |  | HLA for this and Noahs Ark , source protection zone as well, can't have it bursting.
14202 | Hankerton Bridge SPS | N | 42 | 39.45 | 6.071% | Oct 23 Report |  |  | 4522800% | June23: Apr23: Look into installing bigger pumps? (Check what flows they would be getting) - check power for the panel to see if we can install 37kw pumps - Possible discharge a portion of the flow into Charlton? - Ask about reconsenting? |  |  | June23: Apr23: Look into installing bigger pumps? (Check what flows they would be getting) - check power for the panel to see if we can install 37kw pumps - Possible discharge a portion of the flow into Charlton? - Ask about reconsenting?
15389 | Pawlett Main Road SPS | W | 19.2 | 12.59 | 34.43% | Sept 23 Report |  |  | 4522700% |  |  |  | trial booster pump has now been wired into storm tank so when it reaches 60% called to run and this should meet consent please monitor
15400 | Bridgwater West Quay SPS | W | 206 | 184.36 | 10.5% | Oct 23 Report |  |  | 4522700% | Jul23: new nrvs installed last week please monitor to see if improvment |  |  | Jul23: new nrvs installed last week please monitor to see if improvment
15244 | Poole Elgin Road | S | 650 | 547.34 | 15.79% | Oct 23 Report |  |  | 4522700% | Meeting with SOE next week to discuss next steps to pass forward more flow. P4 currently out (grit), need to get Celvac down to clean now the inlet penstock has been repaired. Control philosophy needs changing again to limit one pump's operation to 2-3 hours before switching duty |  |  | Meeting with SOE next week to discuss next steps to pass forward more flow. P4 currently out (grit), need to get Celvac down to clean now the inlet penstock has been repaired. Control philosophy needs changing again to limit one pump's operation to 2-3 hours before switching duty
14414 | Charminster North Street SPS | S | 45 | 40 | 11.11% | Oct 23 Report |  |  | 4522700% | Outstanding actions - trim impellers and AV work (HT) |  |  | Outstanding actions AV work (HT)
15207 | SHAFTESBURY LONG CROSS SPS | S |  |  |  | Dec 23 Report |  | Out of Consent | 4532000% |  |  |  | LS to review tesst and look to see if main needs cleaning etc, retest after new impellers
14431 | Bishop Sutton . SPS | N | 19.6 | 17.84 | 8.98% | Oct 23 Report |  |  | 4522700%
15158 | OLVESTON THE COMMON SPS | N | 21 | 19.21 | 8.524% | Oct 23 Report |  |  | 4522700%
14391 | Stoke St Gregory No 1 Lane End | W | 27 | 15.99 | 40.78% | Sept 23 Report |  |  | 4522600% |  |  |  | this site has 2 flow meters and need to be added together to make the consent only happens in wet weather
14112 | WANSTROW SPS | W | 7 | 3.96 | 43.43% | Sept 23 Report |  |  | 4522500% |  |  |  | needs 2 pumps to run to meet consent this only happens in wet wearther
14386 | Greinton Moor Drive SPS | W | 34 | 30 | 11.76% | Oct 23 Report |  |  | 4522400% | Jul23: HLA being undertaken |  |  | Jul23: HLA being undertaken
15311 | Yeovil Mudford SPS | W | 9.3 | 9.166 | 1.441% | Oct 23 Report |  |  | 4522400% | Flow meter seems to be working better now since pump was rebuilt by SW last week |  |  | Flow meter seems to be working better now since pump was rebuilt by SW last week
14337 | Alderbury Home Farm | S | 22.8 | 22 | 3.509% | Oct 23 Report |  |  | 4522400% | Neil carried out on site investigation/training 19/08/20, found to be compliant Flow meter installed 03/11/21 |  |  | Neil carried out on site investigation/training 19/08/20, found to be compliant Flow meter installed 03/11/21
15190 | Milborne St Andrew Manor Farm SPS | S | 47 | 15.86 | 66.26% | Oct 23 Report |  |  | 4522300% | Not been in high level - need storm & DWF pumps to achieve PFF |  |  | Not been in high level - need storm & DWF pumps to achieve PFF
14266 | Wareham Sandford Lane SPS | S | 60 | 58.65 | 2.25% | Oct 23 Report |  |  | 4522300% | Jun23: Maintenance. HT to raise a job for Pump 1 not running |  |  | Jun23: Maintenance. HT to raise a job for Pump 1 not running
14197 | Malmesbury Corston SPS | N | 8 | 5.109 | 36.14% | Oct 23 Report |  |  | 4521900% | LS is going to speak to Adam again…... |  |  | LS is going to speak to Adam again…...
15233 | Poole Wilderton Road | S |  |  |  | Sept 23 Report |  |  | 4521700% |  |  |  | Hidrostall coming to maintain pumps 15th/16th Nov. P2 currently out. At risk of not being compliant. 3 pumps need to run to achieve PFF - Suhaib to check reporting, HT to check pressure transducer, LS to attend to do test and system curve.
15190 | Milborne St Andrew Manor Farm SPS | S |  |  |  | Sept 23 Report |  |  | 4521700% |  |  |  | Not been in high level - need storm & DWF pumps to achieve PFF
15235 | SHORE ROAD POOLE | S |  |  |  | Sept 23 Report |  |  | 4521700% |  |  |  | Do pressure logging along the main to identify the problem - with RG
15244 | Poole Elgin Road | S |  |  |  | Sep 23 Report |  |  | 4521700% |  |  |  | Meeting with SOE next week to discuss next steps to pass forward more flow. P4 currently out (grit), need to get Celvac down to clean now the inlet penstock has been repaired. Control philosophy needs changing again to limit one pump's operation to 2-3 hours before switching duty
14414 | Charminster North Street SPS | S | 45 |  |  | Sep 23 Report |  |  | 4521700% |  |  |  | Outstanding actions - trim impellers and AV work (HT)
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 |  |  | Sep 23 Report |  |  | 4521700% |  |  |  | Both pumps have had impellers replaced - now within 10-12% of PFF, but wet well hasn't gone into high level/spilt. Monitor during high level - site doesn't spill much.
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 |  |  | Sep 23 Report |  |  | 4521700% |  |  |  | Awaiting feedback from Paul M (R&M) - enabling works, ahead of increasing the speed of the pumps in high level. RG to follow up
15389 | Pawlett Main Road SPS | W | 19.2 | 12.77 | 33.49% | Oct 23 Report |  |  | 4521200% | Checking mono power draw against existing booster pump - LS. Next steps, detail what needs doing to formalise the arrangement, civils replacment DWF pumps etc |  |  | Checking mono power draw against existing booster pump - LS. Next steps, detail what needs doing to formalise the arrangement, civils replacment DWF pumps etc
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 6.78 | 15.25% | Oct 23 Report |  |  | 4521200% | Jul23: scheme raised |  |  | Jul23: scheme raised
15111 | All Cannings . SPS | N | 8.5 | 4.8 | 14.59% | Sep 23 Report | Out of Consent |  | 4519600% |  |  |  | LS to arrange retest
14147 | Chippenham Westmead SPS | N | 155 | 143.61 | 7.348% | Sep 23 Report | Out of Consent |  | 4519000% |  |  |  | Currently on watching brief….not spilling at the moment, DD/LS to look at ensuring all pumps are matching and whats been done previously
14197 | Malmesbury Corston SPS | N | 8 | 4.82 | 39.75% | Jul 23 Report | Out of Consent |  | 4519000% |  |  |  | LS is going to speak to Adam again……
15311 | Yeovil Mudford SPS | W | 9.3 | 9.24 | 0.6452% | June 23 Report | At Risk | Out of Consent | 4513900% | May23: Waiting from update from LS /DDP -> Scaling okay, LS to check flowmeter Apr23: LS team to verify the flowmeter (AP to email LS), AP to check with Sam about P2, DDP to check scaling on the flowmeter |  |  | Flow meter seems to be working better now since pump was rebuilt by SW last week
15715 | Bridgwater Horsey Bath Road SPS | W | 54 | 52.65 | 2.5% | Jul-23 report |  |  | 4543300% |  |  |  | LS to retest in wetter weather
15715 | Bridgwater Horsey Bath Road SPS | W | 54 | 52.65 | 2.5% | Jul-23 report |  |  | 4513900% |  |  |  | Aug-23: Confirm if site runs as duty assist was this with 2 pumps running. Pumps frequently air locking
14145 | Malmesbury Tanners Bridge | N | 18 | 13.32 | 26% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | HLA for this and Noahs Ark , source protection zone as well, can't have it bursting.
15572 | LOCKING VILLAGE SPS | W | 56 | 27.19 | 40.89% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: need both flow meter readings to be taken as seperate rising mains. Summing flows - looks to be compliant
15389 | Pawlett Main Road SPS | W | 19.2 | 12.35 | 35.68% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: temp pipe work to be installed this week to trail temp tamdem pump when this is delivered
15322 | Pitney . SPS | W | 5.3 | 4.28 | 19.25% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: new pumps and panel installed last week just needs to be set up for PFF
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 6.63 | 17.12% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: scheme raised
14386 | Greinton Moor Drive SPS | W | 34 | 28.48 | 16.24% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: HLA being undertaken
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 11.56 | 14.37% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: Still waiting for feedback from site visit LS RG AP
14095 | Glastonbury Porchestall SPS | W | 200 | 171.68 | 14.16% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: scheme raised
14116 | GURNEY SLADE SPS | W | 7 | 6.28 | 10.29% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: site upgrade has started last week
15400 | Bridgwater West Quay SPS | W | 206 | 194.73 | 5.471% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: new nrvs installed last week please monitor to see if improvment
15317 | NORTON SUB HAMDON SPS | W | 15.4 | 14.59 | 5.26% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: VSD have been increased on FRI 28/7
14372 | West Huntspill Sloway Lane | W | 130 | 125.42 | 3.523% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: please monitor as pumps have been air locked due to falut on low level sensor in wet well
15715 | Bridgwater Horsey Bath Road SPS | W | 54 | 52.65 | 2.5% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: site runs as duty assist was this with 2 pumps running
15311 | Yeovil Mudford SPS | W | 9.3 | 9.24 | 0.6452% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | Jul23: p2 has been rebuilt 28/7 and flow is only for info as not accurate
14328 | Hanging Langford . SPS | S | 12 | 9.71 | 19.08% | Jul 23 Report | Out of Consent |  | 4513400%
15244 | Poole Elgin Road | S | 650 | 548.25 | 15.65% | Jul 23 Report | Out of Consent |  | 4513400%
15190 | Milborne St Andrew Manor Farm SPS | S | 47 | 41.69 | 11.3% | Jul 23 Report | Out of Consent |  | 4513400%
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 307.3 | 10.93% | Jul 23 Report | Out of Consent |  | 4513400%
15235 | SHORE ROAD POOLE | S | 90 | 82.77 | 8.033% | Jul 23 Report | Out of Consent |  | 4513400%
15257 | Poole Bridge Poole Quay | S | 15 | 14.2 | 5.333% | Jul 23 Report | Out of Consent |  | 4513400%
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 350.59 | 5.246% | Jul 23 Report | Out of Consent |  | 4513400%
15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 14.33 | 4.467% | Jul 23 Report | Out of Consent |  | 4513400%
10312 | Iron Acton Hoovers Lane SPS | N | 400 | 205.7 | 48.58% | Jul 23 Report | Out of Consent |  | 4513400%
15100 | North Newnton . SPS | N | 10 | 6.99 | 30.1% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | With HLA team
14174 | Box Mill Lane SPS | N | 27.3 | 25.07 | 8.168% | Jul 23 Report | Out of Consent |  | 4513400%
15158 | OLVESTON THE COMMON SPS | N | 21 | 19.98 | 4.857% | Jul 23 Report | Out of Consent |  | 4513400% |  |  |  | NOV23: LS to update plan and proceed with replacement if we get a dry couple of weeks, needs AMS availability
14431 | Bishop Sutton . SPS | N | 19.6 | 18.87 | 3.724% | Jul 23 Report | Out of Consent |  | 4513400%
15389 | Pawlett Main Road SPS | W | 19.2 | 11.94 | 37.81% | Site specific meeting | At Risk | At Risk | 4510400% |  |  |  | Site Specific Meeting: Booster trial for Grundfos (still being discussed internally) -> tell Grundfos that we would like to trail overground and ask if they can send stuff over to us (LS to ask Dave Little). Consider also asking Pump Supplies (AP to ask them) for a trial as Grundfos are taking a while. Confirm whether PVC main. AP, RG, LS to meet on-site to confirm what we want to done with the site (Thurs 29th June).
10312 | Iron Acton Hoovers Lane SPS | N | 400 | 201.5 | 49.62% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Jun23: Mimic needs to be redrawn (NB to do). ESD scheme looking at imoriving the flows (scheme code: C00613) Apr23: ESD scheme. Put serviced pump back in, then take out and service other pump
14197 | Malmesbury Corston SPS | N | 8 | 4.26 | 46.75% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Jun23: Pump testing at 4.8 l/s. Would be running at 6bar down a PVC RM to meet the flows. Long term: Possible options: set up a PD/set up two stations. Needs a HLA. Short term: Going up a impellor size would give us 5.8 l/s (LS to speak to Adam and get new impellors).
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 189.1 | 45.19% | June 23 Report | Out of Consent | Out of Consent | 4510300% |  |  |  | Oct 23 p3 awaiting trimming following lifting improvements. Watching brief aug 23 HT to replace p2 and 3 imepllors and test Jun23: Only 2 pumps (P1 out), and doesn't bring in a second pump during high level -> HT raise a job to look at. Impellor still not delivered yet (arrive next week - wk comm 1/7) Apr23: Waiting for new impellors to be delivered
15257 | Poole Bridge Poole Quay | S | 15 | 9.76 | 34.93% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Jun23: Swap out pump 1. Put in new impellors once delivered. Apr23: HT ordered new impellors
15389 | Pawlett Main Road SPS | W | 19.2 | 11.94 | 37.81% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | 01/08/23 - pipework mods done for tandem pumps today - look to install pumps in the next week. May23: Waiting for Grundfos to come back with booster pump info DDPhas amended plc to run pumps in duty assist and runsignals have been looked at as not going back to prism. LS to leave to fill and see what flows are achieved (maybe take out NRV and let fill). Take it out of duty/assist. Arrange a brief meeting once AP is back Apr23: Short term Plan: Grundfos looking at different options, waiting to see what they come back with (Booster would have to be 500-800m along rising main and couldnt be at station itself - Land purchase issues etc. - could we put at Rose Farm? - Spur with an NRV). AP and DDP to trial running duty/assist Long term plan: Send in HLA request to SHS (RG to do)
14328 | Hanging Langford . SPS | S | 12 | 9.75 | 18.75% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Jun23: NR,RG,LS to disuss in HLA meeting 29/6 Apr23: Scheme being raised for it - should soon be out of high level for the summer
15244 | Poole Elgin Road | S | 650 | 546.93 | 15.86% | June 23 Report | Out of Consent | Out of Consent | 4510300% |  |  |  | Jun23: Meeting to discuss 29/6 - PGG with Asset Strategy + Compliance to discuss risk of returning site to pump forward 650 l/s, following engineering scheme to upgrade pumps and install surge tank. Pumps currently capped at 550 l/s (43Hz) Apr23: HT to speak to Chris about how the pumps are running - The set up a meeting to discuss the pump operation (why only 2 pumps are running during high level, etc.) - work out what pumps should be doing in dry weather
15322 | Pitney . SPS | W | 5.3 | 4.28 | 19.25% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | 01/08/23 scheme now complete, final commissioning to get pumps up to full flow - monitor flow in the next month. Testing showed pumps doing 7.3 l/s May23: Site update has started with building works being completed. Apr23: Short Term plan: Civil work ongoing - work (pumps, panels, etc.) should be completed by June. (AP to let RG know when work done) (Delays due to manafactureres)
15235 | SHORE ROAD POOLE | S | 90 | 78.65 | 12.61% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | June23: RG to look into pressure along main to look for air pockets. New pressure transducer delivered 30/6 Apr23: Pump and AV maintenance (change from 12 monthly to 6 monthly - RG to send note to Carla) - pressure transducer needs fixing - RG and Andy Bolden to go to site and monitor the flows
14386 | Greinton Moor Drive SPS | W | 34 | 28.87 | 15.09% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Aug23: On HLA list, get Meteor camera installed or storm chamber Apr 23: Currently doing HLA with site to work out best thing to do |  | 4538200%
14404 | Beaminster Southgate SPS | S | 31 | 27.36 | 11.74% | June 23 Report | Out of Consent | Out of Consent | 4510300% |  |  |  | Jun23: HT to try different impellor sizes, switch VSD off, keep below 31. RG to meet with Andy Bolden and HT to look at pressure along RM (19/7)
14116 | GURNEY SLADE SPS | W | 7 | 6.12 | 12.57% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Aug23: panel being installed Aug-23 May23: y3 scheme no change from last month - pumps at WSM, waiting for panel Apr23: Short Term plan: Civil work ongoing - work (pumps, panels, etc.) doesnt have a ETA yet. (AP to let RG know when work done) (Delays due to manafactureres) Mar 23 Comment: y3 scheme to be delivered in May |  | 4516900%
14174 | Box Mill Lane SPS | N | 27.3 | 24.87 | 8.901% | June 23 Report | Out of Consent | Out of Consent | 4510300% |  |  |  | Aug23: Damian to adjust VSd's to meet consent…..ICA job Jun23: Ops to do outstanding pump maintenance |  | 4512100% | 2280162
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 7.27 | 9.125% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Aug23 Y4 scheme, panel & pumps on order, due later in Y4 May23: AP has met L Chant on site to go through what is needed last week for new scheme - keep an eye on and keep flows as high as possible - new panels been ordered, AP team to be replacing pumps Apr23: y4 Scheme raised, with divisional engineering, AP meeting with them next week, should be delivered similar time to Pill Avon Road
15158 | OLVESTON THE COMMON SPS | N | 21 | 19.76 | 5.905% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Aug23: LS to arrange tankers for replacment of foot stools for pumps. EW checking on EDM config Apr23: Review once pumps put in
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 348.17 | 5.9% | June 23 Report | At Risk | Out of Consent | 4510300% |  |  |  | June23: Contingency plan ongoing - penstock diverting flow to Iford Lane and 2 points for over pumping Apr23: RG to follow up with PM concerning mitigation options
14431 | Bishop Sutton . SPS | N | 19.6 | 18.73 | 4.439% | June 23 Report | At Risk | Out of Consent | 4510300% |  |  |  | Sep23:TE onsite with D&C, Possibly look to install AV on tanker point for trial as well? DD to get start level increased Aug23: RG to check with TE regarding order of pipework for trial. Apr23: RG to meet TE to look at site
13273 | Shipton Gorge Off Markets Lane SPS | S | 6.3 | 6.07 | 3.651% | June 23 Report | At Risk | Out of Consent | 4510300% |  |  |  | June23: LS to test. Check whether impellors were trimmed Apr23: Maintenance due - trim impellors while there
15317 | NORTON SUB HAMDON SPS | W | 15.4 | 14.42 | 6.364% | June 23 Report | At Risk | Out of Consent | 4510300% |  |  |  | Aug23: VSDs adjusted last week, monitor in high flows over the next month, swithcing duty between pumps now
14414 | Charminster North Street SPS | S | 45 | 44.16 | 1.867% | June 23 Report | At Risk | Out of Consent | 4510300% |  |  |  | Aug23 - HT to check AV's and order new impellors Jun23: Put in 2 new chambers. HT going there with Paul Apr23: Re-raised job with R&M so they re-visit site
14202 | Hankerton Bridge SPS | N | 42 | 41.3 | 1.667% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | June23: Apr23: Look into installing bigger pumps? (Check what flows they would be getting) - check power for the panel to see if we can install 37kw pumps - Possible discharge a portion of the flow into Charlton? - Ask about reconsenting?
14266 | Wareham Sandford Lane SPS | S | 60 | 59.04 | 1.6% | June 23 Report | Compliant | Compliant | 4510300% |  |  |  | Jun23: Maintenance. HT to raise a job for Pump 1 not running
15400 | Bridgwater West Quay SPS | W | 206 | 198.78 | 3.505% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Aug23: Meter calibration team on site this week, new NRVs have been installed last week. Monitor. May23: No change waiting for update from AW - RG to follow up with Alex and Will Apr23: Passed to AW on Flow Team, Pumps need to be replaced, confirm flowmeters are reading correctly, RG to follow up with AW
15311 | Yeovil Mudford SPS | W | 9.3 | 9.24 | 0.6452% | June 23 Report | At Risk | Out of Consent | 4510300% |  |  |  | May23: Waiting from update from LS /DDP -> Scaling okay, LS to check flowmeter Apr23: LS team to verify the flowmeter (AP to email LS), AP to check with Sam about P2, DDP to check scaling on the flowmeter
14145 | Malmesbury Tanners Bridge | N | 18 | 17.45 | 3.056% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Aug 23: HLA required for whole catchment upstream Jun23: Apr23: LS to do a system review (with Noah's Ark)
15111 | All Cannings . SPS | N | 8.5 | 7.37 | 13.29% | June 23 Report | Out of Consent | Out of Consent | 4510300% |  |  |  | Aug23: AV maintence to be released, then review. RS still not operational-s2000 required Apr23: Mapping still ongoing (RG to send follow up email), maintenance completed
14147 | Chippenham Westmead SPS | N | 155 | 130.05 | 16.1% | June 23 Report | At Risk | At Risk | 4510300% |  |  |  | Aug -Doing 145l/s on 14/7/23, 1m below spill level, hold further work. Jun23: Ramp up to 145l/s and see what it does over the summer. DD to look a pump 2 Apr23: Ongoing investigation - RG to meet DD on site to look into control philosophy (7/5)
15100 | North Newnton . SPS | N | 10 | 5.63 | 43.7% | June 23 Report | Out of Consent | Out of Consent | 4510300% |  |  |  | June23: To be discussed at HLA meeting 29/6. Short term: Going up an impellor size & cleaning the scale/rust off the RM. Raise with camera crew to look into RM from discharge end Apr23: Look at isolation valve and AV maintenance
14197 | Malmesbury Corston SPS | N | 8 | 3.92 | 51% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Newly Added
10312 | Iron Acton Hoovers Lane SPS | N | 400 | 251 | 37.25% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Apr23: ESD scheme. Put serviced pump back in, then take out and service other pump
15244 | Poole Elgin Road | S | 650 | 415.95 | 36.01% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | Apr23: HT to speak to Chris about how the pumps are running - The set up a meeting to discuss the pump operation (why only 2 pumps are running during high level, etc.) - work out what pumps should be doing in dry weather
14328 | Hanging Langford . SPS | S | 12 | 9.22 | 23.17% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | Apr23: Scheme being raised for it - should soon be out of high level for the summer
15389 | Pawlett Main Road SPS | W | 19.2 | 11.74 | 38.85% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | May23: Waiting for Grundfos to come back with booster pump info DDPhas amended plc to run pumps in duty assist and runsignals have been looked at as not going back to prism. LS to leave to fill and see what flows are achieved (maybe take out NRV and let fill). Take it out of duty/assist. Arrange a brief meeting once AP is back Apr23: Short term Plan: Grundfos looking at different options, waiting to see what they come back with (Booster would have to be 500-800m along rising main and couldnt be at station itself - Land purchase issues etc. - could we put at Rose Farm? - Spur with an NRV). AP and DDP to trial running duty/assist Long term plan: Send in HLA request to SHS (RG to do)
15322 | Pitney . SPS | W | 5.3 | 4.19 | 20.94% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | May23: Site update has started with building works being completed. Apr23: Short Term plan: Civil work ongoing - work (pumps, panels, etc.) should be completed by June. (AP to let RG know when work done) (Delays due to manafactureres)
14289 | Ilchester Ilchester Main SPS | W | 45 | 35.65 | 20.78% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | job already raised to investigate as picked up by sewerage monitoring team - looks better now
15257 | Poole Bridge Poole Quay | S | 15 | 13.09 | 12.73% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Apr23: HT ordered new impellors
15158 | OLVESTON THE COMMON SPS | N | 21 | 18.7 | 10.95% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Apr23: Review once pumps put in
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 311.45 | 9.725% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Apr23: Waiting for new impellors to be delivered
14414 | Charminster North Street SPS | S | 45 | 40.68 | 9.6% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Apr23: Re-raised job with R&M so they re-visit site
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 11.45 | 15.19% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Aug23 burst detection working ok now, can do more analysis on the data. Trial inflow check valves at Othery, one at high point. May23: awaiting feedback from RG AP LS site visit from last month - lots of air in the main -> try with equal flow valve ->go back with R&M to replace chamber with equal T and new AV (RG to send email out). AP to speak with Dave Comer Apr23: Short TermPlan: Could have been put out by Middlezoy, LS to trial putting 451 impellors for both sites (AP to buy the 451's). RG to visit site to look at air in the rising main
14174 | Box Mill Lane SPS | N | 27.3 | 25.06 | 8.205% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | -
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.19 | 8.75% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | May23: Update due to start later this month - about 1/2 way through Apr23: Overrun Engineering delivery (Should start 22th May, hopefully compliant within 2 weeks of this) Mar 23 Comment: y3 scheme delivered next month Feb23 Comment: y3 scheme - delivered next 2 months
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 7.35 | 8.125% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | May23: AP has met L Chant on site to go through what is needed last week for new scheme - keep an eye on and keep flows as high as possible - new panels been ordered, AP team to bereplaceing pumps Apr23: y4 Scheme raised, with divisional engineering, AP meeting with them next week, should be delivered similar time to Pill Avon Road
14414 | Charminster North Street SPS | S | 45 | 40 | 11.11% | Jan 24 Report |  |  | 4532000% |  |  |  | Outstanding actions AV work (HT)
14311 | Tilshead, Camp Road SPS | S | 12 | 11.1 | 7.5% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Mar23: 1 pump has been installed, 2nd one not installed yet - seems to have been doing flows above 12 l/s since pump installed - HT to switch off and let it go to high level to see what flows we get, also to increase the start levels
15516 | Bilbrook . SPS | W | 4 | 3.69 | 7.75% | May 23 Report | At Risk | Out of Consent | 4507800% |  |  |  | May23: Rebuild pumps to bring them back up above consent - JH to raise job Apr23: Job still in system for this to be checked, JH to get done for this week
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 342.5 | 7.432% | May 23 Report | At Risk | Out of Consent | 4507800% |  |  |  | Apr23: RG to follow up with PM concerning mitigation options
15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 13.9 | 7.333% | May 23 Report | At Risk | Out of Consent | 4507800% |  |  |  | Apr23: HT to look for mystery RM feature again (25/05/23) - if it's an AV then replace and see what happens
13153 | Holton Heath Holton Heath SPS SPS | S | 20 | 18.76 | 6.2% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Apr23: LS to visit site - test EDM - impellors have been ordered
14431 | Bishop Sutton . SPS | N | 19.6 | 18.48 | 5.714% | May 23 Report | At Risk | Out of Consent | 4507800% |  |  |  | Apr23: RG to meet TE to look at site
15400 | Bridgwater West Quay SPS | W | 206 | 190.68 | 7.437% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | May23: No change waiting for update from AW - RG to follow up with Alex and Will Apr23: Passed to AW on Flow Team, Pumps need to be replaced, confirm flowmeters are reading correctly, RG to follow up with AW
15235 | SHORE ROAD POOLE | S | 90 | 87.82 | 2.422% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Apr23: Pump and AV maintenance (change from 12 monthly to 6 monthly - RG to send note to Carla) - pressure transducer needs fixing - RG and Andy Bolden to go to site and monitor the flows
14391 | Stoke St Gregory No 1 Lane End | W | 27 | 26.25 | 2.778% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | May23: sump needs to be full and both pumps foul and storm will monitor - may need a bit of a trim -> JH to raise job to raise both pumps Apr: EJ to check spill level on prism trend and review
14116 | GURNEY SLADE SPS | W | 7 | 6.86 | 2% | May 23 Report | At Risk | Out of Consent | 4507800% |  |  |  | May23: y3 scheme no change from last month - pumps at WSM, waiting for panel Apr23: Short Term plan: Civil work ongoing - work (pumps, panels, etc.) doesnt have a ETA yet. (AP to let RG know when work done) (Delays due to manafactureres) Mar 23 Comment: y3 scheme to be delivered in May
14202 | Hankerton Bridge SPS | N | 42 | 41.54 | 1.095% | May 23 Report | At Risk | Out of Consent | 4507800% |  |  |  | Apr23: Look into installing bigger pumps? (Check what flows they would be getting) - check power for the panel to see if we can install 37kw pumps - Possible discharge a portion of the flow into Charlton? - Ask about reconsenting?
14095 | Glastonbury Porchestall SPS | W | 200 | 196.34 | 1.83% | May 23 Report | At Risk | Out of Consent | 4507800% |  |  |  | Aug-23 New panel on order, scheme to be delivered ~Jan-24. Look to run site off temp panel in the meantime and bigger pumps. May23: AP has met divisional eng for y4 scheme - on the list for new RM and new panel - RG to speak to AP about 2nd assist pump being started a bit earlier Apr23: Short/long term plan:y4 Scheme raised, with divisional engineering, AP meeting with them next week
15311 | Yeovil Mudford SPS | W | 9.3 | 9.24 | 0.6452% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | May23: Waiting from update from LS /DDP -> Scaling okay, LS to check flowmeter Apr23: LS team to verify the flowmeter (AP to email LS), AP to check with Sam about P2, DDP to check scaling on the flowmeter
14145 | Malmesbury Tanners Bridge | N | 18 | 10.92 | 39.33% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | Apr23: LS to do a system review (with Noah's Ark)
15111 | All Cannings . SPS | N | 8.5 | 6.2 | 27.06% | May 23 Report | Out of Consent | Out of Consent | 4507800% |  |  |  | Apr23: Mapping still ongoing (RG to send follow up email), maintenance completed
14147 | Chippenham Westmead SPS | N | 155 | 129.65 | 16.35% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Apr23: Ongoing investigation - RG to meet DD on site to look into control philosophy (7/5)
15100 | North Newnton . SPS | N | 10 | 5.74 | 42.6% | May 23 Report | At Risk | At Risk | 4507800% |  |  |  | Apr23: Look at isolation valve and AV maintenance
10312 | Iron Acton Hoovers Lane SPS | N | 400 | 193.6 | 51.6% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | ESD scheme. Put serviced pump back in, then take out and service other pump
15389 | Pawlett Main Road SPS | W | 19.2 | 11.45 | 40.36% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Short term Plan: Grundfos looking at different options, waiting to see what they come back with (Booster would have to be 500-800m along rising main and couldnt be at station itself - Land purchase issues etc. - could we put at Rose Farm? - Spur with an NRV). AP and DDP to trial running duty/assist Long term plan: Send in HLA request to SHS (RG to do)
15244 | Poole Elgin Road | S | 650 | 437.12 | 32.75% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | Apr23: HT to speak to Chris about how the pumps are running - The set up a meeting to discuss the pump operation (why only 2 pumps are running during high level, etc.) - work out what pumps should be doing in dry weather
14328 | Hanging Langford . SPS | S | 12 | 9.05 | 24.58% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | Apr23: Scheme being raised for it - should soon be out of high level for the summer
15322 | Pitney . SPS | W | 5.3 | 4.1 | 22.64% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | Apr23: Short Term plan: Civil work ongoing - work (pumps, panels, etc.) should be completed by June. (AP to let RG know when work done) (Delays due to manafactureres) Mar 23 Comment:y3 scheme to be delivered start of next week Feb23 Comment:- y3 scheme - waiting for civil work update from MH
15158 | OLVESTON THE COMMON SPS | N | 21 | 16.7 | 20.48% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | Review once pumps put in
15190 | Milborne St Andrew Manor Farm SPS | S | 47 | 37.45 | 20.32% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Aug23 HT to attend and review setpoints and site operation Apr23: HT to raise job to look at the VSD control for the DWF pump (switch off, fill up, and see what happens) - also see what switching duty for pumps 1 & 2 and storm pumps 1 & 2 does to the flows Mar 23 Comment: Able to do well over consent - but treatment can't cope with these larger flows. HT to get VSD's to cap the flows at 47 l/s Feb23 Comment: Tested to do around 60l/s. EJ to look whether we're getting these flows on Prism
15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 12.73 | 15.13% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | Apr23: HT to look for mystery RM feature again (25/05/23) - if it's an AV then replace and see what happens Mar 23 Comment: LS to investigate mystery RM feature Feb23 Comment: New impellors delivered, HT to install
14116 | GURNEY SLADE SPS | W | 7 | 5.95 | 15% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Short Term plan: Civil work ongoing - work (pumps, panels, etc.) doesnt have a ETA yet. (AP to let RG know when work done) (Delays due to manafactureres) Long Term Plan: Mar 23 Comment: y3 scheme to be delivered in May Feb23 Comment: y3 scheme - AS installing early April Site still running duty/assist - out of consent
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 11.5 | 14.81% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Short TermPlan: Could have been put out by Middlezoy, LS to trial putting 451 impellors for both sites (AP to buy the 451's). RG to visit site to look at air in the rising main Long Term Plan: Mar 23 Comment:May need to replace a chunk of the rising main before we start playing with the flows - RG to add to list Feb23 Comment: LS was looking at different impellor for this site - P1 airlocked/blocked & 2 bursts in January - Wait until wet weather and monitor then
14095 | Glastonbury Porchestall SPS | W | 200 | 171.53 | 14.24% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | Apr23: Short/long term plan:y4 Scheme raised, with divisional engineering, AP meeting with them next week Feb23 Comment: - needs new MCC to allow control changes in philosophy -Wait until RM is replaced in June/July 2023
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.07 | 13.75% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | Apr23: Overrun Engineering delivery (Should start 22th May, hopefully compliant within 2 weeks of this) Mar 23 Comment: y3 scheme delivered next month Feb23 Comment: y3 scheme - delivered next 2 months
14431 | Bishop Sutton . SPS | N | 19.6 | 17.29 | 11.79% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | RG to meet TE to look at site
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 308.48 | 10.59% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Waiting for new impellors to be delivered Mar 23 Comment: RM scheme to be delivered later this year - EJ to do manual checks during HL, instead of Suhaib's code
15235 | SHORE ROAD POOLE | S | 90 | 81.46 | 9.489% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Pump and AV maintenance (change from 12 monthly to 6 monthly - RG to send note to Carla) - pressure transducer needs fixing - RG and Andy Bolden to go to site and monitor the flows Mar 23 Comment: HT to do site maintenance
15400 | Bridgwater West Quay SPS | W | 206 | 186.68 | 9.379% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Passed to AW on Flow Team, Pumps need to be replaced, confirm flowmeters are reading correctly, RG to follow up with AW Mar 23 Comment: Pumps 1&2 okay, P3 struggling - EJ to keep an eye on - RG to ask AW to look at flowmeters 2&3 Feb23 Comment: - pumps have been trimmed by Adam - Separate out 3 signals from combined
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 7.29 | 8.875% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: y4 Scheme raised, with divisional engineering, AP meeting with them next week, should be delivered similar time to Pill Avon Road Mar 23 Comment: Needs scheme raised - needs bigger pump i.e. a bigger panel (AP condition graded panel, NR to check with AW) Feb23 Comment: this will need a scheme, new uprated MCC to allow bigger pump, 3171 273 impellor to achieve PFF and keep main cleansed LS to investigate adding a booster
15002 | Boscombe No 1 SPS | S | 45 | 41.19 | 8.467% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr 23: HT to look into replacing hydrosal pumps with flights - LS to test and compare to magflows - wind up VSD and see if we meet flows
15449 | Meare Green Wrantage SPS | W | 1 | 0.92 | 8% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Review after maintenance on P1, if that doesn’t work do a suck and blow on the rising main Mar 23 Comment: AP to look into - site on&off or suck & blow of the rising main - or experiment changing the pump starts (AP to raise job) Feb23 Comment: - monitor site
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 341.09 | 7.814% | Apr 23 Report | At Risk | Out of Consent | 4504700% |  |  |  | Apr23: RG to follow up with PM concerning mitigation options
15516 | Bilbrook . SPS | W | 4 | 3.71 | 7.25% | Apr 23 Report | At Risk | Out of Consent | 4504700% |  |  |  | Apr23: Job still in system for this to be checked, JH to get done for this week Mar 23 Comment: JH to raise job for air valves - look at pressure trend when well let to fill - AP to get Sam/Henry down Feb23 Comment: - looks ok on trend 9lps
14202 | Hankerton Bridge SPS | N | 42 | 39.04 | 7.048% | Apr 23 Report | At Risk | Out of Consent | 4504700% |  |  |  | Look into installing bigger pumps? (Check what flows they would be getting) - check power for the panel to see if we can install 37kw pumps - Possible discharge a portion of the flow into Charlton? - Ask about reconsenting?
14420 | Minehead Quay West | W | 14 | 13.04 | 6.857% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr: AP to speak to EW to get a spill count and review consent, send over to Andy Mears for consent review
15317 | NORTON SUB HAMDON SPS | W | 15.4 | 14.37 | 6.688% | Apr 23 Report | At Risk | Out of Consent | 4504700% |  |  |  | Apr: Able to do the flows Mar 23 Comment: EJ to keep an eye on
14386 | Greinton Moor Drive SPS | W | 34 | 32.15 | 5.441% | Apr 23 Report | At Risk | Out of Consent | 4504700% |  |  |  | Mar & Apr 23: Currently doing HLA with site to work out best thing to do Feb23 Comment: HW's team looking at it
13273 | Shipton Gorge Off Markets Lane SPS | S | 6.3 | 6.06 | 3.81% | Apr 23 Report | At Risk | Out of Consent | 4504700% |  |  |  | Apr23: Maintenance due - trim impellors while there
14414 | Charminster North Street SPS | S | 45 | 43.94 | 2.356% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Re-raised job with R&M so they re-visit site Mar 23 Comment: HT to complete AV maintenance and find control philosophy for the site
14391 | Stoke St Gregory No 1 Lane End | W | 27 | 26.37 | 2.333% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr: EJ to check spill level on prism trend and review
15002 | Boscombe No 1 SPS | S | 45 | 41.19 | 8.467% |  |  |  | 4532000% |  |  |  | LS to look at measurements to install Flygt pump, plan is to permanently replace 1 pump with flygts then use the hydrostal as spare
14265 | Upton Moorlands Way | S | 45 | 44.38 | 1.378% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Waiting for some spare impellors - Have a look at the flowmeter - Alex to visit site with LS Mar 23 Comment: LS to plan and trial some different impellors and/or different pumps
15311 | Yeovil Mudford SPS | W | 9.3 | 9.21 | 0.9677% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: LS team to verify the flowmeter (AP to email LS), AP to check with Sam about P2, DDP to check scaling on the flowmeter Mar 23 Comment: EJ to keep an eye on Feb23 Comment: please check when flow dropped off could be due to S2000 install
13153 | Holton Heath Holton Heath SPS SPS | S | 20 | 19.82 | 0.9% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: LS to visit site - test EDM - impellors have been ordered Mar 23 Comment: EJ to monitor
14145 | Malmesbury Tanners Bridge | N | 18 | 9.72 | 46% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | LS to do a system review (with Noah's Ark) -
14147 | Chippenham Westmead SPS | N | 155 | 115.58 | 25.43% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | Apr23: Ongoing investigation - RG to meet DD on site to look into control philosophy (7/5) Jan 23 - Need a control philosophy for the new panel - DD and RG to visit site
15111 | All Cannings . SPS | N | 8.5 | 5.64 | 33.65% | Apr 23 Report | Out of Consent | Out of Consent | 4504700% |  |  |  | Apr23: Mapping still ongoing (RG to send follow up email), maintenance completed Jan23: -RG to speak to Brian about mapping of the new RM -Check new air valves, do maintenance on pumps and review
15100 | North Newnton . SPS | N | 10 | 5.53 | 44.7% | Apr 23 Report | At Risk | At Risk | 4504700% |  |  |  | Apr23: Look at isolation valve and AV maintenance Jan 23: When dry - check isolation valves are correctly open/closed on both sites of river - NB to speak to TE NR to raise job - liase with LS to make sure he's there on same day
14311 | Tilshead, Camp Road SPS | S | 12 | 6.28 | 47.67% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | 1 pump has been installed, 2nd one not installed yet - seems to have been doing flows above 12 l/s since pump installed - HT to switch off and let it go to high level to see what flows we get, also to increase the start levels Feb23 Comment: New pumps ready to be delivered to site
15389 | Pawlett Main Road SPS | W | 19.2 | 11.36 | 40.83% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Mar23: awaiting Grundfos booster trial/solution - Grundfos to visit 19/4 LS to speak to Hydrostall Site Specific Meeting (31/1/23): Darren to check levels in storm tank/EDM spill level and where it comes from (storm tank or wet well?), raise stop and start levels and install low flow alert, get IFM checked/cleaned. LS to consider a trial pump to go into the storm tank to pump more flow forward when the storm tank is filling Jan 23 Comment: LS to investigate agaisnst Grundfos
15100 | North Newnton . SPS | N | 10 | 6.35 | 36.5% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Feb23 Comment: Jan 23: When dry - check isolation valves are correctly open/closed on both sites of river - NB to speak to TE NR to raise job - liase with LS to make sure he's there on same day
14095 | Glastonbury Porchestall SPS | W | 200 | 137.43 | 31.28% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Feb23 Comment: - needs new MCC to allow control changes in philosophy -Wait until RM is replaced in June/July 2023
15322 | Pitney . SPS | W | 5.3 | 4.1 | 22.64% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | y3 scheme to be delivered start of next week Feb23 Comment:- y3 scheme - waiting for civil work update from MH
15158 | OLVESTON THE COMMON SPS | N | 21 | 16.41 | 21.86% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | New pumps and footstalls are on site ready to fit. LS and TE agreed to wait for drier weather to fit the footstalls so the flows are managed easier.
14328 | Hanging Langford . SPS | S | 12 | 9.75 | 18.75% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | Trimming implellors didn’t make much difference, RG email to ask SHS to raise a HLA for the rising main changes, and ask AB about reduction of consented flow Feb23 Comment: LS to discuss changing RM (see if it could be dropped into Stoford/South Newton?) with RG, NR to get costs for pumps upgrades, LS to look at pump selection
15190 | Milborne St Andrew Manor Farm SPS | S | 47 | 39.17 | 16.66% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Able to do well over consent - but treatment can't cope with these larger flows. HT to get VSD's to cap the flows at 47 l/s Feb23 Comment: Tested to do around 60l/s. EJ to look whether we're getting these flows on Prism
14116 | GURNEY SLADE SPS | W | 7 | 6.06 | 13.43% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | y3 scheme to be delivered in May Feb23 Comment: y3 scheme - AS installing early April Site still running duty/assist - out of consent
14202 | Hankerton Bridge SPS | N | 42 | 36.42 | 13.29% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | Feb23 Comment: -
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 6.96 | 13% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Needs scheme raised - needs bigger pump i.e. a bigger panel (AP condition graded panel, NR to check with AW) Feb23 Comment: this will need a scheme, new uprated MCC to allow bigger pump, 3171 273 impellor to achieve PFF and keep main cleansed LS to investigate adding a booster
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 11.81 | 12.52% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | May need to replace a chunk of the rising main before we start playing with the flows - RG to add to list Feb23 Comment: LS was looking at different impellor for this site - P1 airlocked/blocked & 2 bursts in January - Wait until wet weather and monitor then
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.51 | 11.18% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | Scheme complete, some issue with NRV's - some commitioning issues atm Feb23 Comment: - y3 scheme - to be completed next few weeks
14050 | Collingbourne Ducis SPS | N | 20 | 17.79 | 11.05% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Feb23 Comment: -
15516 | Bilbrook . SPS | W | 4 | 3.59 | 10.25% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | JH to raise job for air valves - look at pressure trend when well let to fill - AP to get Sam/Henry down Feb23 Comment: - looks ok on trend 9lps
15645 | PILL AVON ROAD SPS | W | 80 | 72.36 | 9.55% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | New pump put in last week (31/3), next one to be put in tomorrow (5/4) - EJ to check flows once site set up Feb23 Comment: y3 scheme
15402 | Middlezoy Nethermoor Road SPS | W | 11 | 9.99 | 9.182% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | May need to replace a chunk of the rising main before we start playing with the flows - RG to add to list Feb23 Comment: P2 reached 10.2 l/s in high level, P1 9.3 l/s. Look to produce combined system curves for Middlezoy and Othery to come up with a solution for both sites - both sites pumping into the same system - with Asset Reliability/Ops
14386 | Greinton Moor Drive SPS | W | 34 | 30.89 | 9.147% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | Currently doing HLA with site to work out best thing to do Feb23 Comment: HW's team looking at it
14431 | Bishop Sutton . SPS | N | 19.6 | 17.95 | 8.418% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | Feb23 Comment: Damian's team (possible also R&M) to investigate air valve by chip shop [Mon/Tue/Wed - in school term time] - temporary air valve to check it works RG to arrange
14414 | Charminster North Street SPS | S | 45 | 41.37 | 8.067% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | SR looking at infiltration issues, R&M clearing out Air Valves (HT to chase up) Feb23 Comment: HT to complete AV maintenance and find control philosophy for the site
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 343.15 | 7.257% | Mar 23 Report | At Risk | Out of Consent | 4501700% |  |  |  | Waiting for costs for LEP before changing flows Feb23 Comment: monitor site
15257 | Poole Bridge Poole Quay | S | 15 | 13.95 | 7% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | HT ordered new impellors Feb23 Comment: HT to look into ordering new impellors, check pumps are sat right
15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 14.02 | 6.533% | Mar 23 Report | At Risk | Out of Consent | 4501700% |  |  |  | LS to investigate mystery RM feature Feb23 Comment: New impellors delivered, HT to install
15449 | Meare Green Wrantage SPS | W | 1 | 0.94 | 6% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | AP to look into - site on&off or suck & blow of the rising main - or experiment changing the pump starts (AP to raise job) Feb23 Comment: - monitor site
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.28 | 5% | Mar 23 Report | At Risk | Out of Consent | 4501700% |  |  |  | y3 scheme delivered next month Feb23 Comment: y3 scheme - delivered next 2 months
15400 | Bridgwater West Quay SPS | W | 206 | 196.52 | 4.602% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Pumps 1&2 okay, P3 struggling - EJ to keep an eye on - RG to ask AW to look at flowmeters 2&3 Feb23 Comment: - pumps have been trimmed by Adam - Separate out 3 signals from combined
15002 | Boscombe No 1 SPS | S | 45 | 42.98 | 4.489% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Both pumps should be doing 30l/s individually - HT to order some new impellors Feb23 Comment: Tested to do 48 l/s. Monitor
15078 | Ferndown A31 Tricketts Cross SPS | S | 218 | 211.78 | 2.853% | Mar 23 Report | At Risk | Out of Consent | 4501700% |  |  |  | HT to install the remaining 2 impellors - depends on which configuration but flows seem okay
15235 | SHORE ROAD POOLE | S | 90 | 87.56 | 2.711% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Maintenance onging Feb23 Comment: HT to do site maintenance
13273 | Shipton Gorge Off Markets Lane SPS | S | 6.3 | 6.16 | 2.222% | Mar 23 Report | At Risk | Out of Consent | 4501700% |  |  |  | Maintenance Feb23 Comment: will raise job to get impellors cchecked
14265 | Upton Moorlands Way | S | 45 | 44.41 | 1.311% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Feb23 Comment: LS to plan and trial some different impellors and/or different pumps
15311 | Yeovil Mudford SPS | W | 9.3 | 9.23 | 0.7527% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | EJ to keep an eye on Feb23 Comment: please check when flow dropped off could be due to S2000 install
15317 | NORTON SUB HAMDON SPS | W | 15.4 | 15.34 | 0.3896% | Mar 23 Report | At Risk | Out of Consent | 4501700% |  |  |  | EJ to keep an eye on
14147 | Chippenham Westmead SPS | N | 155 | 109.81 | 29.15% | Mar 23 Report | At Risk | At Risk | 4501700% |  |  |  | Feb23 Comment: Jan 23 - Need a control philosophy for the new panel - DD and RG to visit site
15111 | All Cannings . SPS | N | 8.5 | 6.97 | 18% | Mar 23 Report | Out of Consent | Out of Consent | 4501700% |  |  |  | Feb23 Comment: Jan23: -RG to speak to Brian about mapping of the new RM -Check new air valves, do maintenance on pumps and review
14145 | Malmesbury Tanners Bridge | N | 18 | 8.86 | 50.78% | Mar 23 Report | Out of Consent | Out of Consent | 4501700%
14414 | Charminster North Street SPS | S | 45 | 41 ish | ~8% | Site specific meeting |  | At Risk | 4500100% |  |  |  | HT to complete AV maintenance and find control philosophy for the site |  |  | 6480427 6480431
15100 | North Newnton . SPS | N | 10 | 6.5 | 35% | Feb 23 Report |  | At Risk | 4499300% |  |  |  | Jan 23: When dry - check isolation valves are correctly open/closed on both sites of river - NB to speak to TE NR to raise job - liase with LS to make sure he's there on same day |  |  | 2242051
10312 | Iron Acton Hoovers Lane SPS | N | 400 | 186.75 | 53.31% | Feb 23 Report |  | At Risk | 4499300% |  |  |  | -
14095 | Glastonbury Porchestall SPS | W | 200 | 123.47 | 38.27% | Feb 23 Report |  | Out of Consent | 4499300% |  |  |  | Jan23: - needs new MCC to allow control changes in philosophy -Wait until RM is replaced in June/July 2023
15400 | Bridgwater West Quay SPS | W | 206 | 195.84 | 4.932% | Feb 23 Report |  | At Risk | 4499300% |  |  |  | Jan23: - pumps have been trimmed by Adam - Separate out 3 signals from combined
15317 | NORTON SUB HAMDON SPS | W | 15.4 | 15.17 | 1.494% | Feb 23 Report |  | At Risk | 4499300% |  |  |  | -
14147 | Chippenham Westmead SPS | N | 155 | 86.57 | 44.15% | Feb 23 Report |  | Out of Consent | 4499300% |  |  |  | Jan 23 - Need a control philosophy for the new panel - DD and RG to visit site
14311 | Tilshead, Camp Road SPS | S | 12 | 6.15 | 48.75% | Feb 23 Report |  | Out of Consent | 4498700% |  |  |  | New pumps ready to be delivered to site
14096 | Coxley Mill Lane SPS | W | 10.8 | 5.9 | 45.37% | Feb 23 Report |  | Out of Consent | 4498700% |  |  |  | Jan23: -Macerators unblocked, new plates installed on both pumps 16/12/22 -y3 scheme - to be completed next week
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 197.63 | 42.72% | Feb 23 Report |  | Out of Consent | 4498700% |  |  |  | RM scheme to be delivered later this year - EJ to do manual checks during HL, instead of Suhaib's code
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.26 | 25.88% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | Jan23:- y3 scheme - to be completed next few weeks
15322 | Pitney . SPS | W | 5.3 | 4.2 | 20.75% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | Jan23: - y3 scheme - waiting for civil work update from MH
14328 | Hanging Langford . SPS | S | 12 | 9.64 | 19.67% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | LS to discuss changing RM with RG, NR to get costs for pumps upgrades, LS to look at pump selection
15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 12.26 | 18.27% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | New impellors delivered, HT to install
15235 | SHORE ROAD POOLE | S | 90 | 73.86 | 17.93% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | HT to do site maintenance |  |  | 2204836
15645 | PILL AVON ROAD SPS | W | 80 | 66.23 | 17.21% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | y3 scheme
15318 | Stoford Hillside Main SPS | W | 36 | 30.69 | 14.75% | Feb 23 Report |  | Out of Consent | 4498700% |  |  |  | Jan 23: Being modelled by ESD No further actions done yet - RG to speak with Kieron
15449 | Meare Green Wrantage SPS | W | 1 | 0.86 | 14% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | Jan23: - monitor site
15158 | OLVESTON THE COMMON SPS | N | 21 | 18.28 | 12.95% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | Jan23: - LS to fit new pump
14420 | Minehead Quay West | W | 14 | 12.84 | 8.286% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | Jan23: - will monitor as needs full sump to get max flow
14414 | Charminster North Street SPS | S | 45 | 41.59 | 7.578% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | EW,NR and LS to look into wording of consent. HT to redo AV maintenance and come back and test
14265 | Upton Moorlands Way | S | 45 | 42.86 | 4.756% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | LS to plan and trial some different impellors and/or different pumps |  |  | 6480431
15516 | Bilbrook . SPS | W | 4 | 3.86 | 3.5% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | Jan23: - looks ok on trend 9lps
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.33 | 2.917% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | y3 scheme - delivered next 2 months
15075 | Corfe Mullen Pardys Hill SPS | S | 42 | 41.18 | 1.952% | Feb 23 Report |  | Out of Consent | 4498700% |  |  |  | Look into ordering new impellors. LS to carry out pump testing with HT's team
15257 | Poole Bridge Poole Quay | S | 15 | 14.91 | 0.6% | Feb 23 Report |  | Out of Consent | 4498700% |  |  |  | HT to look into ordering new impellors, check pumps are sat right
13153 | Holton Heath Holton Heath SPS SPS | S | 20 | 19.93 | 0.35% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | EJ to monitor
14227 | Studland Wadmore Lane | S | 11 | 11.51 | -4.64% | Feb 23 Report |  | Compliant | 4498700% |  |  |  | LS to monitor over weekend
15111 | All Cannings . SPS | N | 8.5 | 6.16 | 27.53% | Feb 23 Report |  | At Risk | 4498700% |  |  |  | Jan23: -RG to speak to Brian about mapping of the new RM -Check new air valves, do maintenance on pumps and review
15389 | Pawlett Main Road SPS | W | 19.2 | 16.27 | 15.26% | Feb 23 Report |  | At Risk | 4498600% |  |  |  | Site Specific Meeting (31/1/23): Darren to check levels in storm tank/EDM spill level and where it comes from (storm tank or wet well?), raise stop and start levels and install low flow alert, get IFM checked/cleaned. LS to consider a trial pump to go into the storm tank to pump more flow forward when the storm tank is filling Jan 23 Comment: LS to investigate agaisnst Grundfos
14145 | Malmesbury Tanners Bridge | N | 18 | 17.61 | 2.167% | Feb 23 Report |  | At Risk | 4498600% |  |  |  | -
15100 | North Newnton . SPS | N | 10 | 4.85 | 51.5% | Jan 23 Report |  | DWEF Compliant | 4496300% | P1 did not run during HL | 4.85 |  | When dry - check isolation valves are correctly open/closed on both sites of river - NB to speak to TE NR to raise job - liase with LS to make sure he's there on same day |  |  | 2242051
14096 | Coxley Mill Lane SPS | W | 10.8 | 5.27 | 51.2% | Jan 23 Report |  | Compliant | 4496300% | 5.98 | 5.27 |  | Macerators unblocked, new plates installed on both pumps 16/12/22 y3 scheme - to be completed next week
15389 | Pawlett Main Road SPS | W | 19.2 | 10.9 | 43.23% | Jan 23 Report |  | At Risk | 4496300% | Pump RS not showing | Pump RS not showing |  | Site Specific Meeting Comment (31/1/23): Darren to check levels in storm tank/EDM spill level and where it comes from (storm tank or wet well?), raise stop and start levels and install low flow alert, get IFM checked/cleaned. LS to consider a trial pump to go into the storm tank to pump more flow forward when the storm tank is filling Jan 23 Comment: LS to investigate agaisnst Grundfos
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1 | 41.18% | Jan 23 Report |  | Compliant | 4496300% | P1 did not run during HL | 1 |  | y3 scheme - to be completed next few weeks
15318 | Stoford Hillside Main SPS | W | 36 | 22.1 | 38.61% | Jan 23 Report |  | Compliant | 4496300% | 22.1 | 22.3 |  | Being modelled by ESD No further actions done yet - RG to speak with Kieron
15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 9.64 | 35.73% | Jan 23 Report |  | Compliant | 4496300% | 9.64 | 9.68 |  | Nov 22 Comment:New impellors have been ordered. HT to raise job
14328 | Hanging Langford . SPS | S | 12 | 8.99 | 25.08% | Jan 23 Report |  | DWEF Compliant | 4496300% | 9.19 | 8.99 |  | Nov 22 Comment:LS: Early 2023 attend and replace both impellers and wear plates to re test and find the best possible pumped forward flow at normal operating levels and top water level. Re-test site and produce system curve now the RM is clean.
14311 | Tilshead, Camp Road SPS | S | 12 | 9.17 | 23.58% | Jan 23 Report |  | DWEF Compliant | 4496300% | 9.33 | 9.17 |  | Y3 capital maintenance scheme
15322 | Pitney . SPS | W | 5.3 | 4.1 | 22.64% | Jan 23 Report |  | Compliant | 4496300% | 3.82 | 4.1 |  | y3 scheme - waiting for civil work update from MH
15235 | SHORE ROAD POOLE | S | 90 | 71.29 | 20.79% | Jan 23 Report |  | At Risk | 4496300% | 71.29 | P2 did not run during HL | 73.26 | Dec 22 Comment:RG arranged meeting for Jan to discuss with HT/LS/AB
15158 | OLVESTON THE COMMON SPS | N | 21 | 17.18 | 18.19% | Jan 23 Report |  | DWEF Compliant | 4496300% | P1 did not run during HL | 17.18 |  | LS to fit new pump
14116 | GURNEY SLADE SPS | W | 7 | 5.86 | 16.29% | Jan 23 Report |  | At Risk | 4496300% | 5.86 | 5.86 |  | y3 scheme - AS installing early April Site still running duty/assist - out of consent
14414 | Charminster North Street SPS | S | 45 | 37.85 | 15.89% | Jan 23 Report |  | DWEF Compliant | 4496300% | 37.85 |  |  | Nov 22 Comment:HT to visit site and investigate. NR and EW to look at consent and how it works with 13033. Outstanding maintenance, so look at what flow does once this is finished
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 6.74 | 15.75% | Jan 23 Report |  | At Risk | 4496300% | 6.74 | 6.76 |  | this will need a scheme, new uprated MCC to allow bigger pump, 3171 273 impellor to achieve PFF and keep main cleansed LS to investigate adding a booster
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 292.21 | 15.3% | Jan 23 Report |  | Compliant | 4496300% | P1 did not run during HL | 292.12 | 292.12 | Nov 22 Comment:Awaiting RM scheme
15400 | Bridgwater West Quay SPS | W | 206 | 176.85 | 14.15% | Jan 23 Report |  | At Risk | 4496300% | 185.63 | 185.63 | 176.85 | pumps have been trimmed by Adam Separate out 3 signals from combined
15645 | PILL AVON ROAD SPS | W | 80 | 70.15 | 12.31% | Jan 23 Report |  | Compliant | 4496300% | 70.15 | 75.69 |  | y3 scheme
14413 | Chideock Seatown | S | 9.7 | 8.51 | 12.27% | Jan 23 Report |  | At Risk | 4496300% | 8.57 | 8.51
14097 | Baltonsborough Baltonsborough Main SPS | W | 17 | 14.98 | 11.88% | Jan 23 Report |  | Compliant | 4496300% | 14.98 | P2 did not run during HL |  | air valve has installed in NRV chamber (7/2/23) will need to monitor for drop in flow in wet weather AP to raise job for P2
14420 | Minehead Quay West | W | 14 | 12.41 | 11.36% | Jan 23 Report |  | At Risk | 4496300% | 12.41 |  |  | will monitor as nneds full sump to get max flow
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.13 | 11.25% | Jan 23 Report |  | Compliant | 4496300% | 2.13 | P2 did not run during HL |  | y3 scheme - delivered next 2 months
15233 | Poole Wilderton Road | S | 350 | 311.69 | 10.95% | Jan 23 Report |  | Compliant | 4496300% | 155 | P1&P2&P3 = 311.69
14082 | Street Main SPS | W | 190 | 171.88 | 9.537% | Jan 23 Report |  | Compliant | 4496300% | P1 did not run during HL | 171.88 | P3 did not run during HL | this has been resolved on site - AP to raise job to look at 2 pumps not running together
14386 | Greinton Moor Drive SPS | W | 34 | 30.79 | 9.441% | Jan 23 Report |  | At Risk | 4496300% | 30.79 | 31.01 |  | HW's team looking at it
14095 | Glastonbury Porchestall SPS | W | 200 | 181.3 | 9.35% | Jan 23 Report |  | At Risk | 4496300% | 190.67 | Storm pump 1: 190.67 | Storm pump 2 = 190.67 | needs new MCC to allow control changes in philosophy Wait until RM is replaced in June/July 2023
13153 | Holton Heath Holton Heath SPS SPS | S | 20 | 18.19 | 9.05% | Jan 23 Report |  | DWEF Compliant | 4496300% | 18.19 | 18.38 |  | Nov 22 Comment:Maintenance. HT to raise job for pumps to be trimmed etc.
14431 | Bishop Sutton . SPS | N | 19.6 | 18.22 | 7.041% | Jan 23 Report |  | At Risk | 4496300% | 18.22 | P2 did not run during HL |  | Damian's team (possible also R&M) to investigate air valve by chip shop [Mon/Tue/Wed - in school term time] - temporary air valve to check it works RG to arrange
14391 | Stoke St Gregory No 1 Lane End | W | 27 | 25.1 | 7.037% | Jan 23 Report |  | Compliant | 4496300% |  | 13.07 | Storm flow = 12.03 | needs full sump to get max flow AP to look into pump maintenance - checking impellors
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 12.58 | 6.815% | Jan 23 Report |  | At Risk | 4496300% | 12.58 | 14.01 |  | LS was looking at different impellor for this site - P1 airlocked/blocked & 2 bursts in January - Wait until wet weather and monitor then | RG
15257 | Poole Bridge Poole Quay | S | 15 | 14.02 | 6.533% | Jan 23 Report |  | Compliant | 4496300% | 14.8 | 14.02 |  | Nov 22 Comment:HT to raise job for pump maintenance
14265 | Upton Moorlands Way | S | 45 | 42.45 | 5.667% | Jan 23 Report |  | At Risk | 4496300% | 42.45 | P2 did not run during HL |  | Nov 22 Comment:HT to raise job for pump maintenance
15314 | Upton near Langport | W | 5 | 4.72 | 5.6% | Jan 23 Report |  | At Risk | 4496300% |  |  |  | pumps in to common main AP and LS to look into diverting flow from Wagg Drove (Discharge from RM into Gravity Main) - RG to speak to Steve
15278 | BENNETTS ORCHARD SPS | W | 7.8 | 7.41 | 5% | Jan 23 Report |  | Compliant | 4496300% | Storm pump: 7.41 |  |  | as above
14372 | West Huntspill Sloway Lane | W | 130 | 123.86 | 4.723% | Jan 23 Report |  | Compliant | 4496300% |  | 123.86 | 123.86 | Aug23: snore cycle now fixed, pumps previously air locking due to falut on low level sensor in wet well. Monitor over the next month. maintenace done 14/2/23 - pumps trimmed
14371 | FROGLAND CHEDDAR | W | 48 | 45.82 | 4.542% | Jan 23 Report |  | Compliant | 4496300% | 46.02 | 45.82 |  | please check when flow dropped off could be due to S2000 install
14266 | Wareham Sandford Lane SPS | S | 60 | 57.47 | 4.217% | Jan 23 Report |  | At Risk | 4496300% | 57.47 | 56.89 |  | monitor site
15516 | Bilbrook . SPS | W | 4 | 3.87 | 3.25% | Jan 23 Report |  | Compliant | 4496300% | 3.87 | 3.88 |  | looks ok on trend 9lps
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 359.19 | 2.922% | Jan 23 Report |  | DWEF Compliant | 4496300% | 359.19 | 362.57 |  | monitor site
14185 | MALMESBURY ST JOHNS | N | 60 | 58.36 | 2.733% | Jan 23 Report |  | DWEF Compliant | 4496300% | 29.24 | 29.12 |  | monitor site - check after pump maintenance (NSD 26/02/23)
13273 | Shipton Gorge Off Markets Lane SPS | S | 6.3 | 6.13 | 2.698% | Jan 23 Report |  | Compliant | 4496300% | P1 did not run during HL | 6.13 |  | will raise job to get impellors cchecked
14083 | West Pennard Havyatt SPS | W | 8.1 | 7.92 | 2.222% | Jan 23 Report |  | Compliant | 4496300% | 7.92 | P2 did not run during HL |  | maintenace due will get pumps trimmed
15311 | Yeovil Mudford SPS | W | 9.3 | 9.1 | 2.151% | Jan 23 Report |  | Compliant | 4496300% | 9.37 | 9.1 |  | please check when flow dropped off could be due to S2000 install
14415 | LITTON CHENEY CHICKSBRIDGE SPS | S | 5.3 | 5.22 | 1.509% | Jan 23 Report |  | Compliant | 4496300% | P1 did not flow during HL | 5.22 |  | monitor site
15075 | Corfe Mullen Pardys Hill SPS | S | 42 | 41.56 | 1.048% | Jan 23 Report |  | At Risk | 4496300% | 41.56 | 42.44 |  | looks ok on trend 9lps
15449 | Meare Green Wrantage SPS | W | 1 | 0.99 | 1% | Jan 23 Report |  | Compliant | 4496300% | 0.99 | 0.99 |  | monitor site
14216 | Stoborough Kings Arms | S | 15.3 | 15.19 | 0.719% | Jan 23 Report |  | Compliant | 4496300% | 15.19 | 15.88 |  | monitor site
15334 | CHARLTON ADAM | W | 21 | 20.86 | 0.6667% | Jan 23 Report |  | Compliant | 4496300% |  |  |  | will raise job to get impellors cchecked
14202 | Hankerton Bridge SPS | N | 42 | 41.73 | 0.6429% | Jan 23 Report |  | DWEF Compliant | 4496300% | 41.73 | 48.41 |  | -
14147 | Chippenham Westmead SPS | N | 155 | 109.68 | 29.24% | Jan 23 Report |  | At Risk | 4496300% | Storm Pump 1&2: 109.68 | Storm Pump 1&3: 114.49 |  | Dec 22 Comment:Flow currently being held back due to pressure/velocity in the rising main - considering increasing the flow and monitoring Jan 23: Need a control philosophy for the new panel - DD and RG to visit site
15111 | All Cannings . SPS | N | 8.5 | 4.81 | 43.41% | Jan 23 Report |  | DWEF Compliant | 4496300% | 4.81 | P2 did not run during HL |  | RG to speak to Brian about mapping of the new RM Check new air valves, do maintenance on pumps and review
15389 | Pawlett Main Road SPS | W | 19.2 | 12 | 37.5% | Site specific meeting |  | At Risk | 4495700% | 12 | 12 |  | Darren to check levels in storm tank/EDM spill level and where it comes from (storm tank or wet well?), raise stop and start levels and install low flow alert, get IFM checked/cleaned. LS to consider a trial pump to go into the storm tank to pump more flow forward when the storm tank is filling
15090 | West Parley Church Lane | S | [6 empty] | 4495500% |  |  |  | Panel for yr5, Luke S to suggest pumps, Separate meeting with CM/LS, RG to check FM operation. LS to do some testing on RM's
15100 | North Newnton . SPS | N | 10 | 5.34 | 46.6% | Dec 22 Report |  | DWEF Compliant | 4493200% | 5.34 | 5.53 |  | Luke's team to test pumps Tim/Damian - to complete overdue AV maintenance. Possible restriction in rising main under river?
14467 | Holt the Star | N | 100 | 23 | 77% | Dec 22 Report |  | Not currently assessed | 4493200% |  |  |  | Consent is wrong, historically. 2 different sized pumps currently installed. Neither achieves SCV. New rising main (+ flow meter) due to be installed Sept 2023. Look to trial new pump on completion and reproduce system curve. Review spill rate with trial pump. If successful, get site repermitted and install 2no. pumps. Look to achieve SCV - aim for 24 l/s. DD to check panel for both pumps to see if they can take 2x bigger pumps. LS recommendation is HT 3153, but re-test with new rising main.
15622 | Clevedon Marine Parade | W | 42 | 11.47 | 72.69% | Dec 22 Report |  | Not currently assessed | 4493200% | VDT = 11.47 | VDT = 11.52 |  | Site to be left alone for now: AM - 2022 investigation, 0 spills in recent years, highest level reached in c3 years is 0.77m vs spill level of 3.21m. Overflow should never spill in storm so PumpFF permit limit is irrelevant.
14096 | Coxley Mill Lane SPS | W | 10.8 | 5.14 | 52.41% | Dec 22 Report |  | Compliant | 4493200% | 5.85 | 5.14 |  | Y3 capital maintenance scheme
14311 | Tilshead, Camp Road SPS | S | 12 | 6.52 | 45.67% | Dec 22 Report |  | DWEF Compliant | 4493200% | 6.52 | 9.61 |  | Y3 capital maintenance scheme
15318 | Stoford Hillside Main SPS | W | 36 | 22.1 | 38.61% | Dec 22 Report |  | Compliant | 4493200% | 22.1 | 22.3
15389 | Pawlett Main Road SPS | W | 19.2 | 12 | 37.5% | Dec 22 Report |  | At Risk | 4493200% | Pump RS not showing | Pump RS not showing |  | Hidrostall pumps currently installed. Can't achieve PFF with these. LS to measure dry well and consider what Flygt pumps could be installed & panel limitations
15158 | OLVESTON THE COMMON SPS | N | 21 | 14.09 | 32.9% | Dec 22 Report |  | DWEF Compliant | 4493200% | 14.09 | 17.06
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.15 | 32.35% | Dec 22 Report |  | Compliant | 4493200% | P1 did not run during HL | 1.15
15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 10.63 | 29.13% | Dec 22 Report |  | Compliant | 4493200% | 10.63 | 10.63
15322 | Pitney . SPS | W | 5.3 | 4.15 | 21.7% | Dec 22 Report |  | Compliant | 4493200% | P1 did not run during HL | 4.15
14328 | Hanging Langford . SPS | S | 12 | 9.51 | 20.75% | Dec 22 Report |  | DWEF Compliant | 4493200% | 10.09 | 9.51
15233 | Poole Wilderton Road | S | 350 | 278.7 | 20.37% | Dec 22 Report |  | Compliant | 4493200% | 183 | P1&P2&P4 = 274.87
14428 | Corston Newton St Loe | N | 23.5 | 18.9 | 20% | Dec 22 Report |  | Not currently assessed | 4493200% |  |  |  | LS to trial pump and review flows/pressure when Midland Road is pumping at the higher head
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 6.69 | 16.37% | Dec 22 Report |  | At Risk | 4493200% | 6.69 | 6.84
14414 | Charminster North Street SPS | S | 45 | 37.8 | 16% | Dec 22 Report |  | DWEF Compliant | 4493200% | 37.8 | 38.65
15235 | SHORE ROAD POOLE | S | 90 | 77 | 14% | Dec 22 Report |  | At Risk | 4493200% |  |  | 76.65 | RG arranged meeting for Jan to discuss with HT/LS/AB
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 301.1 | 12.72% | Dec 22 Report |  | Compliant | 4493200% | P1 did not run during HL | 301.1 | 301.1
14202 | Hankerton Bridge SPS | N | 42 | 37.35 | 11.07% | Dec 22 Report |  | DWEF Compliant | 4493200% | 37.35 | 42.57
15645 | PILL AVON ROAD SPS | W | 80 | 71.86 | 10.18% | Dec 22 Report |  | Compliant | 4493200% | P1 did not run during HL | 71.86
14216 | Stoborough Kings Arms | S | 15.3 | 13.75 | 10.13% | Dec 22 Report |  | Compliant | 4493200% | 13.75 | 14.75
14095 | Glastonbury Porchestall SPS | W | 200 | 181.3 | 9.35% | Dec 22 Report |  | At Risk | 4493200% | 181.3 | 181.3 | 181.3
15313 | HUISH EPISCOPI PIBSBURY | W | 1.4 | 1.27 | 9.286% | Dec 22 Report |  | Compliant | 4493200% | 1.27 | 1.56
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 12.25 | 9.259% | Dec 22 Report |  | At Risk | 4493200% | 12.41 | 12.25
15400 | Bridgwater West Quay SPS | W | 206 | 188 | 8.738% | Dec 22 Report |  | At Risk | 4493200% | 188 |  | 188
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 337.97 | 8.657% | Dec 22 Report |  | DWEF Compliant | 4493200% | 340.28 | 337.97
13153 | Holton Heath Holton Heath SPS SPS | S | 20 | 18.44 | 7.8% | Dec 22 Report |  | DWEF Compliant | 4493200% | 18.44 | 18.8
14266 | Wareham Sandford Lane SPS | S | 60 | 56.4 | 6% | Dec 22 Report |  | At Risk | 4493200% | 56.4 | P2 did not run during HL
14116 | GURNEY SLADE SPS | W | 7 | 6.65 | 5% | Dec 22 Report |  | At Risk | 4493200% | 6.65 | 6.65
15257 | Poole Bridge Poole Quay | S | 15 | 14.5 | 3.333% | Dec 22 Report |  | Compliant | 4493200% | P1 did not run during HL | 14.5
15311 | Yeovil Mudford SPS | W | 9.3 | 9 | 3.226% | Dec 22 Report |  | Compliant | 4493200% | 9.25 | 9
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.34 | 2.5% | Dec 22 Report |  | Compliant | 4493200% | P1 did not run during HL | 2.34
15075 | Corfe Mullen Pardys Hill SPS | S | 42 | 41.2 | 1.905% | Dec 22 Report |  | At Risk | 4493200% | 41.51 | 41.2
14374 | Highbridge Newton SPS | W | 300 | 297 | 1% | Dec 22 Report |  | At Risk | 4493200%
15278 | BENNETTS ORCHARD SPS | W | 7.8 | 7.73 | 0.8974% | Dec 22 Report |  | Compliant | 4493200% | Storm pump: 7.73
15317 | NORTON SUB HAMDON SPS | W | 15.4 | 15.35 | 0.3247% | Dec 22 Report |  | At Risk | 4493200% | 16.4 | 15.35
14147 | Chippenham Westmead SPS | N | 155 | 104.5 | 32.58% | Dec 22 Report |  | At Risk | 4493200% | Storm Pump 1&2: 104.5 | Storm Pump 1&3: 116.2 |  | Flow currently being held back due to pressure/velocity in the rising main - considering increasing the flow and monitoring
15111 | All Cannings . SPS | N | 8.5 | 7.2 | 15.29% | Dec 22 Report |  | DWEF Compliant | 4493200%
14096 | Coxley Mill Lane SPS | W | 10.8 | 5.6 | 48.15% | Nov 22 Report |  |  | 4490400% | 5.6 | 4.9 |  | Y3 scheme. AP to raise job for Sam to replace rotors and stators until scheme is delivered. Same pumps as at Kilmersdon
15389 | Pawlett Main Road SPS | W | 19.2 | 11 | 42.71% | Nov 22 Report |  |  | 4490400% | Pump RS not showing | Pump RS not showing |  | With West SPS team to resolve run stop signals - should resolve when S2000 is installed in the next few months. LS to check flowmeter is verified. Open job to be completed. Review next month
15318 | Stoford Hillside Main SPS | W | 36 | 23.6 | 34.44% | Nov 22 Report |  |  | 4490400% | 23.6 | 23.8 |  | Being modelled by ESD
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.14 | 32.94% | Nov 22 Report |  |  | 4490400% | P1 did not run during HL | 1.14 |  | y3 scheme. Under duty/assist until scheme is finished
15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 10.1 | 32.67% | Nov 22 Report |  |  | 4490400% | 10 | 10.1 |  | New impellors have been ordered. HT to raise job
15322 | Pitney . SPS | W | 5.3 | 4.1 | 22.64% | Nov 22 Report |  |  | 4490400% | P1 did not run during HL | 4.1 |  | y3 scheme.
14067 | Bitton . SPS | N | 14.85 | 11.5 | 22.56% | Nov 22 Report |  |  | 4490400% | 11.5 | 21.5
15233 | Poole Wilderton Road | S | 350 | 278.7 | 20.37% | Nov 22 Report |  |  | 4490400% | Pump 1 hasn't run - check | 149.3 | 130 - pump 4, 156.8 - pump 3
14328 | Hanging Langford . SPS | S | 12 | 10 | 16.67% | Nov 22 Report |  |  | 4490400% | 10 | 10 |  | LS: Early 2023 attend and replace both impellers and wear plates to re test and find the best possible pumped forward flow at normal operating levels and top water level. Re-test site and produce system curve now the RM is clean.
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 6.7 | 16.25% | Nov 22 Report |  |  | 4490400% | 6.7 | 6.7 |  | AP to send details of pump and panel to NR and MH for y4 scheme
14202 | Hankerton Bridge SPS | N | 42 | 36.2 | 13.81% | Nov 22 Report |  |  | 4490400% | 36.2 | 40.6
14414 | Charminster North Street SPS | S | 45 | 38.8 | 13.78% | Nov 22 Report |  |  | 4490400% | 38.8 | Storm = 38.8 |  | HT to visit site and investigate. NR and EW to look at consent and how it works with 13033. Outstanding maintenance, so look at what flow does once this is finished
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.07 | 13.75% | Nov 22 Report |  |  | 4490400% | 2.11 | 2.07 |  | y3 scheme.
15278 | BENNETTS ORCHARD SPS | W | 7.8 | 6.8 | 12.82% | Nov 22 Report |  |  | 4490400% | Storm pump: 6.8 |  |  | VSD being ammended to new target flow of 7bar. RG reviewing Upton Pibsbury and Wagg Drove to see if we can amend any of these sites to achive higher flows at Bennets Orchard. Meeting 12/01/2023 to further discuss changing flows for RM system
15400 | Bridgwater West Quay SPS | W | 206 | 182 | 11.65% | Nov 22 Report |  |  | 4490400% | 182 |  | 182 | EJ to check flows after pump maintenance tomorrow (13/12)
13153 | Holton Heath Holton Heath SPS SPS | S | 20 | 17.7 | 11.5% | Nov 22 Report |  |  | 4490400% | 17.7 | 17.7 |  | Maintenance. HT to raise job for pumps to be trimmed etc.
15715 | Bridgwater Horsey Bath Road SPS | W | 54 | 48.9 | 9.444% | Nov 22 Report |  |  | 4490400% | 48.9 |  | 48.9
15002 | Boscombe No 1 SPS | S | 45 | 41 | 8.889% | Nov 22 Report |  |  | 4490400% | 41 | P2 did not run during HL |  | Tested to do 48 l/s. Monitor
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 318.5 | 7.681% | Nov 22 Report |  |  | 4490400% | P1 did not run during HL | 318.6 | 318.6 | Awaiting RM scheme
15311 | Yeovil Mudford SPS | W | 9.3 | 8.6 | 7.527% | Nov 22 Report |  |  | 4490400% | 9 | 8.6 |  | Rising main changed recently, so EJ to monitor flows over next month, AP to consider changing motors if flows still non-compliant
15645 | PILL AVON ROAD SPS | W | 80 | 74 | 7.5% | Nov 22 Report |  |  | 4490400% |  | 74 |  | y3 scheme
15313 | HUISH EPISCOPI PIBSBURY | W | 1.4 | 1.3 | 7.143% | Nov 22 Report |  |  | 4490400% | 1.3 | 1.6 |  | See Bennetts Orchard. Meeting 12/01/2023 to further discuss changing flows for RM system
15158 | OLVESTON THE COMMON SPS | N | 21 | 19.6 | 6.667% | Nov 22 Report |  |  | 4490400% | 13.5 | 19.6
14227 | Studland Wadmore Lane | S | 11 | 10.3 | 6.364% | Nov 22 Report |  |  | 4490400% | P1 did not run during HL | 10.3 |  | Getting in a new pump.
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 351 | 5.135% | Nov 22 Report |  |  | 4490400% | 351 |  |  | EJ compiling LEP - looking at penstocks and valve complexes. HT will then look at increasing speeds
14431 | Bishop Sutton . SPS | N | 19.6 | 18.6 | 5.102% | Nov 22 Report |  |  | 4490400% | P1 did not run during HL | 18.6
14095 | Glastonbury Porchestall SPS | W | 200 | 190 | 5% | Nov 22 Report |  |  | 4490400% | 190 | 190 | 190 | Has been shown to do 204l/s, AP to amend relay configuration during wet weather
15190 | Milborne St Andrew Manor Farm SPS | S | 47 | 44.8 | 4.681% | Nov 22 Report |  |  | 4490400% | P2 - 18.6 | 26.2 |  | Tested to do around 60l/s. EJ to look whether we're getting these flows on Prism
14266 | Wareham Sandford Lane SPS | S | 60 | 57.2 | 4.667% | Nov 22 Report |  |  | 4490400% | 58.8 | 57.2 |  | HT to raise job for pump maintenance
14386 | Greinton Moor Drive SPS | W | 34 | 33.1 | 2.647% | Nov 22 Report |  |  | 4490400% | P1 did not run during HL | 33.1 |  | Meeting 12/01/2023 to further discuss changing flows for RM system
14265 | Upton Moorlands Way | S | 45 | 44.1 | 2% | Nov 22 Report |  |  | 4490400% | 43.3 | 44.1 |  | HT to raise job for pump maintenance
15257 | Poole Bridge Poole Quay | S | 15 | 14.8 | 1.333% | Nov 22 Report |  |  | 4490400% | P1 did not run during HL | 14.8 |  | HT to raise job for pump maintenance
15317 | NORTON SUB HAMDON SPS | W | 15.4 | 15.2 | 1.299% | Nov 22 Report |  |  | 4490400% | 15.2 | P2 did not run during HL |  | EJ to monitor. VSDs keeping flows around 15.2
14379 | Fiddington SPS | W | 5.3 | 5.25 | 0.9434% | Nov 22 Report |  |  | 4490400% |  |  |  | Job on systsem to rebuild one of the rotors
14621 | PORTISHEAD TOWN HARBOUR | W | 260 | 259.9 | 0.03846% | Nov 22 Report |  |  | 4490400% |  |  |  | Impellors have been replaced, should be reaching consent now
15237 | Poole Magna Road SPS | S | 100 |  |  | Nov 22 Report |  |  | 4490400% |  |  |  | HT to raise job for shut down for dry well changes
14147 | Chippenham Westmead SPS | N | 155 | 111.3 | 28.19% | Nov 22 Report |  |  | 4490400% | Storm Pump 1&3: 111.3
14067 | Bitton . SPS | N | 14.85 | 11.5 | 22.56% | Dec 22 Report |  |  | 4489100% | 11.5 | 21.5
14096 | Coxley Mill Lane SPS | W | 10.8 | 5.9 | 45.37% | Oct 22 Report |  |  | 4485900% | 5.9 | 5.4 |  | Y3 capital maintenance scheme
15389 | Pawlett Main Road SPS | W | 19.2 | 11 | 42.71% | Oct 22 Report |  |  | 4485900% | NO RS coming through | NO RS coming through |  | With Mechanical Optimisation Team to investigate/carry out pump testing. EJ to raise IT ticket to try to resolve the pump RSs. Pass to AP if this doesn't solve the issue
15158 | OLVESTON THE COMMON SPS | N | 21 | 14.2 | 32.38% | Oct 22 Report |  |  | 4485900% | 13.8 | 14.2 |  | Plan to test site with upsized pump, temporary panel witih VSD on the 22nd Nov
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.19 | 30% | Oct 22 Report |  |  | 4485900% | P1 did not run during HL | 1.19 |  | y3 scheme
15318 | Stoford Hillside Main SPS | W | 36 | 25.4 | 29.44% | Oct 22 Report |  |  | 4485900% | 25.1 | 25.4 |  | Under permit review with modelling team, LS and AP looking at options with pumps and RM: DS and team – look to clear up the differences between the model and observed, then attempt this: Derive forecast spill freq / vols from an ‘as permit’ model And forecast spill freq / vols from an ‘as is’ model with the replaced storage included but the ‘low’ PFF retained As long as the spill freq / vols in either scenario are similar, EA should be willing to issue a revised permit. AP and LS – look into the costs and practicality, at a high level, of upsizing the rising main and pumps; and look into the flows coming from Bradford Abbas, CT – carry on with the new storage option unless the results of the above suggest a better way forward at some point.
14067 | Bitton . SPS | N | 14.85 | 11.7 | 21.21% | Oct 22 Report |  |  | 4485900% | 11.7 | 22.3
15322 | Pitney . SPS | W | 5.3 | 4.2 | 20.75% | Oct 22 Report |  |  | 4485900% | P1 did not run during HL | 4.2 |  | y3 scheme
14202 | Hankerton Bridge SPS | N | 42 | 34.2 | 18.57% | Oct 22 Report |  |  | 4485900% | 34.2 | 39.1
14414 | Charminster North Street SPS | S | 45 | 40.9 | 9.111% | Oct 22 Report |  |  | 4485900% | 40.9 | Storm = 40.9
14431 | Bishop Sutton . SPS | N | 19.6 | 18 | 8.163% | Oct 22 Report |  |  | 4485900% | 18 | P2 did not run during HL
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S | 345 | 318.5 | 7.681% | Oct 22 Report |  |  | 4485900% | P1 did not run during HL | 318.6 | 318.6
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 343 | 7.297% | Oct 22 Report |  |  | 4485900% | 343 | 327
15645 | PILL AVON ROAD SPS | W | 80 | 74.4 | 7% | Oct 22 Report |  |  | 4485900% | NO RS coming through | NO RS coming through |  | y3 scheme
15311 | Yeovil Mudford SPS | W | 9.3 | 8.8 | 5.376% | Oct 22 Report |  |  | 4485900% | 9.1 | 8.8 |  | Awaiting RM replacement, connections on 29th Nov
15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 14.3 | 4.667% | Oct 22 Report |  |  | 4485900% | 14.3 | 14.3
14266 | Wareham Sandford Lane SPS | S | 60 | 57.2 | 4.667% | Oct 22 Report |  |  | 4485900% | 58.8 | 57.2
15400 | Bridgwater West Quay SPS | W | 206 | 197.1 | 4.32% | Oct 22 Report |  |  | 4485900% | 195.6 | 195.6 | Storm = 195.6 | New impellors installed on DWF pumps in March, EJ to work out dry weather equivilent flow and discuss with NR and RG to monitor on Amulet etc.
15002 | Boscombe No 1 SPS | S | 45 | 43.3 | 3.778% | Oct 22 Report |  |  | 4485900% | 43.3 | P2 did not run during HL
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.32 | 3.333% | Oct 22 Report |  |  | 4485900% | P1 did not run during HL | 2.32 |  | y3 scheme
14095 | Glastonbury Porchestall SPS | W | 200 | 194 | 3% | Oct 22 Report |  |  | 4485900% | 194 | Storm P2 = 194 | Storm P3 = 194 | AP and RG to discuss (consider looking at setpoints for assist pump), also awaiting survey of network between SPS and CSO (in Jan), look at spills from upstream site as well, NR to speak with EW about validating levels at 16514 EDM
14227 | Studland Wadmore Lane | S | 11 | 10.7 | 2.727% | Oct 22 Report |  |  | 4485900% | P1 did not run during HL | 10.7 |  | 3102 recommended bY LS's team as a trial - P1. Installed 04/11/22. Monitor through November
15278 | BENNETTS ORCHARD SPS | W | 7.8 | 7.6 | 2.564% | Oct 22 Report |  |  | 4485900% | NO RS coming through | NO RS coming through |  | JH to raise job to increase RPM of storm pump and monitor |  |  | 2175262
14147 | Chippenham Westmead SPS | N | 155 | 112 | 27.74% | Oct 22 Report |  |  | 4485900% | Storm Pump 1&3: 122
15320 | Long Sutton Knole | W | 2.8 | 2.6 | 7.143% | Sept 22 Report |  |  | 4483300% | P1 did not run during HL | 2.6
15400 | Bridgwater West Quay SPS | W | 206 | 197.1 | 4.32% | Sept 22 Report |  |  | 4483300% | 197.1 | 197.1 | P3 did not run during HL
14096 | Coxley Mill Lane SPS | W | 10.8 | 6.4 | 40.74% | Sept 22 Report |  |  | 4483000% | 6.4 | 6.5 |  | y3 scheme
14067 | Bitton . SPS | N | 14.85 | 11.5 | 22.56% | Sept 22 Report |  |  | 4483000% | 11.5 | P2 did not run during HL
14431 | Bishop Sutton . SPS | N | 19.6 | 18.2 | 7.143% | Sept 22 Report |  |  | 4483000% | P1 did not run during HL | 18.2
14202 | Hankerton Bridge SPS | N | 42 | 33.9 | 19.29% | Sept 22 Report |  |  | 4482700% | P1 did not run during HL | 35.3
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.25 | 26.47% | Sept 22 Report |  |  | 4482100% | P1 did not run during HL | 1.25
14095 | Glastonbury Porchestall SPS | W | 200 | 117.4 | 41.3% | Sept 22 Report |  |  | 4481700% | 117.4 | 117.4 (Storm pump 2) |  | Y4 scheme
14414 | Charminster North Street SPS | S | 45 | 41.2 | 8.444% | Sept 22 Report |  |  | 4481400% | P1 did not run during HL | 41.2 |  | LS to retest
15318 | Stoford Hillside Main SPS | W | 36 | 25 | 30.56% | Sept 22 Report |  |  | 4481300% | 25 | 25.2
15322 | Pitney . SPS | W | 5.3 | 4.2 | 20.75% | Sept 22 Report |  |  | 4481300% | 4.2 | P2 did not run during HL
14227 | Studland Wadmore Lane | S | 11 | 10.3 | 6.364% | Sept 22 Report |  |  | 4481300% | 10.3 | 10.3 |  | New trial pumps to be installed tomorrow 21/10
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.32 | 3.333% | Sept 22 Report |  |  | 4481300% | P1 did not run during HL | 2.32
15190 | Milborne St Andrew Manor Farm SPS | S | 47 | 20.5 | 56.38% | Sept 22 Report |  |  | 4481200% | P1 - 20.5 | Storm Pump has not run in a while - reading 0 |  | Flow measured 57 l/s on 21/10. Therefore is likely to be within consent. Storm pump hadn't run for a few months before 2/20, only runs under very extreme rainfall. EJ will continue to monitor
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 12.4 | 8.148% | Sept 22 Report |  |  | 4481200% | 12.4 | P2 did not run during HL
15075 | Corfe Mullen Pardys Hill SPS | S | 42 | 39 | 7.143% | Sept 22 Report |  |  | 4481200% | 39 | 45.9 |  | HT to look at next week. Maintenance due March
15002 | Boscombe No 1 SPS | S | 45 | 44 | 2.222% | Sept 22 Report |  |  | 4481200% | 44 | P2 did not run during HL |  | HT to arrange hydrostall to maintain pumps
14147 | Chippenham Westmead SPS | N | 155 | 120 | 22.58% | Sept 22 Report |  |  | 4481000% | Storm Pump 1: 120
15158 | OLVESTON THE COMMON SPS | N | 21 | 14.2 | 32.38% | Sept 22 Report |  |  | 4480900% | 14.2 | 14.7
14328 | Hanging Langford . SPS | S | 12 | 10.6 | 11.67% | Sept 22 Report |  |  | 4480900% | P1 did not run during HL | 10.6 |  | RG and EJ to investigate flows. Then to raise captial scheme to address panel and optimising pump configuration
14404 | Beaminster Southgate SPS | S | 31 | 27.6 | 10.97% | Sept 22 Report |  |  | 4480900% | 27.6 | 30.8 |  | EJ to recheck flows for recent weeks
15645 | PILL AVON ROAD SPS | W | 80 | 73.6 | 8% | Sept 22 Report |  |  | 4480900% | P1 did not run during HL | 73.6
14252 | Studland Combe | S | 16.2 | 15 | 7.407% | Sept 22 Report |  |  | 4480900% | P1 did not run during HL | 15 |  | EJ to monitor during HL. Conserters - can be ramped up
14266 | Wareham Sandford Lane SPS | S | 60 | 58.1 | 3.167% | Sept 22 Report |  |  | 4480900% | 58.1 | 59.7 |  | Maintenance due Feb
14528 | CARLINGCOTT STONEAGE SPS | N | 50 | 48.5 | 3% | Sept 22 Report |  |  | 4480900% | 48.5 | 48.5
15495 | Netherbury Beaminster SPS | S | 3.8 | 3.7 | 2.632% | Sept 22 Report |  |  | 4480900% | 4.7 | 3.7 |  | Installing new motors in next few weeks
14621 | PORTISHEAD TOWN HARBOUR | W | 260 | 259.6 | 0.1538% | Sept 22 Report |  |  | 4480900% |  | 259.6= P4
15313 | HUISH EPISCOPI PIBSBURY | W | 1.4 | 1.26 | 10% | Sept 22 Report |  |  | 4479000% | 0.98 | P2 did not run during HL
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S | 370 | 337.4 | 8.811% | Sept 22 Report |  |  | 4479000% | 347.7 | 337.4 |  | EJ and RG to update LEP prior to increase in pump speed during storms
14386 | Greinton Moor Drive SPS | W | 34 | 30.2 | 11.18% | Sept 22 Report |  |  | 4478900% | 27.3 | 30.2
14311 | Tilshead, Camp Road SPS | S | 12 | 10.2 | 15% | Sept 22 Report |  |  | 4476400% | P1 Out of Action | 10.2 |  | Capital scheme to be devilered in y3
14256 | Affpuddle . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2
14337 | Alderbury Home Farm | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Neil carried out on site investigation/training 19/08/20, found to be compliant Flow meter installed 03/11/21
15088 | Alderholt Sandleheath Road | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Permit application made for CSO Andy Mears confirmed 43.6 l/s is the PFF that will be in the new permit Virtual drop test showed 17.9 l/s (P1) and 19.9 l/s for (P2)
14304 | Allington Old Inn SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flygt NP 3102 460 impeller, NP 3102 430 impeller, check pump asset details, check/adjust/shim pumps. With Sean Smith to look at pumps/impellers w/c 30/03/20
15189 | Aust Village | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Mono
13014 | AXBRDGE OLD | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flygt 3202 454 impellers, duty/standby, check pumps
15183 | Bagstone SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 13.7 l/s
14097 | Baltonsborough Baltonsborough Main SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Data suggests pump blockage history. P2 particularly poor performance - new pump fitted 08/08/19?? NO ASSET DATA. Carry out wet well clean, followed by mainteance and check pumps/impellers/NRVs, update asset details. NR received quote from Nige to change to Concertors. 13/02/20 further decrease in performance and the site is spilling. E-mail to Fred - Harry is going to arrange service exchange pump Pumps have arrived, installation has been chased 17/03/20. Pump 1 installed on 20/02/20. Concerter pumps ordered 30/03/20, installed 27/04/20, pumps achieving >16l/s
14354 | Barford St Martin . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 2018 drop test shows 6 l/s for pump 1 and 7.6 l/s for pump 2. Unable to perform virtual drop test due to irregular sump volume
15316 | Barton St David Tootal Bridge SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flow meter commissioning Dec-20. Site is not compliant (flow) & also running duty/assist and should have a standby pump. West in talks with Stuart Pugsley to improve the flow from the existing Monos.
16050 | Bath Ea Depot SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15435 | Bathpool Hyde Lane SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 18.1 l/s. May need checking as previous drop test from 2018 showed 42 l/s.
14404 | Beaminster Southgate SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Like for like impellers didn't improve flow, larger impellers on order from Workshop, being fitted by Harry Tucker w/c 01/02/21 (or as soon as arrive), also Swingcheck valves in place of the NRVs. AVs to be maintained w/c 01/02/21. New impellers and returned/refurbished pumps fitted on 25/02/21. Upsized impeller installed 20/03/21 which successfully produced compliant flow. 2nd impeller installed 08/04/21, both pumps compliant.
14397 | Beer Hackett SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flygt CT 3152 432 impeller. Check pumps. Dry well
15278 | BENNETTS ORCHARD SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | VSDs adjusted Jan-21 (increased speed), monitor. Storm pump needs tweaking.
14179 | BIDDESTONE MANOR COT | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Look at historic max flows, PPM history, pass to North / Sean to investigate on site. Flow meter is a clamp-on Flow Pulse. Could put a flow meter/portable flow meter in NRV chamber. Feedback from Luke Sturgeon - pumps achieving 11 and 8 l/s. P1 273 and P2 274 impellers - 8.1 l/s and 7.9 l/s, measured with Katronics flow meter. DD to re-calibrate the Pulsar flow meter w/c 15/11/21. P1 should be doing 10l/s. P2 should be doing 8.5 l/s. DD to look at swapping a pump in from Westerleigh SPS and/or maintaining P1 Flow meter needs calibrating
14431 | Bishop Sutton . SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Pumps produce PFF flow until main fully primed then drops off a bit, until WW level builds up. NRVs changed to Swingflex Dec-20, fit pressure logger in Jan-21, AV maintenance/re-install AV in March/April 2021. Bigger impellers (451) installed 11/10/21 Flow/pressure monitoring being installed in December - on completion, RG to analyse data and confirm if we should trial an AV being reinstated
15718 | Bishops Hull Shutemead | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Permit application made for CSO. Sean Smith & West team looking at 02/04/20 - new impellers to be fitted. Pre works P1 was delivering 8l/s & P2 delivering 6.5 l/s. Now with 245 impellers installed P1 is delivering 16.6 l/s and P2 15.8 l/s. The static head is 13.5 mtrs with a THD @ 16.6 l/s of 32 mtrs.
14067 | Bitton . SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | P1 not run since 14/12/2022, will check flows when it does run
15206 | Blandford Langton Road (Blandford No. 1) | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Area calculated by finding the area of trainlges then adding 1 l3 to compensate the curve. Duty/assist/standby, Flygt 3171 431 impellers. Check pumps, re-test duty/assist - do drop test to check flow
15573 | Bleadon Purn SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | P2 has recently been refurbished. P2 flowmeter now commissioned, pressure monitor is in situ but not commissioned yet. Pumps have a history of airlocking. Awaiting feedback/proposals from Mechanical Optimisation Team.
14423 | Blue Anchor Pill Bridge | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | OK no action
15002 | Boscombe No 1 SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flow meters installed 19/03/21 (not on Prism yet) - P1 24.3 l/s, P2 42.0 l/s. JJ returning w/c 05/04/21 to carry out pipework mods, check for grit, replace P1 with boxed spare
13389 | Bossington . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 8.9 l/s
15007 | Bournemouth Iford Lane Tuckton | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Impellers and NRVs replaced on P1 & P2 in June. Harry - the site has 3 pumps - 2 DWF & a bigger storm pump. Non of these 3 pumps can run as duty/assist.The DWF pumps both do around 55ls. The storm pump does 65-70ls at high level which I tested today Electrician completed job on 06/07/20, flows correctly recording now. Storm pump often gets air locked Scheme in for 2021/22 to reconfigure pumps, ideally duty/assist with VSDs, low spilling site
14235 | Bovington Duncan Crescent SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
19699 | Bovington Lytchett Lane SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14240 | Bovington Morris Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1.
14270 | Bovington Terminal SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 3. Pump 2 at 51 l/s, pump 1 at 36 l/s
15463 | Bradford On Tone Tone Green SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
13033 | Bradford Peverell Giles Cross | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pumps
14408 | Bradford Peverell SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flow meter to be installed by March/April 2021
14456 | Bratton Trowbridge Road | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 2no. Flygt 3127s, installed 2007. Pump test carried out by Neil Fletcher & Sean Smith 11/06/20
14272 | Briantspuddle . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1.
14378 | Bridgwater Blake Gardens | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | OK no action
15393 | Bridgwater Taunton Road | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Recent maintenance increased flow, history of blocked NRVs, changing to Swingflex, ok. Wet well needs to be in very high level to reach PFF
15400 | Bridgwater West Quay SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Review with Ash, Mark, Rich - what can we do here?
14385 | Bridgwater, Bristol Road SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | New chopper impellers awaiting fitting Installed 19/03/20
14384 | Bridgwater, Chilton St SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | OK no action
15415 | Bridgwater, Colley Lane SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | OK no action
15243 | Bridgwater, East Quay SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | OK no action
15507 | Bridport West Bay Sluices | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | OK no action
18710 | Bristol Royal Edward Dock | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Get flow meter fixed, confirm required PFF. This came from Andy Mears.
14581 | Bristol Victoria Road SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14583 | Bristol West Town Road SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 44 l/s
14475 | Broughton Gifford The Green SPS | N | [6 empty] | 4545500% |  |  |  | R&M Lining pipework before FM.on overlander at the mo 18th June2024
14475 | Broughton Gifford The Green SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | With Ops to carry out maintenance on pumps. Flow meter and pressure monitor currently not working correctly (Jan-22)
14410 | Burton Bradstock Burton Southover SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 14.5 l/s
15042 | Burton Stony Lane SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 18 l/s and pump 3 at 19 l/s
14152 | Calne Broads Green | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | PPM due 26/12/19 - NR generated WAM job early for PPM team to check impellers etc. Re-test afterwards. Luke carried out pump testing 30/04/21, flows 6 & 4.2 l/s. Check impellers.
14157 | Calne Rough Leaze | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 2no. Flygt 3171 SH pumps, installed 2017. Not sure what the flow meter on Prism is measuring/calculating (~6 l/s), sometimes unusual flow trend. There are 2 rising mains going to 2 different STWs, with a control valve directing flow. Usually 0-38% on the rising main with the flow meter. Tim E/Sean attending 02/06/20 - carried out maintenance on the pumps, flow increased up to 14.6 l/s. Looking at system/pump curves to check impellers/pumps next
15246 | CANFORD MAIN SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | P1 replaced with temporary hire pump 22/01/21
14528 | CARLINGCOTT STONEAGE SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Raised job for Damian/Tim to review (attending 06/07/20) - old C type Flygt pumps. Nick Buller asked Phil Bowen for pump/system curve info from rising main replacement scheme (2018), no info NRVs and valves replaced 23/07/20. Recent high level - flow is compliant (53 l/s) when P2&P3 run duty/assist, but 49 l/s (not quite in high level) when P1&P2 run duty/assist. Continue to monitor. DD to raise job for pumps to be lifted, impellers checked etc. P1 needs looking at, P3 run stops not archiving, outstation needs reconfiguring.....
15334 | CHARLTON ADAM | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Impellers have been changed, NRVs, flow monitor being installed 17/02/20. Pumps reviewed by Sean Aug-20 - could save 2kW with a more efficient pump. P2 not delivering consented flow on 16/05/2021.P1 able to deliver 22 l/s. Maintenance carried out 13/07/21, P1 ok, P2 non compliant, new impeller ordered, shimmed, back to compliant
14414 | Charminster North Street SPS | S | 45 |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | New impellers/insert rings fitted by South SPS team 22/01/21, flow increased to 41/42 l/s. Monitor in high level. With Mechanical Optimisation Team to recommend larger pumps (if these can be run from the current VSDs)
15441 | Cheddon Fitzpaine Cheddon Farm SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Suck and blow carried out on rising main 19/01/21, has history of fatting/gritting up. Increasing wet well cleaning to 3 monthly. With Ops - trialling a new super head pump but covers are too small. Civils work to get the pump in for regular maintenance. Monitor once new pump is installed.
14430 | Chew Magna Dumpers Lane | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Analyse flow / PFF - problem passing more forward - burst history on rising main. Scheme in 2020/2021 to update pumps & panel. Gerald to install pressure monitor. DD to increase speed of pumps when in high level for a trial
15630 | Chickerell Lower Way | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | P1 11.8 l/s, P2 14.5 l/s measured in recent flooding scheme survey, asked to confirm PFF at NRM (Tolulope Finnih) - pass to Flygts to investigate. Flygts maintained pumps and fedback flow rates - 15.8 & 14.3 l/s (Sept-20)
14413 | Chideock Seatown | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Find pump curves. Request maintenance - lift pumps, update asset data, check NRVs, ask Nigel (10/01/20) about pump/impellor change - the max flow in 2019 was 8.8 l/s. Further drop off in flow - e-mailed Fred (13/02/20) to see what's happening - Harry to attend w/c 17/02/20. Passed to Flygts to do w/c 2/3/20. Harry installed hire pumps 13/2/20 while we wait for new pumps.
14362 | Chilmark . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14232 | Church Knowle Animal Sanctuary SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 3 l/s
14226 | Church Knowle Glebe Farm SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 2.8 l/s
15621 | Clevedon Ladye Bay SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Neil and Sean carried out on site investigations 01/07/20, found to be compliant. Virtual drop test for June 21 shows 31 l/s for both pumps. Flow meter now installed. Should reach consented flow in high level
14495 | Clevedon Main | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Need to check set points for VSD speeds for the pumps in high level. Site hasn't spilt from the storm tank since Oct-21
15622 | Clevedon Marine Parade SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pumps. Site to be left as is for now - 2022 investigation, 0 spills in recent years, highest level reached in c3 years is 0.77m vs spill level of 3.21m. Overflow should never spill in storm so PumpFF permit limit is irrelevant.
15606 | Clevedon The Beach SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14425 | Clutton Greenbrook | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 2 storm pumps, 1 DWF sewage pump, D/S/A - 2 pumps not tested in duty/assist mode. 3 different pump types listed - Flygt CP 3201 (264 impeller), NP 3202 (452 impeller), NP 3171 (274 impeller). Changed impellers/wear plates/NRVs. P1 & 3 doing 57.1 l/s, P1 & 2 doing 54.7 l/s, P 2 & 3 doing 55.9 l/s (measured by Flygts after work)
14047 | Coate Spaniel's Bridge | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | N type 3127, 487 impellers - adjust/shim? Job 1682563 raised 14/07/20, completed 30/07/20 - both pumps underperforming
14432 | Compton Dando Turnbridge SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 2.9 l/s
14275 | Corfe Castle Halves Cottages SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14263 | Corfe Castle Red Lane SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 2.5 l/s
14276 | Corfe Castle Studland Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 25.5 l/s
14428 | Corston Newton St Loe | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 2no. Flygt 3127s. Refer to e-mail forwarded by Nick Buller about the consent at this site feeding into the Midland Road rising main. Not enough info for virtual drop test.
14450 | Coulston | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Mono AC1 pumps (2.2 kW)
14096 | Coxley Mill Lane SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Borger pumps. Pulsar clamp-on flow monitor installed, not overly accurate. New flow meter (burst detection) being commissioned - review when we have more accurate flows. Flow meters installed (Apr-21)
15454 | Creech St Michael North End SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
17285 | Cromhall Church Lane SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15167 | Cromhall Jubilee Lane SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15163 | Cromhall Townwell SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test. Luke Sturgeon's team have done pump testing here. Associated upstream flooding
15117 | Devizes Dunkirk Hill | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Pass to Flygts to investigate - C type 3152, 264 impellers. Changed impellers and NRV
13093 | DONIFORD SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | With Mechanical Optimisation Team to investigate/carry out pump testing. New pump(s) installed 12/07/22. Flow meter needs re-ranging. Looks like site is compliant now. New pumps installed Nov-22
14294 | Donyatt . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 7.3 l/s
14248 | East Burton Cross Roads SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flow meter now at discharge end, installed by Ops
14274 | East Chaldon . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 3.1 l/s
14264 | East Knighton . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 3.2 l/s
14222 | East Knighton Blacknoll SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1
14490 | Edington Tinhead (Lower Baynton Road) | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Permit application made for CSO (syphon) of 16 l/s
14076 | Evercreech Stoney Stratton SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 1.9 l/s, pass out to Ash's team (06/01/21). C9909 project report back non-compliant
15091 | Ferndown Aldridge Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15053 | Ferndown Golf Links Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14379 | Fiddington SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Mono pumps, need munchers instead of macerators
15551 | Fisherbridge SPS, Weymouth | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | No PFF in the consent. DWF consent is 20 l/s however this is an EO Richard to ask Andy B about what model PFF should be .
14340 | Fovant Church Lane | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Diameter of rising main is more likely to be 160mm not 225mm. Still not achieving SCV. Ask Luke's team to look at this site
15493 | Frampton Muckleford SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 2.6 l/s
14371 | FROGLAND CHEDDAR | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Both pumps well below consent, adjustments on drop test volume because of fat build up and pump housing volume. Both impellers have been changed, flow meter on discharge end, flow monitor being installed w/c 17/02/20 on SPS end
14563 | Frome Courts Barton Marston Lane SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF
14114 | Glastonbury Edgarley Millfield School SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Mechanical Optimisation Team has visited, changed impellers to super heads, steep system curve, not able to deliver PFF. Grit in sump/rising main. With Ops to clean rising main again. Ongoing investigations.
14095 | Glastonbury Porchestall SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | With Ops. New pumps (Grundfos) have been installed (Jun-21) but P2 is recirculating. P2 needs fitting on new guide rails and adaptor claws - to be done in the next month. Have reconfigured pumps - monitor after P2 work completed
14070 | Godney | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | EO not CSO. DWF in consent is 6m^3/day. 6x DWF = 0.42 l/s - confirm
14057 | Great Cheverell Cheverell Green SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 6.8 l/s
14386 | Greinton Moor Drive SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | New impellers (450) installed on 7th Dec. Pump 1 & 2 PFF = 40 l/s. Monitor to confirm this is now compliant
14116 | GURNEY SLADE SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | This site doesn't seem to be doing high flows in high level. Do we need 1 minute data to investigate further? Consent only acheived when both pumps running. Lots of missing value points? Data missing - IT ticket raised.
14328 | Hanging Langford . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test Portable flow meter test carried out by Fred on 17/05/21. Under investigation. Pump 2 hasn't ran since 23rd September, so no pump 2 flow. Job has been raised. Pump 2 not running so only flow from Pump 1. Ops to carry out maintenance on pumps and confirm AVs on rising main
14202 | Hankerton Bridge SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Ops carried out maintenance on pumps & replaced NRVs with Swingflexes. No improvement in flow. Pass to Sean's team to produce system curve & spec replacement pumps. Awaiting CCTV survey on rising main - bad condition from H2S attack With Ops/Mechanical Optimisation Team. Current impellers won't achieve FFT. Biggest impellers on these pumps would achieve 41 l/s. Next pump size is 3202 with a 452 impeller (37kW) would achieve this. Trial a bigger impeller in the short term, but look to see if we can install a bigger pump here. DD to arrange an inspection of the panel
14395 | Hatch Beauchamp . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15439 | Henlade . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Analogue signals not working
15290 | Henstridge Marsh Lane (Henstridge No 2) SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Pumps have now been replaced by Concertors, carry out virtual drop test/comparison of run-stop times to prove flow has improved.
14374 | Highbridge Newton SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Treatment site
15446 | Hillcommon Hill Common SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 8.3 l/s
15555 | Hillcrest Road PS, Wyke, Weymouth | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 60 sec archive requested for more accurate reading. VSDs will increase flow in high level
14346 | Hindon The Dene SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | With Ops - trialling new impellers
14287 | Hinton St. George SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Check and carry out pump test
14467 | Holt The Star | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Establish what the pumps should/could do as the PFF in the consent is not realistic. 1no. Flygt 3127 and 1no. Flygt 3153 listed. 200mm CI rising main. Current bigger pump wouldn't achieve SCV. Trial a 3153 HT pump to see what this can achieve. Carry out November/December.
14058 | Horton Horton Farm SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flows run through virtual drop test model, validated by drop test carried out in April 2019 (11.6 l/s)
15313 | HUISH EPISCOPI PIBSBURY | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 11/10/22 both pumps achieving PFF - VSDs have been adjusted in Sept-22
15315 | Huish Episcopi Wagg Bridge SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flow meter installed by Ash's team 06/05/21, awaiting electrical connection. Drop test from 2018 showed 2.7 l/s
14158 | Hullavington Raf Station SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1
14317 | Hurdcott . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | LS tested Feb-22, recommending different impellers to achieve PFF
14302 | Idmiston | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flygt CP 3127 430 & 481 impellers. Confirm pumps/impellers, adjust/shim, increase impeller size? Adjust to N-types?
14289 | Ilchester Ilchester Main SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 78 l/s
10312 | Iron Acton Hoovers Lane SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | With Ops - replacing pumps - need to confirm if the consent is for storm flow
14555 | Isle Abbotts Two Bridges SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Sam installed flow meter 04/03/21, awaiting commissioning
15325 | Keinton Mandeville . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pump 1 and 2. Drop test from 2018 showed 13.8 l/s
15542 | Keynsham Keynsham High Level SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Neil Fletcher & Richard Leggo carried out pump testing with portable flow meter in July 2020
14102 | Kilmersdon . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
19725 | Kimmeridge SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pumps
19035 | Kingsbury Episcopi . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
17268 | Kingswood Station Road Storm Tank SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 49 l/s
14176 | Kington Langley . SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 11.5 l/s
15580 | Langford Blackmoor Road SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15298 | Limington Main SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 1.3 l/s LS team carried out pump testing Nov-21. New pumps ordered 01/12/21, installed, achieving 4 l/s in duty/standby instead of duty/assist
14415 | LITTON CHENEY CHICKSBRIDGE SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Noisy Flow
15572 | LOCKING VILLAGE SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Current flowmeter not working properly, new burst detection flow meter will be installed as part of the 2020/2021 programme (John Harper 25/06/20). New flow meter shows 30 l/s for each pump. 01/08/23 summing flows for separate flow meters shows site is compliant
15320 | Long Sutton Knole | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | With Mechanical Optimisation Team/Ops. Borger pumps have been installed - could increase speed but the pressure would wear the pump out very quickly. Looking at upgrading the Borger pump - seeing if the panel can run it. Ongoing.
14286 | Lopen SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Both pumps have been changed - check and carry out pump test. Flow meter installed Jan-22, awaiting connection
14020 | Lower Stanton Drew . SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 5.0 l/s
14220 | LYT MATVRS BULBURY LANE SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Scheme in for new pumps completed. Site calls assist pump in high level
14260 | Lytchett Matravers Glebe Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test done in DWF for pump 1.
14162 | Malmesbury Burton Hill SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 6.9 l/s
14196 | Malmesbury Noahs Ark SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Has a flowmeter but units are l/min. Assume the consent is also in l/min?
14185 | MALMESBURY ST JOHNS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Twin rising mains with 2 flow meters, sum flow
14288 | Marston Magna Church Lane SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 5.6 l/s. Drop test from Jan 2019 gave flow rate of 4.5 l/s for both pumps
15497 | MARTINSTOWN SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | New single pump is not connected with run/stop signals yet. Maintenance carried out 03/07/20, grit damaged impeller on new trial high head pump. Trial looks successful but will fit hardened impeller. Look to replace other set of tandem pumps with other high head pump. Completed now, both pumps delivering 15 l/s 13/07/21
15460 | Meare Green Stoke St Gregory SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14108 | Mells SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Pump 1 not running. Old Biwaters - can we change to Flygts - Ash to get Flygt and Grundfos quotes. New pumps installed and flow meter
15402 | Middlezoy Nethermoor Road SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | P2 reached 10.2 l/s in high level, P1 9.3 l/s. Look to produce combined system curves for Middlezoy and Othery to come up with a solution for both sites - both sites pumping into the same system - with Asset Reliability/Ops
15190 | Milborne St Andrew Manor Farm SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Summed up Storm and DWF flow (don't do a reading unless storm pump flow is non-zero!!). Need to check set points for different pumps.
14420 | Minehead Quay West | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flow had dropped off since Sept-19 - investigate. SR to request 1 minute data. No AVs, low head. NR e-mailed AP (10/01/20) - John Harper will replace NRVs with Swingflex and see if that improves flow, otherwise look at pumps next. This was completed 21/1/20 and no improvement of flow. P2 is only ever used. Suggest switch to P1 and also maintain/adjust/shim both pumps. Ash has installed 2 new pumps
14142 | Minety Station Road SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14285 | MISTERTON | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Sean visited with John Harper, fitted 486 impeller to P2, P1 shimmed the 488 imp. P1 doing 16.6 l/s, P2 doing 21.5 l/s, both at 0.9 sump level. SS will order another 486 impeller for P1. Overloads will need upgrading. Upgrade impellers to 486
15511 | Monksilver B3188 SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Job in for Mono rebuild (Jan-21)
14243 | Morden Cock And Bottle SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 14.7 l/s. Use flow meter at Blackheath WRC and measure flow when Bulbury Lane isn't pumping
15043 | Mudeford Mudeford Gardens SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14458 | North Bradley Churchlands SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pumps
14460 | North Bradley Yarnbrook | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Upstream flooding. Review how pumps are performing against pump curve, create system curve, pass to Sean
15465 | North Curry Stoke Road SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 7 l/s
14380 | North Newton Church Road SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Carry out virtual drop test - C9909 project reported non-compliant
15450 | Norton Fitzwarren Langford Lane | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flow meter installed in-house on Mono pipework. Ash's team looking into this - have checked pumps and AVs, looking at jetting the rising main next, in discussions with Stuart Pugsley to change the gearbox (and increase the speed of the pump) Jan-21. Ice pigging on 11/03/2021 increased P1 flow to 1.9 l/s. Named scheme for Y3 (capital maintenance)
15317 | NORTON SUB HAMDON SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | On-site work, flow meter seemingly ok after 19-Jun, monitor flow when site goes into high level
15158 | OLVESTON THE COMMON SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Passed to Sean to review - old C type Flygt pumps. On site 02/07/20 - carried out pump/system tests, checked flow meter against portable flow meter. Reviewing options as proposed pump required to achieve this flow is 55kW. Look to calibrate/service existing meter as ~1 l/s out. Installing AV - open job (Jan-21). Still non-compliant. Consider for ice-pigging/jetting. Get quote to have inspection chamber/cut-out done ~400m from SPS (09/06/21). The theoretical system curve is a lot flatter than the measured system curve suggesting there is a restriction, but flow is achieving self-cleansing and the flow hasn't really changed in ~15 years. LS to trial a 32kW SH pump to clean the main, monitoring with flow/pressure, or another bigger pump to hire for a few days. DD/LS to arrange site visit to trial
14399 | Osmington Mills SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | The site is an EO so there is no consented flow, but 7.4 l/s is the modelled target flow to avoid the EO operating during rain. New (upsized) impellers installed 03/03/22
15388 | Othery Rye Lane/ Summerhedge Road SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Look to produce combined system curves for Middlezoy and Othery to come up with a solution for both sites - both sites pumping into the same system - with Asset Reliability/Ops
14426 | Paulton Goosard Bridge SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | FSO - flow monitor going in Nov-20. Review flows/pumped flow. Pass to Sean Smith. Not enough info for virtual drop test
15389 | Pawlett Main Road SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | With Mechanical Optimisation Team to investigate/carry out pump testing
15378 | Pawlett Vicarage Lane SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15772 | Peasedown St John Wellow Lane SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test done in DWF. Both pumps at 61 l/s
14046 | Pewsey Swan SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | LS to carry out pump testing Nov/Dec 2021
15645 | PILL AVON ROAD SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Located a new AV - look to access/replace with AVK. Nominated for panel replacement in Y3 (capital maintenance) to run larger pumps
15139 | Pilning Swanmore Bridge SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15322 | Pitney . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Named scheme for Y3 (capital maintenance)
15257 | Poole Bridge Poole Quay | S | 15 |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | NR requested outstanding planned maintenance is completed (this is being done 13/12/19) - lift pumps, check impellers etc. This has been done and flows increased. SR to ask for 1 minute data. New impellers and wear plates have been ordered. Fitted 22/01/20. This improved DWF by ~2 l/s so we think this may be sufficient that in increased head (high wet well level) the PFF will be achieved. No recent high level - continue to monitor. Did not spill through winter 2020/21 - highest level was 75% in December 2020
15236 | Poole Canford Heath Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15270 | Poole Creekmore Lane | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Request flow signal to 1min archiving - done. Achieving PFF. P1 is doing PFF, P2 is just under. Outstanding PPM - NR requested this be completed (10/01/20) Rising Main flowmeter is broken. Hasn't gone into high level recently.
15383 | Poole East Quay Perry Gardens | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Pressure + Rising Main flow available to make system curve. Request 1-min archiving for flow at discharge end (done). Site OK. Not gone into high level for a while Only able to meet consent with pumps 1 and 2 running. Not gone into high level recently.
15252 | Poole Egmont Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pumps
15244 | Poole Elgin Road | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Scheme to replace pumps - CM338. Mark Harris + Cliff to confirm surge vessel and scheme approval. Consented flow confirmed at 650 l/s. Only able to reach consent when pumps 1, 2 and 4 running
15237 | POOLE MAGNA ROAD SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flowmeter installation not finalised Jun-20, not working 10/08/20
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Faulty FM, job raised for JJ to look at flow meter (13/01/21). Only 1 pump running currently following a burst rising main. 2 pumps required (duty/assist) to achieve PFF
15233 | Poole Wilderton Road | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flow rate is not given in permit, but required to avoid spilling to sea via Branksome Chine. Order has been placed with Hidrostal to replace 2no. wet ends and refurb 2no. Pumps. NRM paper 14/01/20 for longer term scheme.
13373 | Porlock Porlock Weir SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14621 | PORTISHEAD TOWN HARBOUR | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Check duty/assist limits to see when assist pump kicks in. Didn't go into high level
15648 | Portland Portland Bill SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 5.6 l/s
17175 | Puriton Downend Terrace SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14293 | Queen Camel Englands Mead Green Lane SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 16.8 l/s
15556 | RADIPOLE SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Treatment site
15166 | Rangeworthy Berrows Mead SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15141 | Rangeworthy Patch Elm Lane SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14059 | Rowde Tower View SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 8.7 l/s
14624 | Saltford Mead Lane SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15574 | Sandford Batch . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pumps. May need checking as previous drop test from 2014 showed 8 l/s.
19817 | Sandford Orcas . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 5.1 l/s
15123 | Seend Bell Inn | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flygt NP 3153, 450 and 454 impellers. Passed to Flygts. Maintenance & retested, now ok
14466 | Semington Brook | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flygt 3152. Flow meter at Bowerhill STW isn't working and isn't just this SPS's flow. Sean placed order for 3017s 02/07/20
15207 | SHAFTESBURY LONG CROSS SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 1 pump unavailable, with Fred's team to get repaired, hire pump in, 24/06/20. SR asked for 1 minute flow data New pump installed 20/07/20, fuse needs replacing, flow meter faulty. Awaiting job completed w/c 27/07/20. Flow sensor is now working but chamber gets flooded so likely to stop working again - review getting replaced with an inline Magflow (can R&M do this?) Monitor flow in high level. P1 needs new impeller. Pumps now achieving 15 and 16 l/s
13273 | Shipton Gorge Off Markets Lane SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Side ID on prism is coming up as 15683 (which is Burton Bradstock)
14507 | Shirehampton Lamplighters SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15235 | SHORE ROAD POOLE | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | The permit is very unusual. It states that 60 l/s is needed as PFF during spills to sea. This was really adopted just to convey screenings away from site during storms. 90 l/s is the normal PFF setting (duty/assist)
15537 | Shoscombe Single Hill SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pumps
14519 | Somerton Barpool Lane (Compton Dundon No.3 on Prism) | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | New flow meter added on 10/09/2020. There is no overflow/consented flow, but this is the target flow for self-cleansing velocity
17027 | South Cadbury . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 7.4 l/s
14358 | South Newton Bell Inn SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2.
15013 | SOUTHBOURNE HENGISTBURY HEAD SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | SR looked into data to confirm deterioration of both pumps Overdue pump maintenance (Jan-20) - NR requested PPM be carried out in the next 2 weeks. Completed 27/05/20, shims ordered (18/06/20), awaiting fitting 20/07/20 Work completed on site, pumps achieving 30l/s more, monitor next time sump goes into high level.
14313 | Stapleford Overstreet SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14320 | Stapleford Pelican Inn SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 1. Pump 2 at 8.7 l/s
14216 | Stoborough Kings Arms | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flow had dropped off since Sept-19, previously doing 15 l/s. Request AV maintenance be completed w/c 13/01/20, then look to lift pumps/split NRVs. AV in field has not been found in years. Pumps lifted/split/maintained 21/1/20, flow has improved afterwards. Suggest replace AV in chamber, maintain NRV, look to change impellers or change to N-type. Impeller change 17/3/20, but still not quite meeting flow. Concertors on order, should arrive w/c 20/04/20. Installed 16/04/20, flow achieved
14326 | Stoford SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 7.1 l/s
15458 | Stoke St Gregory Curload SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14391 | Stoke St Gregory No 1 Lane End | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flygts NP 3127 Ash arranged for new pumps etc. with Sean, installed flow meter May-20 Will only achieve 27l/s when the storm pumps run, not the DWF pumps (2 rising mains). Calculate using sum of 2 flow meters. Separate flow meters on storm and foul rising mains - PFF should be both flow meters summed. Asset Reliability to look at flow data and confirm compliance. AM to ask for minute data
14110 | Stoke St Michael Stoke Hill SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Changed pumps to 22kW pumps, deliverying 15 l/s
19787 | Stour Row . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15473 | Stratton Mill Lane SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14252 | Studland Combe | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Concertors - JJ has adjusted panel and pumps tested 06/07/22 and doing PFF. Site spilt 02/10/22 and both pumps doing 16.8 and 16 l/s so ok
14227 | Studland Wadmore Lane | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Pump 1 failed. Flygt CP 3127 430 impeller, NP 3127 437 impeller. Flygt engineers checked both pumps, recommending new impellers - ordered 05/05/20. Flow meter now installed
14261 | Studland Watery Lane SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | P2 Needs looking at RG 4/8/22
14411 | Sydling St Nicholas . SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 8.1 l/s
15448 | Taunton Longacre Close SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15447 | Taunton Mountway Bishops Hull SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test. Screw pump
15443 | Taunton New Barn Queensway SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14342 | Teffont Evias | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Required flow is based on achieving 0.75 m/s self cleansing velocity in the majority of the rising main (100mm). Virtual drop test gives 8.3 l/s (Lewis)
15544 | Temple Cloud Temple Bridge SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump both pumps.
15723 | Tetbury Springfields SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14311 | Tilshead, Camp Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Flygt NP 3153 450, update asset details for pump 2. Check pumps. Dry well With Sean Smith to look at pumps/impellers w/c 30/03/20
14113 | TRUDOXHILL SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Both pumps have been rebuilt, new flow meter now installed and configured correctly
15140 | Tytherington Southlands SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15164 | Tytherington Stidcott SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 22.0 l/s
14221 | Upton Frenchs Farm | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Permit application made for CSO for 22 l/s. Flygt attended to maintain pumps - need to confirm what was done. Flow from virtual drop test for P1. P2 showing 9.3 l/s. 24/08/21 Pump testing by Luke's team (after cleaning NRVs) - 29 & 33 l/s
14265 | Upton Moorlands Way | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | New upsized impellers ordered before Xmas, should be arriving w/c 30/03/20 Installed 01/04/20
15314 | Upton near Langport | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Being done 2019/2020 as Div Eng full update - Ross Frampton
14219 | Upton Sandy Lane | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | OK no action
15052 | Verwood Ebblake SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15553 | VICTORIA SQUARE SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Treatment site
14229 | Wareham West Mill Crescent SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14435 | Warminster Boreham Road | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Upstream flooding. Review how pumps are performing against pump curve, create system curve, review pumps (currently 1 Sarlin, 1 old Flygt)
14439 | Warminster Calveswater | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | New pumps will be installed as part of AMP7 scheme
15519 | WATCHET MARKET STREET TUNNEL | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Treatment site
14394 | Wellington Mitchells Pool SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15536 | Wellow Mill Hill SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pumps
15381 | Wembdon Common SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 54 l/s
14392 | WEST BUCKLAND SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Impellers and guide rails have already been changed in 2017 - Flygts to re-do pump test and look at pumps
13337 | West Lulworth Hambury Farm SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 12.8 l/s
14588 | West Lulworth Lulworth Outfall Ps SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 8.4 l/s
15060 | West Moors Pennington Copse | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Pass to Flygts to investigate - C type 3152, 431 and 470 impellers? Check and adjust/shim?
15074 | West Moors the Forest | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 7.2 l/s
15090 | West Parley Church Lane | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Duty/standby/assist, Flygt 3127, 480 impeller. Ordered new impellers (for Flygts to fit) 21/01/21, due for installation earch March 2021. Not enough information for virtual drop test.
14405 | West Stafford Dorchester Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15792 | Weston-Super-Mare Knightstone Road SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15391 | Westonzoyland Hamrod Lane SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15370 | Westonzoyland Lakewall Road SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 4.5 l/s
15561 | Weymouth Ferrybridge Portland Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 52 l/s. May need to double check CSA as flow is about 3 times the consent
15552 | Weymouth Knightsdale Newstead Road SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for pump 2. Pump 1 at 200 l/s. May need to double check CSA as flow is about 3 times the consent
15283 | Wincanton Bayford SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
14072 | Wookey Bleadney Mill SPS & CSO | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 60 sec archive requested Sean/Ash installed new super head pump, delivered 4.5 l/s. 2nd pump to be installed after some work to pipework/benching. 2nd pump installed Nov-20, now compliant
14273 | Wool Railway Cottages SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15396 | Woolavington Meadow Farm SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15508 | Wootton Courtenay . SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15125 | Worton Mill Road | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | 2no. Flygt 3127s listed in Hansen but of differing power, missing asset data. Not enough info for virtual drop test.
14324 | Wylye Chequers Cottages SPS | S |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15188 | Yate North Road SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Virtual drop test in DWF for both pumps
15311 | Yeovil Mudford SPS | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Pressure and flow monitoring installed Oct-21 This site is very close to consent during high levels. I only found a few points above consent but most of the time its just below. Not gone into high level for a while.
14295 | YEOVILTON WEIR | W |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | One Concerter has been installed + NRVs, pipework, flow monitor installed (burst detection). 8.5 l/s. Other pump (3127) is doing 2.5 l/s.
14145 | Malmesbury Tanners Bridge | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Pumps were tested in Duty/Assist, but consent requires standby pump. Flygt NP 3153, 275 impellers. Flygts attended, changed impellers and carried out drop test. With Mechanical Optimisation Team to investigate/carry out pump testing Flow reduces when Noah's Ark starts pumping - look to adjust flow at Noah's Ark to allow more flow from Tanners Bridge
14147 | Chippenham Westmead SPS | N |  |  |  | Dump From Old Master |  |  | 3652500% |  |  |  | Not enough info for virtual drop test
15322 | Pitney . SPS | W | [10 empty] | AP to maintain AV, check pressures and do suck and blow on main | AP
15100 | North Newnton . SPS | N | 10 | 5.61 | 43.9% | Dec 23 Report | [6 empty] | DD to Lift and Shim pumps, 25% off from 1 year ago
15389 | Pawlett Main Road SPS | W | 19.2 | 15 |  | 2023-10-01 | [6 empty] | Checking mono power draw against existing booster pump - LS. Next steps, detail what needs doing to formalise the arrangement, civils replacment DWF pumps etc
14179 | BIDDESTONE MANOR COT | N |  |  |  | Dump From Old Master
14067 | Bitton . SPS | N | [10 empty] | Aug 23: LS to arrange revisit following works at station, maybe find BEP for both pumps?
15450 | Norton Fitzwarren Langford Lane | W | 1.7 | 1.44 | 15.29% | Feb 24 Report | [6 empty] | vsd controlled and rising main pressure is high
15389 | Pawlett Main Road SPS | W | 19.2 | 11.1 | 42.19% | Feb 24 Report | [6 empty] | dwf pump has been replaced and now set up as duty standby and run siganl has been set up
15334 | CHARLTON ADAM | W | 21 | 19.21 | 8.524% | Feb 24 Report | [6 empty] | impellors have been trimmed and replacements ordered hit 21lps in high level
14116 | GURNEY SLADE SPS | W | 7 | 5.34 | 23.71% | Feb 24 Report | [6 empty] | looking into get more flow with different gear box
15309 | Charlton Mackerell Rookery Farm | W | 26 | 22.5 | 13.46% | Feb 24 Report | [6 empty] | LS looking at new pumps and flow only drops off when pumping for long periods in wet weather possibly due to wrc in h/l
15400 | Bridgwater West Quay SPS | W | 206 | 191.448 | 7.064% | Feb 24 Report | [6 empty] | monitor
14379 | Fiddington SPS | W | 5.3 | 4.96 | 6.415% | Feb 24 Report | [6 empty] | monitor
15316 | Barton St David Tootal Bridge SPS | W | 2.4 | 2.38 | 0.8333% | Feb 24 Report | [6 empty] | monitor
14420 | Minehead Quay West | W | 14 | 7.28 | 48% | Feb 24 Report | [6 empty] | needs full sump it does 11lps at normal levels not 7.5
15388 | Othery Rye Lane/ Summerhedge Road SPS | W | 13.5 | 11.93 | 11.63% | Feb 24 Report | [6 empty] | no change on going issue
14386 | Greinton Moor Drive SPS | W | 34 | 31.56 | 7.176% | Feb 24 Report | [6 empty] | on HLA list no change
15449 | Meare Green Wrantage SPS | W | 1 | 0.9 | 10% | Feb 24 Report | [6 empty] | possible suck and blow on rising main
15415 | Bridgwater, Colley Lane SPS | W | 123 | 117.56 | 4.423% | Feb 24 Report | [6 empty] | site does 130lps in high level
15278 | BENNETTS ORCHARD SPS | W | 7.8 | 7.32 | 6.154% | Feb 24 Report | [6 empty] | site in consent 7.8lps when storm pump running
15311 | Yeovil Mudford SPS | W | 9.3 | 9.17 | 1.398% | Feb 24 Report | [6 empty] | site meets flow as flow meter is for info only
14621 | PORTISHEAD TOWN HARBOUR | W | 260 | 214 | 17.69% | Feb 24 Report | [6 empty] | site will ramp up to 260lps in high level
14114 | Glastonbury Edgarley Millfield School SPS | W | 8 | 5.9 | 26.25% | Feb 24 Report | [6 empty] | this is doing 9 lps so is in consent
15322 | Pitney . SPS | W | 5.3 | 4.2 | 20.75% | Feb 24 Report | [6 empty] | vsd will ramp up and suck and blow to rising main job to be completed
14648 | CHILTON POLDEN MAIN SPS | W | 36 | 28.9 | 19.72% | Feb 24 Report | [6 empty] | waiting on pumps
Note on E15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Won't work with automation, will need to do manual
Note on B48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Portishead SPS
Note on E54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: P2 achieves consent but P1 just under
Note on E91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only able to meet consent with 3 pumps running at once
Note on E96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Site rarely goes above 50% level Reply: Wet well level was 37.4 at maximum flow. Reply: Add foul and storm together
Note on E101: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Do we need to add the Rising Main Storm Flow and Rising Main DWF Flow?
Note on E134: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only able to meet consent with 3 pumps running at once
Note on E135: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Do we need to add the Rising Main Storm Flow and Rising Main DWF Flow?
Note on E142: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Won't work with automation, will need to do manual
Note on E771: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: P2 achieves consent but P1 just under
Note on B773: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Long Sutton Bennetts Orchard SPS
Note on B775: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Portishead SPS

## Monthly Performance
| Flow4 Sites | [5 empty] | Non-Flow4 Sites | [5 empty] | All Sites | [8 empty] | For Messenger
Month | # of Compliant Sites | # of At Risk Sites | # of Non-Compliant sites | % compliance (within 8%) | % non-compliance | # of Flowmeters | # of Compliant Sites | # of At Risk Sites | # of Non-Compliant sites | % compliance (within 8%) | % non-compliance | # of Flowmeters | # of Compliant Sites | # of At Risk Sites | # Compliant or At Risk | # of Non-Compliant sites | % compliance (within 8%) | % non-compliance | # of Flowmeters | Date of Record | N.B: Please remember to copy the current figure to the relevant month once finalised AND complete the relevant month on the Master sheet | % with flow meters compliant | Monthly tracker
Current | 20 | 4 | 1 | 96% | 4% | 23 | 106 | 18 | 1 | 99.2% | 0.8% | 144 | 126 | 22 | 148 | 2 | 98.67% | 1.333% | 150
2020-03-01 | [14 empty] | 20 | 9 | 68.97% | 31.03% | 29 | -
2020-04-01 | [14 empty] | 22 | 8 | 73.33% | 26.67% | 30 | -
2020-05-01 | [14 empty] | 38 | 12 | 76% | 24% | 50 | -
2020-06-01 | [14 empty] | 54 | 9 | 85.71% | 14.29% | 63 | -
2020-07-01 | [14 empty] | 57 | 10 | 85.07% | 14.93% | 67 | 4403300%
2020-08-01 | [14 empty] | 62 | 8 | 88.57% | 11.43% | 70 | 4408400%
2020-09-01 | [14 empty] | 57 | 13 | 81.43% | 18.57% | 70 | 4410500%
2020-10-01 | [14 empty] | 55 | 10 | 84.62% | 15.38% | 65 | 4413700%
2020-11-01 | [14 empty] | 60 | 14 | 81.08% | 18.92% | 74 | 4416200%
2020-12-01 | [14 empty] | 66 | 22 | 75% | 25% | 88 | 4420300%
2021-01-01 | [14 empty] | 63 | 27 | 70% | 30% | 90 | 4423000%
2021-02-01 | [14 empty] | 67 | 23 | 74.44% | 25.56% | 90 | 4425700%
2021-03-01 | [14 empty] | 70 | 22 | 76.09% | 23.91% | 92 | 4428500%
2021-04-01 | [14 empty] | 71 | 24 | 74.74% | 25.26% | 95 | 4431500%
2021-05-01 | [14 empty] | 72 | 30 | 70.59% | 29.41% | 102 | 4435000%
2021-06-01 | [14 empty] | 73 | 28 | 72.28% | 27.72% | 101 | 4437800%
2021-07-01 | [14 empty] | 78 | 26 | 75% | 25% | 104 | 4440600%
2021-08-01 | [14 empty] | 73 | 25 | 74.49% | 25.51% | 98 | 4444100%
2021-09-01 | [14 empty] | 74 | 29 | 71.84% | 28.16% | 103 | Est data
2021-10-01 | [14 empty] | 78 | 26 | 75% | 25% | 104 | Est data
2021-11-01 | [14 empty] | 82 | 24 | 77.36% | 22.64% | 106 | Est data
2021-12-01 | [14 empty] | 86 | 22 | 79.63% | 20.37% | 108 | 4456100%
2022-01-01 | [14 empty] | 90 | 20 | 81.82% | 18.18% | 110 | 4459400%
2022-02-01 | [14 empty] | 84 | 23 | 78.5% | 21.5% | 107 | 4462000%
2022-03-01 | [14 empty] | 89 | 17 | 83.96% | 16.04% | 106 | 4465900%
2022-04-01 | [14 empty] | 91 | 15 | 85.85% | 14.15% | 106 | 4469000%
2022-05-01 | [14 empty] | 105 | 12 | 89.74% | 10.26% | 117 | 4472100%
2022-06-01 | [14 empty] | 103 | 16 | 86.55% | 13.45% | 119 | 4475000%
2022-07-01 | [14 empty] | 115 | 16 | 87.79% | 12.21% | 131 | 4478200%
2022-08-01 | [14 empty] | 118 | 10 | 92.19% | 7.812% | 128 | 4481300%
2022-09-01 | [14 empty] | 120 | 10 | 92.31% | 7.692% | 130 | 4484500%
2022-10-01 | [14 empty] | 120 | 11 | 91.6% | 8.397% | 131 | 4487400%
2022-11-01 | [14 empty] | 119 | 14 | 89.47% | 10.53% | 133 | 4490200%
2022-12-01 | [14 empty] | 118 | 18 | 86.76% | 13.24% | 136 | 4493400%
2023-01-01 | [14 empty] | 113 | 24 | 82.48% | 17.52% | 137 | 4496600%
2023-02-01 | [14 empty] | 133 | 2 | 98.52% | 1.481% | 135 | 4499500%
2023-03-01 | [14 empty] | 119 | 17 | 87.5% | 12.5% | 136 | 4501600%
2023-04-01 | [14 empty] | 122 | 16 | 88.41% | 11.59% | 138 | 4504700%
2023-05-01 | 18 | 4 | 1 | 95.65% | 4.348% | 23 | 89 | 12 | 17 | 85.47% | 14.53% | 118 | 107 | 16 | 123 | 18 | 87.23% | 12.77% | 141 | 4507800%
2023-06-01 | 19 | 2 | 2 | 91.3% | 8.696% | 23 | 95 | 13 | 10 | 91.53% | 8.475% | 118 | 114 | 15 | 129 | 12 | 91.49% | 8.511% | 141 | 4510300%
2023-07-01 | 19 | 4 | 1 | 95.83% | 4.167% | 24 | 93 | 19 | 5 | 95.73% | 4.274% | 117 | 112 | 23 | 135 | 6 | 95.74% | 4.255% | 141 | 4514800%
2023-08-01 | 17 | 7 | 0 | 100% | 0% | 24 | 89 | 25 | 2 | 98.27% | 1.72% | 119 | 106 | 32 | 138 | 2 | 98.57% | 1.42% | 143 | 4516900%
2023-09-01 | 20 | 2 | 1 | 91.3% | 8.7% | 23 | 93 | 20 | 7 | 83.33% | 16.66% | 120 | 113 | 22 | 135 | 8 | 84.61% | 15 | 143 | 4519900%
2023-10-01 | 20 | 2 | 1 | 91.3% | 8.7% | 23 | 93 | 22 | 5 | 95.83% | 4.167% | 120 | 113 | 24 | 137 | 6 | 95.8% | 4.196% | 143 | 4523000%
2023-11-01 | 18 | 3 | 2 | 87.5% | 12.5% | 23 | [6 empty] | 120 | 14 | 134 | 12 | 91.78% | 8.219% | 146
2023-12-01 | 16 | 5 | 3 | 82.6% | 17.4% | 23 | 95 | 9 | 18 | 80.3% | 14.7% | 122 | 101 | 14 | 115 | 21 | 79.31% | 14.4% | 145 | 4530100%
2024-01-01 | 14 | 6 | 3 | 86.95% | 13.05% | 23 | 85 | 21 | 14 | 88.3% | 11.7% | 120 | 99 | 27 | 126 | 17 | 88.11% | 11.88% | 143 | 4534500% |  | 88.11% | á
2024-02-01 | 16 | 3 | 5 | 79.1% | 20.83% | 24 | 76 | 28 | 19 | 84.55% | 15.44% | 123 | 92 | 31 | 123 | 24 | 83.6% | 16.32% | 147 | 4536200%
2024-03-01 | 19 | 3 | 1 | 95.6% | 4.4% | 23 | 82 | 29 | 10 | 91.73% | 8.26% | 121 | 101 | 32 | 133 | 11 | 92.36% | 7.64% | 144 | 4539900%
2024-04-01 | 19 | 3 | 1 | 95.6% | 4.4% | 23 | 83 | 30 | 8 | 93.33% | 6.67% | 121 | 102 | 33 | 135 | 9 | 93.75% | 6.25% | 144 | 4544100%
2024-05-01 | 18 | 4 | 1 | 95.65% | 4.34% | 23 | 95 | 20 | 6 | 95.04% | 4.95% | 121 | 113 | 24 | 137 | 7 | 95.13% | 4.86% | 144 | 4545600%
2024-06-01 | 20 | 3 | 0 | 91.3% | 8.69% | 23 | 104 | 18 | 0 | 90.98% | 9.02% | 122 | 124 | 21 | 145 | 0 | 91.3% | 8.7% | 145 | 4549600%
2024-07-01 | 20 | 3 | 0 | 91.3% | 8.69% | 23 | 104 | 18 | 0 | 90.98% | 9.02% | 122 | 124 | 21 | 145 | 0 | 91.3% | 8.7% | 145 | 4549600%
2024-08-01 | 20 | 3 | 0 | 91.3% | 8.69% | 23% | 106 | 17 | 0 | 90.24% | 9.76% | 123 | 126 | 20 | 146 | 0 | 90.41% | 9.6% | 146 | 4555100%
Sites not achieving compliance
| Site ID | Site name | Div | Consented flow (l/s) | Max flow measured / estimated (l/s) | % out Of consent or Below SCV | Action plan to resolve
1 | 14145 | Malmesbury Tanners Bridge | N | 18 | 8.1% | 55% | HLA on Malmesbury catchment/under-performing SPSs underway
2 | 15100 | North Newnton SPS | N | 10 | 5 | 50% | HLA completed. Downstream catchments can't receive any more flow. Looking to carry out infiltration sealing in upstream catchment to reduce flows
3 | 13153 | Holton Heath SPS | S | 20 | 16.56% | 17.2% | Ops to check/maintain/replace impellers, pump testing to be carried out to optimise pumps/impellers
4 | 14416 | Gurney Slade SPS | W | 7 | 5.97 | 14.71% | Ops to reattend and test, with new parts for Pump 1.
5 | 15244 | Poole Elgin Road | S | 650 | 553.2% | 14.88% | Rising main section (at highest risk of bursting) being replaced to reduce the risk of bursting when we increase the flows (currently capped to protect the rising main)
| Site ID | Site name | Div | Consented flow (l/s) | Max flow measured / estimated (l/s) | % out Of consent or Below SCV | Action plan to resolve
| 14116 | GURNEY SLADE SPS | W | 7 | 5.09 | 27.29% | Ops to reattend and test, with new parts for Pump 1.
| 15244 | POOLE ELGIN ROAD SPS | S | 650 | 550 | 15.38% | Rising main section (at highest risk of bursting) being replaced to reduce the risk of bursting when we increase the flows (currently capped to protect the rising main)
| 14179 | BIDDESTONE MANOR COTTAGE SPS | N | 7 | 6.1 | 12.86% | New impellers have been fitted. Monitor flows.
| 15207 | SHAFTESBURY LONG CROSS SPS | S | 15 | 13.42 | 10.53% | New impellors were installed 10/03/24. SPS team to trial a Grundfos superhead pump with the MOT.
| 14185 | MALMESBURY ST JOHNS SPS | N | 60 | 54.8905 | 8.516% | HLA on Malmesbury catchment/under-performing SPSs underway
| Site ID | Site name | Div | Consented flow (l/s) | Max flow measured / estimated (l/s) | % out Of consent or Below SCV | Action plan to resolve
| 15389 | Pawlett Main Road SPS | W | 19.2 | 11.28 | 41.25% | Trial booster pump has been installed to deal with increased flows, monitor over the next couple of months
| 14147 | Chippenham Westmead SPS | N | 155 | 133.75 | 13.71% | Site has had a new panel installed including VSDs. Phase 2 now is to rationalise the pumps and optimise the pumping regime.
| 14431 | Bishop Sutton . SPS | N | 19.6 | 18.5 | 5.612% | The AV how now been reinstalled but no improvement on flow. Looking into options to carry out pigging of the main.
| 14265 | Upton Moorlands Way | S | 45 | 43 | 4.444% | AV maintenance has been carried out by SPS Ops. Pumps/impellers to be maintained.
| 14145 | Malmesbury Tanners Bridge | N | 18 | 17.9 | 0.5556% | HLA on Malmesbury catchment/under-performing SPSs underway
| Site ID | Site name | Div | Consented flow (l/s) | Max flow measured / estimated (l/s) | % out Of consent or Below SCV | Action plan to resolve
| 15158 | Olveston the Common SPS | N | 21 | ? | 100% | New flow meter to be installed by SPS team. Ops to CCTV rising main, MOT to arrange Pigging after CCTV
| 15389 | Pawlett Main Road SPS | W | 19.2 | 10.62 | 45% | Trial booster pump has been installed to deal with increased flows, monitor over the next couple of months
| 14197 | Malmesbury Corston SPS | N | 8 | 5 | 37% | HLA on Malmesbury catchment/under-performing SPSs underway
| 14431 | Bishop Sutton . SPS | N | 19.6 | 15 | 24% | SPS Ops to install inflow check valves and monitor, MOT to assess requirements for pigging.
| 14391 | Stoke St Gregory No 1 Lane End | W | 27 | 21 | 23% | SPS Ops to carry out pump maintenance
| Site ID | Site name | Div | Consented flow (l/s) | Max flow measured / estimated (l/s) | % out Of consent or Below SCV | Action plan to resolve
| 14197 | Malmesbury Corston SPS | N | 8 | 5 | 37.5% | HLA on Malmesbury catchment/under-performing SPSs underway | 1
| 14266 | Wareham Sandford Lane SPS | S | 60 | 43.94 | 27% | SPS Ops to carry out pump maintenance - new impellers and wear rings to be fitted | 2%
| 15244 | Poole Elgin Road SPS | S | 650 | 541.66 | 16.67% | Rising main section (at highest risk of bursting) being replaced to reduce the risk of bursting when we increase the flows (currently capped to protect the rising main) | 3%
| 15235 | Poole Shore Road SPS | S | 90 | 74.2 | 16.67% | Carry out pressure survey along rising main to understand the problem - with Asset Reliability | 4%
| 14147 | Chippenham Westmead SPS | N | 155 | 136.4 | 12% | Site has had a new panel installed including VSDs. Phase 2 now is to rationalise the pumps and optimise the pumping regime. | 5%
Note on E5: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on K5: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R6: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R7: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R8: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R9: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R10: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R11: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R12: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R13: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R14: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R15: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R16: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R17: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R18: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R19: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R20: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R21: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R22: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R23: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R24: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R25: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R26: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R27: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised
Note on R28: Sagar Rana: N.B: Please remember to copy the current figure to the relevant month once finalised

## Consents
Site Id | Site | Site Type Code | Permit No | Permit Status | Permit Type | Granted Date | Consent Comments | Discharge Type | FFT (l/s) | Standby pump required? | No. pumps | No. DWF pumps
10312 | Iron Acton Hoovers Lane SPS | SPS | 100985 | Granted | Numerical | 2000-02-01 | TAKES EFFECT 01/02/2000. Discharge and Sample pts varied from 31/12/2010 to ST 6694 8318 and ST 6703 8319; and telemetry required. CSO 19267 rebuilt in new location at 10312 Oct 2012. | STORM OVERFLOW | 400 | No | 3
13014 | Axbridge Old Stw Site SPS | SPS | 103918 | Granted | Numerical | 2008-01-15 |  | STORM/EMERGENCY | 53.5 | Standby Pumps | 2
13074 | Combwich Quay Road SPS | SPS | 103336 | Granted | Numerical | 2006-07-28 | Takes effect soonest of 01/04/2007 or commissioning. Permit changed from STW to SPS 06/07/2018 | SETTLED STORM OVERFLOW | 4.9 | Standby Pumps | 2
13074 | Combwich Quay Road SPS | SPS | 103336 | Granted | Numerical | 2006-07-28 | Takes effect soonest of 01/04/2007 or commissioning. Permit changed from STW to SPS 06/07/2018 | EMERGENCY OVERFLOW | 4.9 | Standby Pumps | 2
13093 | Doniford . SPS | SPS | 101941 | Granted | Numerical | 2003-01-28 | Takes effect 1/4/03 | STORM/EMERGENCY | 60 | Standby Pumps | 8
13153 | Holton Heath Holton Heath SPS SPS | SPS | 41577 | Granted | Numerical | 1990-04-25 | Converted from STW permit to SPS permit 28/03/2013. PS EO management plan required. | STORM/EMERGENCY | 20 | No | 5
13189 | Lympsham Worthy Crescent SPS | SPS | 71507 | Granted | Numerical | 1991-04-08 | SPS REPLACED STW c1991. RTC in place to inhibit pumps when level at D/S SPS 17034 goes high. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
13216 | Monkton Deverill High Street SPS | SPS | 401862 | Granted | Numerical | 2005-03-31 | SPS CONSENT: Takes effect 31/12/2005 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
13265 | Shapwick Somerset SPS | SPS | 72077 | Granted | Numerical | 1992-10-23 |  | STORM/EMERGENCY | 7 | Standby Pumps | 4
13273 | Shipton Gorge Off Markets Lane SPS | SPS | NPSWQD008206 | Granted | Numerical | 2009-08-06 | Takes effect soonest of 31/03/2010 or commissioning. SPS consent to replace STW site. NPSWQD008206. Inhibit when Anning's Lane (15683) is inoperative | STORM/EMERGENCY | 6.3 | Standby Pumps | 4
13283 | Spaxton . SPS | SPS | 70975 | Granted | Numerical | 1989-10-30 | Converts to SPS Consent 31/03/2010. All text conditions take effect then. | STORM/EMERGENCY | 11.5 | Standby Pumps | 2
13334 | Bridport West Bay SPS | SPS | 400678 | Granted | Numerical | 2000-10-20 | Takes effect soonest of 31/12/2000 or commissioning | STORM/EMERGENCY | 414 | Standby Pumps | 6
13337 | West Lulworth Hambury Farm SPS | SPS | 401815 | Granted | Numerical | 2005-03-24 | Takes effect soonest of 30/04/2006 and commissioning | STORM/EMERGENCY | 15.9 | Standby Pumps | 7
13340 | Weston-Super-Mare Black Rock Windwhistle Road SPS | SPS | 101579 | Granted | Numerical | 2002-12-03 | Takes effect when granted and major review 31/03/2015. Tide locking is when sea level >4.75mAOD - see Permit for full details. | STORM OVERFLOW | 1000 | No | 17
13373 | Porlock Porlock Weir SPS | SPS | 100353 | Granted | Numerical | 1997-10-24 |  | STORM/EMERGENCY | 7 | Standby Pumps | 4
13375 | Lyneham Preston Lane SPS | SPS | 12200 | Granted | Numerical | 1993-03-05 | SCHEME CHANGED SITE FROM WRC TO SPS FEB19; the RAF contract to accept WW pumped away flows will need to be renegotiated in time for 2023 – WRC permit to be retained until 2023, review then. | BIOLOGICAL TREATMENT | #N/A | No | 6
13389 | Bossington . SPS | SPS | 100138 | Granted | Numerical | 1997-10-24 |  | STORM/EMERGENCY | 13 | Standby Pumps | 3
14002 | Bath Midland Road Twerton SPS | SPS | 102287 | Granted | Numerical | 2004-07-28 | Takes effect 31/3/2005 | STORM/EMERGENCY | 1050 | Standby Pumps | 4
14009 | Norton Fitzwarren Wassail View (Manor Farm) SPS | SPS | 72227 | Granted | Numerical | 1993-06-04 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14013 | Clifton Low Level SPS | SPS | 102907 | Granted | Numerical | 2005-03-30 | Takes effect 01/04/2005 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
14014 | Bristol Kings Walk SPS | SPS | 103304 | Granted | Numerical | 2007-03-16 | Spills via Site 16277. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14016 | Bristol Ashton Avenue SPS | SPS | 102970 | Granted | Numerical | 2005-03-13 | Replaces 011820 from soonest of 31/12/2011 or AMP 4 works commissioning. Duplicate power supply clause replaced standby generator clause from 31/12/2011. Spills via Site 16266. | STORM/EMERGENCY | 2050 | Standby Pumps | 18
14020 | Lower Stanton Drew . SPS | SPS | 12370 | Granted | Numerical | 1993-12-10 |  | STORM/EMERGENCY | 2.3 | Standby Pumps | 2
14046 | Pewsey Swan SPS | SPS | 401642 | Granted | Numerical | 2004-05-14 | Takes effect 31/12/2004. Serves SPS but spills via Site 16445. | STORM/EMERGENCY | 53 | Standby Pumps | 6
14047 | Coate Spaniels Bridge SPS | SPS | NPSWQD008925 | Granted | Numerical | 2009-10-09 | Geny connection / link box required by 31/03/2010: NPSWQD008925 | STORM/EMERGENCY | 7.4 | Standby Pumps | 2
14049 | Pewsey Wilcot Lodge SPS | SPS | NPSWQD003670 | Granted | Numerical | 2008-09-10 | Geny connection / link box reqd by 30/09/2009: NPSWQD003670 | STORM/EMERGENCY | 4 | Standby Pumps | 2
14050 | Collingbourne Ducis . SPS | SPS | 401764 | Granted | Numerical | 2004-08-10 | Takes effect 01/11/2004 | STORM/EMERGENCY | 20 | Standby Pumps | 5
14054 | Pewsey Jubilee SPS | SPS | 401776 | Granted | Numerical | 2005-04-25 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14055 | Marden High Street SPS | SPS | 402523 | Granted | Numerical | 2007-11-26 | See NoV, Jan09 | STORM/EMERGENCY | 8 | Standby Pumps | 2
14057 | Great Cheverell Cheverell Green SPS | SPS | 21366 | Granted | Numerical | 1968-08-15 |  | STORM/EMERGENCY | 6 | No | 2
14058 | Horton Horton Farm SPS | SPS | 401149 | Granted | Numerical | 2001-12-11 | Takes effect 31/3/2002. Spills via Site 19772. | STORM/EMERGENCY | 5.6 | Standby Pumps | 2
14059 | Rowde Tower View SPS | SPS | 103621 | Granted | Numerical | 2007-10-11 | Geny connection to be provided by 31/03/2008 | STORM/EMERGENCY | 7.7 | Standby Pumps | 2
14064 | Kingswood Willsbridge SPS | SPS | NPSWQD001439 | Granted | Numerical | 2008-03-04 | Takes effect when granted, NPSWQD001439 | STORM/EMERGENCY | 30 | Standby Pumps | 2
14067 | Bitton . SPS | SPS | 10665 | Granted | Descriptive | 1989-10-31 | Deemed determined Apr09: BITTON ST6800069400 RIVER BOYD. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 14.85 | Standby Pumps | 2
14068 | Glastonbury Bushycombe SPS | SPS | 102493 | Granted | Numerical | 2004-08-24 | Telemetry must be in place by 31/08/2004 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14069 | Street Houndwood Drove SPS | SPS | 103572 | Granted | Numerical | 2007-03-16 | Takes effect when granted. Telemetry and geny connection to be installed by 31/10/2007. | STORM/EMERGENCY | 31.4 | Standby Pumps | 2
14070 | Godney . SPS | SPS | 102494 | Granted | Numerical | 2004-08-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14071 | Meare Oxenpill SPS | SPS | 102495 | Granted | Numerical | 2004-08-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14072 | Bleadney Bleadney Mill SPS | SPS | 102371 | Granted | Numerical | 2004-02-04 | Takes effect 01/04/2004 | STORM/EMERGENCY | 3.5 | Standby Pumps | 2
14074 | Shepton Mallet Fosse Lane Charlton SPS | SPS | 103573 | Granted | Numerical | 2007-03-16 | Telemetry and "Genny connection" required by 31/10/2007 | STORM/EMERGENCY | 16.5 | Standby Pumps | 2
14075 | Glastonbury North Load Bridge SPS | SPS | 102496 | Granted | Numerical | 2004-08-24 | Oct08 Modification takes effect 31/03/2009 (includes geny connection / link box by 30/09/2009) | STORM/EMERGENCY | 3 | Standby Pumps | 2
14076 | Evercreech Stoney Stratton SPS | SPS | 103622 | Granted | Numerical | 2007-10-11 | Geny connection to be provided by 31/03/2008 | STORM/EMERGENCY | 6 | Standby Pumps | 2
14078 | Wells Haybridge SPS | SPS | 102370 | Granted | Numerical | 2004-02-04 | Takes effect 01/04/2004 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 4
14080 | Henton Ford Lane SPS | SPS | 102372 | Granted | Numerical | 2004-02-04 | Takes effect 01/04/2004 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14082 | Street Main SPS | SPS | 100740 | Granted | Numerical | 1999-08-11 | Pumping station key protection measures document from 12/09/2016 | STORM/EMERGENCY | 190 | Standby Pumps | 3
14083 | West Pennard Havyatt SPS | SPS | 102369 | Granted | Numerical | 2004-02-04 | Takes effect 01/04/2004 | STORM/EMERGENCY | 8.1 | Standby Pumps | 3
14084 | Glastonbury Actis SPS | SPS | 102497 | Granted | Numerical | 2004-08-24 |  | STORM/EMERGENCY | 21.9 | Standby Pumps | 4
14085 | Coxley Coxley Ripple SPS | SPS | 102367 | Granted | Numerical | 2004-02-04 | Takes effect 01/04/2004. See NoM, Sep08. Geny connection / link box reqd by 30/09/2009. | STORM/EMERGENCY | 6 | Standby Pumps | 2
14089 | Westhay . SPS | SPS | 102498 | Granted | Numerical | 2004-08-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14090 | Butleigh Wootton . SPS | SPS | 102499 | Granted | Numerical | 2004-08-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14092 | Glastonbury Wells Road SPS | SPS | 102377 | Granted | Numerical | 2004-02-04 | Takes effect 01/04/2004 | STORM/EMERGENCY | 12.8 | Standby Pumps | 3
14093 | West Pennard Page Lane SPS | SPS | 103782 | Granted | Numerical | 2007-10-11 | Geny connection/link box required by 31/03/2008 | STORM/EMERGENCY | 5 | Standby Pumps | 2
14094 | Glastonbury Thorndun SPS | SPS | 102376 | Granted | Numerical | 2004-02-04 | Takes effect 01/04/2004 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14095 | Glastonbury Porchestall SPS | SPS | 71825 | Granted | Numerical | 1993-03-05 | Spills via Site 16514. | STORM/EMERGENCY | 200 | Standby Pumps | 6
14096 | Coxley Mill Lane SPS | SPS | 102834 | Granted | Numerical | 2005-03-16 | Takes effect when granted | STORM/EMERGENCY | 10.8 | Standby Pumps | 4
14097 | Baltonsborough Baltonsborough Main SPS | SPS | 103055 | Granted | Numerical | 2006-11-24 |  | STORM/EMERGENCY | 17 | Standby Pumps | 5
14097 | Baltonsborough Baltonsborough Main SPS | SPS | 103055 | Granted | Numerical | 2006-11-24 |  | STORM OVERFLOW | 17 | Standby Pumps | 5
14099 | Street Walton Globe SPS | SPS | 103783 | Granted | Numerical | 2007-10-11 | Geny connection/link box required by 31/03/2008 | STORM/EMERGENCY | 5 | Standby Pumps | 2
14102 | Kilmersdon . SPS | SPS | 102698 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 5 | Standby Pumps | 3
14107 | Witham Friary . SPS | SPS | 102695 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 5 | Standby Pumps | 2
14108 | Mells . SPS | SPS | 102696 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 11 | Standby Pumps | 2
14110 | Stoke St Michael Stoke Hill SPS | SPS | 102699 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 11.3 | Standby Pumps | 4
14112 | Wanstrow . SPS | SPS | 102697 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 7 | Standby Pumps | 3
14113 | Trudoxhill . SPS | SPS | 102700 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 6 | Standby Pumps | 2
14114 | Glastonbury Edgarley Millfield School SPS | SPS | 102378 | Granted | Numerical | 2004-02-04 | Takes effect 01/04/2004 | STORM/EMERGENCY | 8 | Standby Pumps | 3
14116 | Gurney Slade . SPS | SPS | 101865 | Granted | Numerical | 2002-08-14 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 7 | Standby Pumps | 2
14117 | Street Petvine Close Portway Also S0118 SPS | SPS | 100745 | Granted | Numerical | 1999-08-11 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14119 | Wells Keward Avenue (Bishops Lea Close) SPS | SPS | 102373 | Granted | Numerical | 2004-02-04 | Takes effect 01/04/2004 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14120 | Street Middle Brooks Road SPS | SPS | 100744 | Granted | Numerical | 1999-08-11 | See NoM, Sep08. Geny connection / link box reqd by 30/09/2009. | STORM/EMERGENCY | 6 | Standby Pumps | 2
14125 | Gillingham Buckingham Road SPS | SPS | 42428 | Granted | Numerical | 1992-12-30 | Takes effect 31/05/1993 | STORM/EMERGENCY | 149 | Standby Pumps | 4
14126 | Shroton . SPS | SPS | 402122 | Granted | Numerical | 2006-08-09 | Rear of Ranston Mill House | STORM/EMERGENCY | 9.6 | Standby Pumps | 2
14127 | Gillingham Brickyard Lane SPS | SPS | 401128 | Granted | Numerical | 2001-10-30 | Takes effect 31/1/2002 | STORM/EMERGENCY | 65 | Standby Pumps | 3
14132 | Bransgore Wiltshire Gardens SPS | SPS | 401565 | Granted | Numerical | 2004-02-19 | Takes effect soonest of 30/09/2004 or commissioning | STORM OVERFLOW | 115 | Standby Pumps | 4
14139 | Christian Malford Swalletts Gate SPS | SPS | NPSWQD004959 | Granted | Numerical | 2009-09-08 | Takes effect soonest of 28/02/2010 or commissioning: NPSWQD004959 | STORM/EMERGENCY | 10 | Standby Pumps | 2
14142 | Minety Station Road SPS | SPS | 2213A | Granted | Numerical | 1984-01-10 | Also see 011477. Replacement consent takes effect 01/04/2007. | STORM OVERFLOW | 6.5 | Standby Pumps | 7
14142 | Minety Station Road SPS | SPS | 2213A | Granted | Numerical | 1984-01-10 | Also see 011477. Replacement consent takes effect 01/04/2007. | EMERGENCY OVERFLOW | 6.5 | Standby Pumps | 7
14145 | Malmesbury Tanners Bridge SPS | SPS | 103784 | Granted | Numerical | 2007-10-11 |  | STORM/EMERGENCY | 18 | Standby Pumps | 2
14147 | Chippenham Westmead SPS | SPS | 100823 | Granted | Numerical | 1999-09-10 |  | STORM/EMERGENCY | 155 | Standby Pumps | 5
14149 | Chippenham Field View SPS | SPS | 100805 | Granted | Numerical | 1999-09-10 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14151 | Dauntsey The Green SPS | SPS | 102280 | Granted | Numerical | 2003-12-15 | Takes effect 31/12/2003 | STORM/EMERGENCY | 5.6 | Standby Pumps | 6
14152 | Broads Green . SPS | SPS | 101985 | Granted | Numerical | 2002-11-29 | TAKES EFFECT 28/2/03 | STORM/EMERGENCY | 7.6 | Standby Pumps | 3
14157 | Calne Rough Leaze SPS | SPS | 101356 | Granted | Numerical | 2000-11-21 | Effective from 30/12/2000 | STORM/EMERGENCY | 20 | Standby Pumps | 2
14158 | Hullavington Raf Station SPS | SPS | 101678 | Granted | Numerical | 2002-01-11 | TAKES EFFECT 31/3/2002 | STORM/EMERGENCY | 4.8 | Standby Pumps | 2
14161 | Compton Bassett The Pond SPS | SPS | 103449 | Granted | Numerical | 2006-08-09 | The Pond / Manor Farm SPS - takes effect 01/04/2007. Spills via Site 17440. | STORM/EMERGENCY | 6 | Standby Pumps | 2
14162 | Malmesbury Burton Hill SPS | SPS | 103660 | Granted | Numerical | 2007-05-04 | Telemetry to be installed by 30/09/2008 | STORM/EMERGENCY | 8 | Standby Pumps | 2
14174 | Box Mill Lane SPS | SPS | 11833 | Granted | Descriptive | 1989-09-12 | Deemed determined Apr09: MILL LANE ST8240068800 BOX. Deemed determined Sep10 with generic text conditions. PSKPM from 29/04/2016 | STORM/EMERGENCY | 27.3 | Standby Pumps | 3
14176 | Kington Langley . SPS | SPS | 101694 | Granted | Numerical | 2002-01-18 | Takes effect 31/3/2002 | STORM/EMERGENCY | 7 | Standby Pumps | 2
14179 | Biddestone Manor Cottages SPS | SPS | 102548 | Granted | Numerical | 2004-10-25 | Takes effect 01/01/2005 | STORM/EMERGENCY | 7 | Standby Pumps | 6
14185 | Malmesbury St Johns Street SPS | SPS | 12855 | Granted | Numerical | 1995-10-13 |  | STORM/EMERGENCY | 60 | Standby Pumps | 6
14188 | Lower Stanton St Quintin . SPS | SPS | EPR/AB3098VQ | Granted | Numerical | 2014-02-27 | Takes effect when granted. Flow Meas NGR to be supplied by 27/03/2014. Flow meas must be MCERTS. DWF exceedence investigation clause. IRP requirement. PS EO management plan required. EPR/AB3098VQ. | STORM/EMERGENCY | 27.7 | Standby Pumps | 8
14192 | Upper Seagry Upper Seagry SPS | SPS | 11445 | Granted | Numerical | 1991-09-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14196 | Malmesbury Noahs Ark SPS | SPS | 101696 | Granted | Numerical | 2002-01-18 | Takes effect 31/3/02 | STORM/EMERGENCY | 39 | Standby Pumps | 2
14199 | Upper Minety Flisteridge SPS | SPS | 102549 | Granted | Numerical | 2004-07-16 | TAKES EFFECT 01/04/2005 | STORM/EMERGENCY | 12.5 | Standby Pumps | 6
14200 | Lea Lea North SPS | SPS | 101677 | Granted | Numerical | 2002-01-11 | TAKES EFFECT 31/3/2002 | STORM/EMERGENCY | 11.2 | Standby Pumps | 2
14202 | Hankerton Hankerton Bridge SPS | SPS | 2214 | Granted | Numerical | 1996-10-01 | Transferred to WSX 01/10/1996 | STORM OVERFLOW | 42 | No | 2
14216 | Stoborough Kings Arms SPS | SPS | 401198 | Granted | Numerical | 2002-04-24 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 15.3 | Standby Pumps | 2
14219 | Upton Sandy Lane SPS | SPS | 402036 | Granted | Numerical | 2006-07-03 |  | STORM/EMERGENCY | 6.4 | Standby Pumps | 2
14220 | Lytchett Matravers Bulbury Lane SPS | SPS | 401452 | Granted | Numerical | 2003-07-02 | Takes effect when granted | STORM/EMERGENCY | 26 | Standby Pumps | 4
14222 | East Knighton Blacknoll SPS | SPS | 401166 | Granted | Numerical | 2002-03-26 | TAKES EFFECT 31/3/02 | STORM/EMERGENCY | 11 | Standby Pumps | 3
14226 | Church Knowle Glebe Farm SPS | SPS | 401417 | Granted | Numerical | 2007-10-17 |  | STORM/EMERGENCY | 8 | Standby Pumps | 2
14227 | Studland Wadmore Lane SPS | SPS | 401418 | Granted | Numerical | 2007-10-17 |  | STORM/EMERGENCY | 11 | Standby Pumps | 2
14229 | Wareham West Mill Crescent SPS | SPS | 401202 | Granted | Numerical | 2002-04-15 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 16.7 | Standby Pumps | 2
14232 | Church Knowle Animal Sanctuary SPS | SPS | 401419 | Granted | Numerical | 2007-10-22 |  | STORM/EMERGENCY | 7 | Standby Pumps | 2
14235 | Bovington Duncan Crescent SPS | SPS | 401420 | Granted | Numerical | 2007-10-22 |  | STORM/EMERGENCY | 7 | Standby Pumps | 2
14237 | Winfrith Newburgh Winfrith Church SPS | SPS | 401167 | Granted | Numerical | 2002-03-26 | TAKES EFFECT 31/3/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14240 | Bovington Morris Road SPS | SPS | 401421 | Granted | Numerical | 2007-10-22 |  | STORM/EMERGENCY | 2 | Standby Pumps | 2
14243 | Morden Cock And Bottle SPS | SPS | 401197 | Granted | Numerical | 2002-01-28 | TAKES EFFECT 31/3/2002 | STORM/EMERGENCY | 13.7 | Standby Pumps | 2
14244 | Swanage Durlston Road SPS | SPS | 402252 | Granted | Numerical | 2007-06-20 | EO telemetry alarm and geny "connection" to be installed by 31/03/2008 | STORM/EMERGENCY | 11 | Standby Pumps | 2
14248 | East Burton Cross Roads SPS | SPS | 401422 | Granted | Numerical | 2007-10-22 | Takes effect when granted | STORM/EMERGENCY | 22 | Standby Pumps | 3
14252 | Studland Coombe SPS | SPS | 401199 | Granted | Numerical | 2002-04-15 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 16.2 | Standby Pumps | 2
14255 | Stoborough Ridge SPS | SPS | 401423 | Granted | Numerical | 2007-10-22 |  | STORM OVERFLOW | 5 | Standby Pumps | 2
14255 | Stoborough Ridge SPS | SPS | 401423 | Granted | Numerical | 2007-10-22 |  | EMERGENCY OVERFLOW | 5 | Standby Pumps | 2
14256 | Affpuddle . SPS | SPS | 401424 | Granted | Numerical | 2007-10-29 |  | STORM/EMERGENCY | 6 | Standby Pumps | 2
14259 | Wareham South East SPS | SPS | 402472 | Granted | Numerical | 2007-10-17 | Immediate notification of EO operation also reqd to Local Food Authority / EHO from 31/03/2011 | STORM/EMERGENCY | 54 | Standby Pumps | 2
14260 | Lytchett Matravers Glebe Road SPS | SPS | 41152 | Granted | Descriptive | 1989-10-31 | Deemed determined Sep10 with generic text conditions | STORM/EMERGENCY | 7 | Standby Pumps | 2
14261 | Studland Watery Lane SPS | SPS | 41159 | Granted | Descriptive | 1989-10-31 | Deemed determined Sep10 with generic text conditions | STORM/EMERGENCY | 2.5 | Standby Pumps | 2
14263 | Corfe Castle Red Lane SPS | SPS | 401200 | Granted | Numerical | 2002-04-15 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 18.3 | Standby Pumps | 2
14264 | East Knighton . SPS | SPS | 401425 | Granted | Numerical | 2007-10-29 |  | STORM/EMERGENCY | 1 | Standby Pumps | 2
14265 | Upton Moorlands Way SPS | SPS | 401241 | Granted | Numerical | 2002-09-10 | Takes effect 1/4/03 - replaces/modifies 50681. Storm tank overflow report to EA annually for Shellfish. | STORM/EMERGENCY | 45 | Standby Pumps | 9
14266 | Wareham Sandford Lane SPS | SPS | 401201 | Granted | Numerical | 2002-04-15 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 60 | Standby Pumps | 2
14270 | Bovington Terminal SPS | SPS | 401426 | Granted | Numerical | 2007-10-29 |  | STORM/EMERGENCY | 55 | Standby Pumps | 4
14272 | Briantspuddle . SPS | SPS | 41980 | Granted | Numerical | 1991-09-24 |  | STORM/EMERGENCY | 6 | Standby Pumps | 2
14273 | Wool Railway Cottages SPS | SPS | 401164 | Granted | Numerical | 2002-01-28 | TAKES EFFECT 31/03/2002 | STORM/EMERGENCY | 21 | Standby Pumps | 4
14274 | East Chaldon . SPS | SPS | 401427 | Granted | Numerical | 2007-10-29 |  | STORM/EMERGENCY | 4 | Standby Pumps | 2
14275 | Corfe Castle Halves Cottages SPS | SPS | 401428 | Granted | Numerical | 2007-10-29 |  | STORM/EMERGENCY | 8 | Standby Pumps | 2
14276 | Corfe Castle Studland Road SPS | SPS | 401429 | Granted | Numerical | 2007-10-29 |  | STORM/EMERGENCY | 17 | Standby Pumps | 2
14283 | Barton St David . SPS | SPS | EPR/CB3399AC | Granted | Numerical | 2015-05-28 | EPR/CB3399AC | STORM/EMERGENCY | 5.5 | Standby Pumps | 2
14285 | Misterton . SPS | SPS | 103598 | Granted | Numerical | 2007-01-29 | Takes effect 01/04/2008 | STORM/EMERGENCY | 19.8 | Standby Pumps | 3
14286 | Lopen . SPS | SPS | NPSWQD004020 | Granted | Numerical | 2008-09-10 | Geny connection / link box reqd by 30/09/2009: NPSWQD004020 | STORM/EMERGENCY | 11 | Standby Pumps | 2
14287 | Hinton St George . SPS | SPS | 102398 | Granted | Numerical | 2004-01-15 | Takes effect 01/04/2004 | STORM/EMERGENCY | 7 | Standby Pumps | 2
14288 | Marston Magna Church Lane SPS | SPS | 101772 | Granted | Numerical | 2002-05-07 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 4 | Standby Pumps | 2
14289 | Ilchester Ilchester Main SPS | SPS | 12884 | Granted | Numerical | 1996-01-15 |  | STORM/EMERGENCY | 45 | Standby Pumps | 2
14291 | West Camel . SPS | SPS | 101764 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | STORM/EMERGENCY | 3.5 | Standby Pumps | 2
14293 | Queen Camel Englands Mead Green Lane SPS | SPS | 71692 | Granted | Descriptive | 1989-09-12 | Deemed determined Apr09: GREEN LANE B ST5900024940 RIVER CAM. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 9.3 | No | 3
14294 | Donyatt . SPS | SPS | 102568 | Granted | Numerical | 2004-04-29 | Takes effect when granted | STORM/EMERGENCY | 6 | Standby Pumps | 3
14295 | Yeovilton Weir SPS | SPS | 101765 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | STORM/EMERGENCY | 5 | Standby Pumps | 5
14301 | Stalbridge . SPS | SPS | 50979 | Granted | Numerical | 1984-06-06 | Replaced / modified Dec08. Geny connection / link box reqd by 31/03/2010 | STORM/EMERGENCY | 61 | Standby Pumps | 2
14302 | Idmiston . SPS | SPS | 401574 | Granted | Numerical | 2004-02-19 | Takes effect 31/03/2004 | STORM/EMERGENCY | 14.5 | Standby Pumps | 2
14303 | Berwick St John . SPS | SPS | 41381 | Granted | Numerical | 1990-03-23 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14304 | Allington Old Inn SPS | SPS | 401580 | Granted | Numerical | 2004-02-19 | Takes effect 31/03/2004 | STORM/EMERGENCY | 6.8 | Standby Pumps | 2
14309 | Donhead St Andrew . SPS | SPS | 41380 | Granted | Numerical | 1990-03-23 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 6
14311 | Tilshead Camp Road SPS | SPS | 401790 | Granted | Numerical | 2005-04-01 |  | STORM/EMERGENCY | 12 | No | 3
14317 | Hurdcott . SPS | SPS | 401575 | Granted | Numerical | 2004-02-19 | Takes effect 31/03/2004 | STORM/EMERGENCY | 60 | Standby Pumps | 5
14323 | Amesbury Flower Lane SPS | SPS | 401046 | Granted | Numerical | 2001-06-04 | Takes effect soonest of 31/03/2004 or commissioning of works | STORM/EMERGENCY | 120 | Standby Pumps | 3
14328 | Hanging Langford . SPS | SPS | NPSWQD003662 | Granted | Numerical | 2008-09-15 | Takes effect soonest of 31/03/2010 or commissioning: NPSWQD003662. Reed bed to be maintained with even distribution, minimal weeds and no short circuiting. Spills via Site 17970. | STORM OVERFLOW | 12 | Standby Pumps | 5
14337 | Alderbury Home Farm SPS | SPS | 41885 | Granted | Numerical | 1993-05-06 |  | STORM/EMERGENCY | 22.8 | Standby Pumps | 2
14346 | Hindon The Dene SPS | SPS | 42095 | Granted | Numerical | 1992-04-09 |  | STORM/EMERGENCY | 13 | Standby Pumps | 2
14354 | Barford St Martin . SPS | SPS | 50763 | Granted | Numerical | 1977-04-28 | - | STORM/EMERGENCY | 5 | No | 2
14362 | Chilmark . SPS | SPS | 41188 | Granted | Numerical | 1989-10-31 | Deemed determined Sep10 with generic text conditions | STORM/EMERGENCY | 4.9 | Standby Pumps | 2
14368 | Mere Edgebridge SPS | SPS | 401447 | Granted | Numerical | 2003-04-25 | TAKES EFFECT 31/03/2003 | STORM/EMERGENCY | 11 | Standby Pumps | 2
14371 | Cheddar Froglands SPS | SPS | 101665 | Granted | Numerical | 2002-01-25 | TAKES EFFECT 31/3/2002 | STORM/EMERGENCY | 48 | Standby Pumps | 3
14372 | West Huntspill Sloway Lane SPS | SPS | 100880 | Granted | Numerical | 1999-11-11 |  | STORM/EMERGENCY | 130 | Standby Pumps | 7
14374 | Highbridge Newton SPS | SPS | 102480 | Granted | Numerical | 2004-03-26 | Takes effect 01/04/2004 | SETTLED STORM OVERFLOW | 300 | Standby Pumps | 20
14374 | Highbridge Newton SPS | SPS | 102480 | Granted | Numerical | 2004-03-26 | Takes effect 01/04/2004 | STORM/EMERGENCY | 300 | Standby Pumps | 20
14375 | Pedwell . SPS | SPS | 102298 | Granted | Numerical | 2004-06-23 | Takes effect when granted - telemetry required by 31/08/2004. | STORM/EMERGENCY | 16 | Standby Pumps | 1
14376 | Moorlinch Right Drove SPS | SPS | 101708 | Granted | Numerical | 2002-03-06 | TAKES EFFECT 6/3/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14378 | Bridgwater Blake Gardens SPS | SPS | 102691 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005. Telemetry alarm must inhibit Taunton Rd SPS 15393 - see consent for full conditions. | STORM/EMERGENCY | 90 | Standby Pumps | 5
14379 | Fiddington . SPS | SPS | 102215 | Granted | Numerical | 2003-09-19 | TAKES EFFECT 29/02/2004 | STORM/EMERGENCY | 5.3 | Standby Pumps | 2
14380 | North Newton Church Road SPS | SPS | 101802 | Granted | Numerical | 2002-05-27 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 13.2 | Standby Pumps | 2
14383 | Combwich Brookside SPS | SPS | 101714 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14384 | Bridgwater Chilton Street Saltlands SPS | SPS | 102690 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 242 | Standby Pumps | 10
14385 | Bridgwater Bristol Road SPS | SPS | 82162 | Granted | Numerical | 1982-10-08 |  | STORM/EMERGENCY | 160 | No | 9
14386 | Greinton Moor Drive SPS | SPS | 102299 | Granted | Numerical | 2004-06-23 | Takes effect when granted - telemetry required by 31/08/2004. PS EO management plan required from 27/09/2013. | STORM/EMERGENCY | 34 | Standby Pumps | 2
14388 | Berkeley Park View Road SPS | SPS | 103822 | Granted | Numerical | 2007-10-17 |  | STORM/EMERGENCY | 40 | Standby Pumps | 2
14389 | Taunton Priory Storm Tanks SPS | SPS | 102258 | Granted | Numerical | 2004-01-07 | Takes effect 01/04/2004. Spills via Site 13240. | SETTLED STORM OVERFLOW | 360 | No | 10
14389 | Taunton Priory Storm Tanks SPS | SPS | 102258 | Granted | Numerical | 2004-01-07 | Takes effect 01/04/2004. Spills via Site 13240. | STORM OVERFLOW | 360 | No | 10
14391 | Stoke St Gregory No 1 Lane End SPS | SPS | 101803 | Granted | Numerical | 2002-03-26 | TAKES EFFECT 1/4/02 | STORM/EMERGENCY | 27 | Standby Pumps | 4
14392 | West Buckland . SPS | SPS | 101804 | Granted | Numerical | 2002-05-27 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 10 | Standby Pumps | 2
14393 | Hillfarrance . SPS | SPS | 101805 | Granted | Numerical | 2002-03-26 | TAKES EFFECT 31/3/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14394 | Wellington Mitchells Pool SPS | SPS | 100238 | Granted | Numerical | 1997-06-30 | EDM effective 31/07/2017 | STORM/EMERGENCY | 70 | No | 4
14395 | Hatch Beauchamp . SPS | SPS | 70916 | Granted | Numerical | 1989-09-12 | Deemed determined Apr09: PALMERS GREE ST3066020040 STREAM. Deemed determined Sep10 with generic text conditions. Spills via Site 16748. | STORM OVERFLOW | 4 | Standby Pumps | 2
14397 | Beer Hackett . SPS | SPS | NPSWQD008609 | Granted | Numerical | 2009-09-04 | Takes effect when granted: NPSWQD008609 | STORM/EMERGENCY | 29 | Standby Pumps | 2
14399 | Osmington Mills . SPS | SPS | 50777 | Granted | Numerical | 1977-02-02 | 14399 SPS has local overflow permitted for emergency operation. 17762 CSO is the second overflow in an emergency. | EMERGENCY OVERFLOW | #N/A | No | 3
14402 | Osmington Pontins SPS | SPS | 51316 | Granted | Numerical | 1987-10-15 | Deemed determined Sep10 with generic text conditions | STORM/EMERGENCY | 11 | Standby Pumps | 2
14404 | Beaminster Southgate SPS | SPS | 401557 | Granted | Numerical | 2004-02-26 | Takes effect 31/03/2004 | STORM/EMERGENCY | 31 | Standby Pumps | 7
14405 | West Stafford Dorchester Road SPS | SPS | 401967 | Granted | Numerical | 2005-11-30 |  | STORM/EMERGENCY | 14.1 | Standby Pumps | 2
14410 | Burton Bradstock Burton Southover SPS | SPS | 401968 | Granted | Numerical | 2005-11-30 |  | STORM/EMERGENCY | 12 | Standby Pumps | 2
14411 | Sydling St Nicholas . SPS | SPS | 401196 | Granted | Numerical | 2002-02-18 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 17 | Standby Pumps | 3
14412 | Puddletown Blandford Road SPS | SPS | 401976 | Granted | Numerical | 2005-11-30 | Takes effect when granted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
14413 | Chideock Seatown SPS | SPS | 43190 | Granted | Numerical | 1997-12-04 |  | STORM/EMERGENCY | 9.7 | Standby Pumps | 2
14414 | Charminster North Street SPS | SPS | 402447 | Granted | Numerical | 2007-09-21 | Takes effect 01/04/2009 | STORM/EMERGENCY | 45 | Standby Pumps | 4
14415 | Litton Cheney Chicksbridge SPS | SPS | 401592 | Granted | Numerical | 2004-02-26 | Takes effect 01/04/2004 | STORM/EMERGENCY | 5.3 | Standby Pumps | 3
14417 | Dunster Dunster Beach SPS | SPS | 71179 | Granted | Numerical | 1991-04-08 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 1
14420 | Minehead Quay West SPS | SPS | 101776 | Granted | Numerical | 2002-03-22 | TAKES EFFECT 01/04/2002 | STORM/EMERGENCY | 14 | Standby Pumps | 3
14421 | Cutcombe . SPS | SPS | 71428 | Granted | Numerical | 1991-02-27 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14423 | Blue Anchor Pill Bridge SPS | SPS | 102437 | Granted | Numerical | 2006-02-14 | Takes effect when granted | STORM/EMERGENCY | 18 | Standby Pumps | 6
14425 | Clutton Greenbrook SPS | SPS | 102915 | Granted | Numerical | 2005-07-06 | Takes effect when granted | STORM/EMERGENCY | 30.9 | Standby Pumps | 3
14426 | Paulton Goosard Bridge SPS | SPS | 102216 | Granted | Numerical | 2003-12-04 | Takes effect when granted | STORM/EMERGENCY | 50 | Standby Pumps | 3
14427 | Hallatrow . SPS | SPS | 101867 | Granted | Numerical | 2002-08-14 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 52 | Standby Pumps | 5
14428 | Corston Newton St Loe SPS | SPS | 10300 | Granted | Numerical | 1989-06-13 | WWA CORSTON P.S. S.W.O. | STORM/EMERGENCY | 23.5 | No | 2
14429 | Chew Stoke Bilbie Road SPS | SPS | 21523 | Granted | Numerical | 1967-03-21 |  | STORM/EMERGENCY | 12.3 | No | 4
14430 | Chew Magna Dumpers Lane SPS | SPS | 102223 | Granted | Numerical | 2003-12-04 | Takes effect 01/02/2005 | STORM/EMERGENCY | 94 | Standby Pumps | 6
14431 | Bishop Sutton . SPS | SPS | EPR/ZP3821GK | Granted | Numerical | 2013-04-16 | Takes effect when granted. PS EO management plan required. EPR/ZP3821GK. | STORM/EMERGENCY | 19.6 | Standby Pumps | 5
14432 | Compton Dando Turnbridge SPS | SPS | 103604 | Granted | Numerical | 2007-05-04 | Telemetry required by 30/09/2008, "Geny connection" by 31/03/2008 | STORM/EMERGENCY | 3.1 | Standby Pumps | 4
14437 | Warminster Portway SPS | SPS | 401658 | Granted | Numerical | 2006-02-12 | Takes effect when granted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14439 | Warminster Calveswater SPS | SPS | 401094 | Granted | Numerical | 2001-10-30 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 95 | Standby Pumps | 3
14440 | Dilton Marsh Pen Knapp SPS | SPS | 103205 | Granted | Numerical | 2005-12-19 | Spills via Site 16902. | STORM/EMERGENCY | 10 | Standby Pumps | 2
14444 | Wingfield Church Lane SPS | SPS | 102026 | Granted | Numerical | 2002-10-21 | TAKES EFFECT 31/3/03 | STORM/EMERGENCY | 2.9 | Standby Pumps | 4
14447 | Keevil The Street SPS | SPS | 11447 | Granted | Numerical | 1991-02-27 |  | STORM/EMERGENCY | 37 | Standby Pumps | 3
14450 | Coulston . SPS | SPS | 103785 | Granted | Numerical | 2007-10-11 | Geny connection/link box required by 31/03/2008 | STORM/EMERGENCY | 3.4 | Standby Pumps | 2
14452 | Freshford New Inn SPS | SPS | 103786 | Granted | Numerical | 2007-10-11 | Geny connection/link box required by 31/03/2008 | STORM/EMERGENCY | 5 | Standby Pumps | 2
14453 | Staverton Nestles SPS | SPS | 101871 | Granted | Numerical | 2002-10-21 | Takes effect 21/10/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
14456 | Bratton Trowbridge Road SPS | SPS | 103243 | Granted | Numerical | 2007-03-16 |  | STORM/EMERGENCY | 18 | Standby Pumps | 2
14457 | Bulkington Wickleaze SPS | SPS | 11485 | Granted | Numerical | 1989-10-31 | Deemed determined Apr09: BULKINGTON ST9430058300 SEMMINGTON BROOK. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 3.3 | Standby Pumps | 2
14458 | North Bradley Churchlands SPS | SPS | 103244 | Granted | Numerical | 2007-03-16 | Telemetry required by 30/06/2007 | STORM/EMERGENCY | 6 | Standby Pumps | 2
14459 | Southwick Chantry Gardens SPS | SPS | 21630 | Granted | Numerical | 1981-07-01 | PS EO management plan required from 31/03/2014 | STORM/EMERGENCY | 22 | Standby Pumps | 6
14462 | Broughton Gifford Curtis Orchard SPS | SPS | 100633 | Granted | Numerical | 1999-06-09 | Telemetry reqd by 31/03/2001. See NoM, Sep08. Geny connection / link box reqd by 30/09/2009. | STORM/EMERGENCY | 3 | Standby Pumps | 2
14463 | Atworth Purlpit SPS | SPS | 100631 | Granted | Numerical | 1999-06-09 | Telemetry reqd by 31/03/2001 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14466 | Semington Semington Brook SPS | SPS | 102810 | Granted | Numerical | 2005-04-01 |  | STORM/EMERGENCY | 18 | Standby Pumps | 3
14467 | Holt The Star SPS | SPS | 101024 | Granted | Numerical | 1999-11-11 |  | STORM/EMERGENCY | 101 | No | 2
14468 | Melksham Semington Road SPS | SPS | 100635 | Granted | Numerical | 1999-06-09 | Telemetry reqd by 31/03/2001. See NoM, Sep08. Geny connection / link box reqd by 30/09/2009. | STORM/EMERGENCY | 7 | Standby Pumps | 2
14469 | Great Hinton . SPS | SPS | NPSWQD008924 | Granted | Numerical | 2009-12-02 | Telemetry to be fitted by 01/04/2010: NPSWQD008924 | STORM/EMERGENCY | 1.6 | Standby Pumps | 2
14473 | Bradford-On-Avon Woolley Green SPS | SPS | 102089 | Granted | Numerical | 2007-10-29 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14474 | Melksham Semington Roundabout SPS | SPS | 100632 | Granted | Numerical | 1999-06-09 | Spills via Site 16912. | STORM/EMERGENCY | 19 | Standby Pumps | 2
14475 | Broughton Gifford The Green SPS | SPS | 100634 | Granted | Numerical | 1999-06-09 | Telemetry reqd by 31/03/2001. Replaced / modified Dec08. Geny connection / link box reqd by 31/03/2010. | STORM/EMERGENCY | 12.2 | Standby Pumps | 2
14486 | Bradford-On-Avon Springfield SPS | SPS | 102061 | Granted | Numerical | 2003-03-25 | Takes effect when granted; TELEMETRY must be provided by 31/03/2005. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14487 | Melksham Berryfields SPS | SPS | 100636 | Granted | Numerical | 1999-06-10 | Telemetry reqd by 31/03/2004 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
14488 | Monkton Farleigh Church Farm SPS | SPS | 100512 | Granted | Numerical | 1998-06-08 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14495 | Clevedon Clevedon Main SPS | SPS | 102134 | Granted | Numerical | 2004-03-17 | Takes effect 01/04/2004 | STORM OVERFLOW | 335 | Standby Pumps | 8
14501 | Bristol Whitby Road St Annes SPS | SPS | 21440 | Granted | Numerical | 1977-01-01 |  | STORM OVERFLOW | 92.1 | No | 2
14502 | Bristol Whitby Road B Co-Op Depot Arnos Vale SPS | SPS | 21674 | Granted | Numerical | 1987-08-01 | Info from EA April 2010. Granted date is approx only. | STORM/EMERGENCY | 30 | No | 2
14505 | Langley Burrel Peckingell Lane SPS | SPS | 11550 | Granted | Numerical | 1991-01-10 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14507 | Shirehampton Lamplighters SPS | SPS | 11540 | Granted | Numerical | 1991-11-08 |  | STORM/EMERGENCY | 37 | Standby Pumps | 2
14508 | Shirehampton Cerney Lane SPS | SPS | 11541 | Granted | Numerical | 1991-11-08 | Also called Nibley Road SPS. Telemetry to be installed by 8 Nov 1992. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14512 | Glastonbury Palmers Road SPS | SPS | 71659 | Granted | Numerical | 1992-02-19 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
14519 | Somerton Barpool Lane SPS | SPS | 70695 | Granted | Numerical | 1989-08-25 | DOE REF: COPA NO. 20245 | EMERGENCY OVERFLOW | #N/A | No | 2
14520 | Heywood Dursley Road SPS | SPS | 11840 | Granted | Numerical | 1991-12-06 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14521 | East Lambrook . SPS | SPS | 71741 | Granted | Numerical | 1992-03-03 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14525 | Babcary Riverside Farm SPS | SPS | 71661 | Granted | Numerical | 1991-09-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14526 | Sopworth . SPS | SPS | 11578 | Granted | Numerical | 1993-02-19 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14528 | Carlingcott Stoneage Lane SPS | SPS | 13269 | Granted | Numerical | 1996-09-30 | Geny Connection / link box to be provided by 31/03/2009 | STORM/EMERGENCY | 50 | Standby Pumps | 3
14531 | Midford Tucking Mill SPS | SPS | 21434 | Granted | Numerical | 1973-01-31 |  | SETTLED STORM OVERFLOW | 6 | No | 2
14532 | Midsomer Norton Rackvernal Court SPS | SPS | 11460 | Granted | Numerical | 1990-03-23 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14535 | Street The Withys Fielding Road SPS | SPS | 72185 | Granted | Numerical | 1993-03-26 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
14540 | Bradford-On-Avon Weavers Brook / St Aldhelms SPS | SPS | 102072 | Granted | Numerical | 2007-10-29 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14542 | Coat Cripple Street (Old Stw Site) SPS | SPS | 71742 | Granted | Numerical | 1992-04-09 | OLD SITE ID : 15280 - BETTER INFO JACQUI RODGERS. See NoM, Sep08. Geny connection / link box reqd by 30/09/2009. | STORM/EMERGENCY | 2.2 | Standby Pumps | 2
14547 | West Harptree . SPS | SPS | 11538 | Granted | Numerical | 1991-02-27 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
14550 | Lacock Nethercote Hill SPS | SPS | 10701 | Granted | Numerical | 1989-10-31 | Deemed determined Sep10 with generic text conditions | STORM/EMERGENCY | 13.5 | Standby Pumps | 3
14554 | Chard Touches Lane SPS | SPS | 71533 | Granted | Numerical | 1991-03-25 | ADOPTED | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14555 | Isle Abbotts Two Bridges SPS | SPS | 71874 | Granted | Numerical | 1992-07-14 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 4
14562 | Glastonbury Wirral Park SPS | SPS | 103823 | Granted | Numerical | 2007-10-17 |  | STORM/EMERGENCY | 3 | Standby Pumps | 4
14563 | Frome Courts Barton Marston Lane SPS | SPS | 102701 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 8 | Standby Pumps | 2
14564 | Chippenham Monkton Park SPS | SPS | 12655 | Granted | Numerical | 1995-01-18 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14573 | Warmley Horsecroft Gardens / Wraxall Road SPS | SPS | 11598 | Granted | Numerical | 1991-06-26 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14577 | Ford Green Lane SPS | SPS | 401576 | Granted | Numerical | 2004-02-19 | Takes effect 31/03/2004 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14580 | Bristol Ullswater Close SPS | SPS | 103824 | Granted | Numerical | 2007-10-17 | Geny connection/link box required by 31/03/2008 | STORM/EMERGENCY | 12 | Standby Pumps | 2
14581 | Bristol Victoria Road SPS | SPS | 12020 | Granted | Numerical | 1996-07-23 |  | STORM/EMERGENCY | 111 | Standby Pumps | 2
14582 | Bristol Riverside St Annes SPS | SPS | 13389 | Granted | Numerical | 1996-08-30 | ADOPTED | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14583 | Bristol West Town Road SPS | SPS | 102067 | Granted | Numerical | 2003-03-26 | TAKES EFFECT 31/03/2003 | STORM/EMERGENCY | 40 | Standby Pumps | 2
14585 | Edington Broadmead Lane (Som) SPS | SPS | NPSWQD006726 | Granted | Numerical | 2009-05-11 | Takes effect soonest of 30/06/2010 or AMP 4 commissioning: NPSWQD006726 | STORM/EMERGENCY | 14 | Standby Pumps | 2
14588 | West Lulworth Lulworth Outfall Ps SPS | SPS | 401864 | Granted | Numerical | 2005-03-24 | WEST LULWORTH BEACH SPS (NEXT TO POND). Replaces Schedule PE/01 from 30/04/2006. | STORM/EMERGENCY | 10.5 | Standby Pumps | 2
14600 | Highbridge Tylers End SPS | SPS | 71039 | Granted | Numerical | 1990-02-01 |  | SURFACE WATER ONLY | #N/A | No | 2
14618 | Bristol Butlers Walk Crews Hole SPS | SPS | 100277 | Granted | Numerical | 1997-06-30 | Telemetry to be installed by 30/06/1998 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14620 | Pewsey Salisbury Road SPS | SPS | 41656 | Deemed | Other | 1990-09-19 | LAND ADJACENT TO HILL VIEW, SALISBURY ROAD, PEWSEY (ST 1570 5913) | STORM/EMERGENCY | 11.3 | Standby Pumps | 2
14621 | Portishead Town Harbour Road SPS | SPS | 70309 | Granted | Numerical | 1986-12-01 | Date is application | EMERGENCY OVERFLOW | 260 | Standby Pumps | 9
14621 | Portishead Town Harbour Road SPS | SPS | 70308 | Granted | Numerical | 1987-07-15 | AMP 4 modification takes effect 01/04/2008 - 6mm screening (See NoMs) | EMERGENCY OVERFLOW | 260 | Standby Pumps | 9
14621 | Portishead Town Harbour Road SPS | SPS | 70308 | Granted | Numerical | 1987-07-15 | AMP 4 modification takes effect 01/04/2008 - 6mm screening (See NoMs) | STORM OVERFLOW | 260 | Standby Pumps | 9
14624 | Saltford Mead Lane SPS | SPS | 11904 | Granted | Numerical | 1992-04-09 |  | STORM/EMERGENCY | 7 | Standby Pumps | 2
14627 | Wickwar Inlet P.S SPS | SPS | 11539 | Granted | Numerical | 1990-11-07 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14632 | Taunton Maidenbrook SPS | SPS | 70804 | Granted | Numerical | 1989-10-31 | Deemed determined Apr09: REFUSE TIP ST2440025700 RIVER TONE. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 82.1 | No | 3
14634 | Wellington Farthings Pitts SPS | SPS | 100137 | Granted | Numerical | 1997-03-24 | Swains Lane / Farthings Pitt | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
14648 | Chilton Polden Main SPS | SPS | 72076 | Granted | Numerical | 1992-10-23 |  | STORM/EMERGENCY | 36 | Standby Pumps | 2
14649 | Taunton Lisieux Way SPS | SPS | 72694 | Granted | Numerical | 1995-04-11 | Adopted 19/08/98 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
15002 | Boscombe No 1 SPS | SPS | 400551 | Granted | Numerical | 2000-01-25 | Surfline site | STORM/EMERGENCY | 45 | Standby Pumps | 4
15007 | Bournemouth Iford Lane Tuckton SPS | SPS | 401244 | Granted | Numerical | 2002-10-14 | Replaces 42469 by modification from 14/10/02 | STORM/EMERGENCY | 65 | Standby Pumps | 3
15013 | Southbourne Hengistbury Head SPS | SPS | 400550 | Granted | Numerical | 2000-01-25 | Takes effect when granted. Surfline site. | STORM/EMERGENCY | 370 | Standby Pumps | 3
15019 | Bournemouth No 1 SPS | SPS | 400758 | Granted | Numerical | 2000-01-25 | Surfline site | STORM/EMERGENCY | 750 | Standby Pumps | 6
15042 | Burton Stony Lane SPS | SPS | 402473 | Granted | Numerical | 2007-10-17 |  | STORM/EMERGENCY | 35 | Standby Pumps | 4
15043 | Mudeford Mudeford Gardens SPS | SPS | 401748 | Granted | Numerical | 2005-01-31 |  | STORM/EMERGENCY | 90 | Standby Pumps | 4
15047 | Ferndown Redwood Drive SPS | SPS | 400647 | Granted | Numerical | 1999-07-29 |  | STORM/EMERGENCY | 6.5 | Standby Pumps | 2
15048 | Verwood Acacia Avenue SPS | SPS | 400642 | Granted | Numerical | 1999-07-29 |  | STORM/EMERGENCY | 8 | Standby Pumps | 2
15051 | Corfe Mullen Rushcombe Bottom SPS | SPS | 401393 | Granted | Numerical | 2003-07-29 | Takes effect when granted | STORM/EMERGENCY | 25 | Standby Pumps | 3
15052 | Verwood Ebblake SPS | SPS | 400643 | Granted | Numerical | 1999-07-29 |  | STORM/EMERGENCY | 5 | Standby Pumps | 2
15053 | Ferndown Golf Links Road SPS | SPS | 401404 | Granted | Numerical | 2003-03-11 | TAKES EFFECT 31/03/2003 | STORM/EMERGENCY | 80 | Standby Pumps | 3
15057 | Ferndown Thames Close SPS | SPS | 401154 | Granted | Numerical | 2002-02-18 | TAKES EFFECT 31/3/03 | STORM/EMERGENCY | 14 | Standby Pumps | 2
15060 | West Moors Pennington Copse SPS | SPS | 400645 | Granted | Numerical | 1999-07-29 |  | STORM/EMERGENCY | 50 | Standby Pumps | 2
15063 | Sturminster Marshall Newton Road SPS | SPS | 401278 | Granted | Numerical | 2002-08-01 | TAKES EFFECT WHEN GRANTED | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15068 | St Leonards Wayside Road No 1 SPS | SPS | 402453 | Granted | Numerical | 2007-10-11 |  | STORM/EMERGENCY | 40 | Standby Pumps | 4
15069 | Wimborne East Borough Road SPS | SPS | 400398 | Granted | Numerical | 1997-08-29 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
15070 | Wimborne Hayes Lane Colehill SPS | SPS | 401780 | Granted | Numerical | 2005-03-16 | Takes effect 01/04/2005. Spills via Site 16941. | STORM/EMERGENCY | 100 | Standby Pumps | 4
15071 | St Leonards Craigside Road SPS | SPS | 401243 | Granted | Numerical | 2002-07-25 | Spills via Site 19955. | STORM/EMERGENCY | 73 | Standby Pumps | 4
15072 | Ferndown Ameysford Road SPS | SPS | 400646 | Granted | Numerical | 1999-07-29 |  | STORM/EMERGENCY | 50 | Standby Pumps | 2
15073 | Wimborne Pilford Heath SPS | SPS | 42514 | Granted | Numerical | 1993-06-17 |  | STORM/EMERGENCY | 47 | Standby Pumps | 3
15075 | Corfe Mullen Pardys Hill SPS | SPS | 401392 | Granted | Numerical | 2004-02-17 | Takes effect when granted | STORM/EMERGENCY | 42 | Standby Pumps | 2
15078 | Ferndown A31 Tricketts Cross SPS | SPS | 401156 | Granted | Numerical | 2002-02-18 | TAKES EFFECT 31/3/03 | STORM/EMERGENCY | 218 | Standby Pumps | 3
15079 | Wimborne Poole Road SPS | SPS | 401624 | Granted | Numerical | 2004-03-06 | Takes effect 01/04/2004 | STORM/EMERGENCY | 55 | Standby Pumps | 3
15080 | Ferndown Dugdell Close SPS | SPS | 400649 | Granted | Numerical | 1999-07-29 |  | STORM/EMERGENCY | 173 | Standby Pumps | 3
15082 | Wimborne Brook Road No 1 SPS | SPS | 401779 | Granted | Numerical | 2005-03-16 | Takes effect 01/04/2005 | STORM/EMERGENCY | 130 | Standby Pumps | 3
15083 | St Leonards Forest Edge Drive SPS | SPS | 402454 | Granted | Numerical | 2007-10-11 | Geny connection/link box required by 31/03/2008 | STORM/EMERGENCY | 10 | Standby Pumps | 2
15084 | Verwood Potterne Way SPS | SPS | 401155 | Granted | Numerical | 2002-02-18 | TAKES EFFECT 31/3/03 | STORM/EMERGENCY | 108 | Standby Pumps | 4
15088 | Alderholt Sandleheath Road SPS | SPS | 401245 | Granted | Numerical | 2002-10-14 | Replaces 40541 by modification from 14/10/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15090 | West Parley Church Lane SPS | SPS | 401157 | Granted | Numerical | 2002-02-18 | TAKES EFFECT 31/3/02 | STORM/EMERGENCY | 118 | Standby Pumps | 3
15091 | Ferndown Aldridge Road SPS | SPS | 400641 | Granted | Numerical | 1999-07-29 | 19468 CSO adjacent, permitted separately. | STORM/EMERGENCY | 28 | Standby Pumps | 2
15095 | Stert Fullaway Farm SPS | SPS | 101809 | Granted | Numerical | 2002-05-09 | TAKES EFFECT WHEN GRANTED | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15100 | North Newnton . SPS | SPS | 402067 | Granted | Numerical | 2007-05-30 | Takes effect 31/07/2007 | STORM/EMERGENCY | 10 | Standby Pumps | 2
15101 | Patney Patney Weir SPS | SPS | 401225 | Granted | Numerical | 2002-05-08 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 2.9 | Standby Pumps | 2
15102 | Marston The Plough SPS | SPS | 101810 | Granted | Numerical | 2002-05-09 | TAKES EFFECT WHEN GRANTED | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15103 | Bromham Loop Hill SPS | SPS | 101693 | Granted | Numerical | 2002-01-11 | TAKES EFFECT 31/03/2002 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15106 | Poulshot Townsend SPS | SPS | 102478 | Granted | Numerical | 2004-03-11 | Takes effect 01/04/2004 | STORM/EMERGENCY | 17 | Standby Pumps | 3
15111 | All Cannings . SPS | SPS | 401226 | Granted | Numerical | 2002-05-08 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 8.5 | Standby Pumps | 2
15115 | Chirton Small Street SPS | SPS | 401765 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 8 | Standby Pumps | 2
15117 | Devizes Dunkirk Hill SPS | SPS | 101767 | Granted | Numerical | 2002-05-07 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 14.6 | Standby Pumps | 2
15120 | Allington . SPS | SPS | 401227 | Granted | Numerical | 2002-05-08 | TAKES EFFECT WHEN GRANTED | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15123 | Seend Bell Inn / Bell Hill SPS | SPS | 102808 | Granted | Numerical | 2005-04-01 |  | STORM/EMERGENCY | 4 | Standby Pumps | 2
15125 | Worton Mill Road SPS | SPS | 102479 | Granted | Numerical | 2004-03-11 | Takes effect 01/04/2004 | STORM/EMERGENCY | 11 | Standby Pumps | 2
15128 | Seend Sellsgreen SPS | SPS | 101813 | Granted | Numerical | 2002-05-09 | TAKES EFFECT WHEN GRANTED | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15129 | Potterne Wick SPS | SPS | 101814 | Granted | Numerical | 2002-05-09 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 6.4 | Standby Pumps | 2
15139 | Pilning Swanmoor Bridge SPS | SPS | 101958 | Granted | Numerical | 2002-12-10 | Takes effect when granted | STORM/EMERGENCY | 17 | Standby Pumps | 2
15146 | Frampton Cotterell Church Road SPS | SPS | 101034 | Granted | Numerical | 2000-03-07 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15158 | Olveston The Common SPS | SPS | 101837 | Granted | Numerical | 2002-08-12 | TAKES EFFECT 31/3/03 | STORM/EMERGENCY | 21 | Standby Pumps | 2
15166 | Rangeworthy Berrows Mead SPS | SPS | 103233 | Granted | Numerical | 2006-02-12 | Takes effect soonest of 01/04/2007 or works commissioning | STORM/EMERGENCY | 8 | Standby Pumps | 3
15167 | Cromhall Jubilee Lane SPS | SPS | 103286 | Granted | Numerical | 2006-07-25 | Takes effect 01/04/2007 | STORM/EMERGENCY | 12 | Standby Pumps | 4
15170 | Horton Kings Lane SPS | SPS | 102905 | Granted | Numerical | 2005-07-05 | Takes effect when granted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15173 | Almondsbury Hortham Lane SPS | SPS | 101352 | Granted | Numerical | 2000-11-21 | Effective from 20/11/00. notlist. storage of 94 m3 to be provided and fully used before storm discharge starts+ 6 hrs of dry weather flow storage upstream, above wet well design top water level. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
15186 | Iron Acton Latteridge Road SPS | SPS | 102906 | Granted | Numerical | 2005-07-05 | Takes effect when granted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15188 | Yate North Road SPS | SPS | 101589 | Granted | Numerical | 2001-10-16 | Takes effect 31/03/2002 | STORM/EMERGENCY | 20 | Standby Pumps | 2
15189 | Aust Village SPS | SPS | 10692 | Granted | Numerical | 1989-10-31 | Deemed determined Sep10 with generic text conditions | STORM/EMERGENCY | 3.1 | Standby Pumps | 2
15190 | Milborne St Andrew Manor Farm SPS | SPS | 42113 | Granted | Numerical | 1992-05-12 |  | STORM/EMERGENCY | 47 | Standby Pumps | 6
15193 | Child Okeford Gold Hill SPS | SPS | 402218 | Granted | Numerical | 2007-05-04 | Telemetry required by 30/09/2008 and "Geny connection" by 31/03/2008 | STORM/EMERGENCY | 5.3 | Standby Pumps | 3
15196 | Sturminster Newton The Bridge SPS | SPS | 402224 | Granted | Numerical | 2007-02-09 |  | STORM/EMERGENCY | 13.7 | Standby Pumps | 2
15197 | Blandford Brewery No 2 SPS | SPS | 40861 | Granted | Numerical | 1990-10-18 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
15200 | Marnhull Sodom Lane SPS | SPS | 402474 | Granted | Numerical | 2007-10-17 |  | STORM/EMERGENCY | 19 | Standby Pumps | 3
15201 | Durweston Water Lane SPS | SPS | 402475 | Granted | Numerical | 2007-10-17 | Geny connection/link box required by 31/03/2008 | STORM/EMERGENCY | 7 | No | 2
15203 | Shillingstone Haywards Bridge SPS | SPS | 402500 | Granted | Numerical | 2007-10-17 | Geny connection/link box required by 31/03/2008 | STORM/EMERGENCY | 8.5 | Standby Pumps | 2
15205 | Blandford St Mary Bournemouth Road SPS | SPS | 402254 | Granted | Numerical | 2007-10-11 | Takes effect when granted. PS EO management plan required. | STORM/EMERGENCY | 12 | Standby Pumps | 2
15206 | Blandford Langton Road (Blandford No 1) SPS | SPS | 401302 | Granted | Numerical | 2002-11-02 | TAKES EFFECT 31/1/03 | STORM/EMERGENCY | 89 | Standby Pumps | 3
15207 | Shaftesbury Long Cross SPS | SPS | 401300 | Granted | Numerical | 2002-11-02 | TAKES EFFECT 31/1/03 | STORM/EMERGENCY | 15 | Standby Pumps | 2
15209 | Spetisbury Crawford Bridge SPS | SPS | 402313 | Granted | Numerical | 2007-03-16 |  | STORM/EMERGENCY | 7 | Standby Pumps | 2
15228 | Poole Rockley Road SPS | SPS | 400790 | Granted | Numerical | 2000-02-14 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15229 | Poole Whitecliff Recreation Ground SPS | SPS | 51301 | Granted | Numerical | 1987-10-15 | Deemed determined Sep10 with generic text conditions | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15230 | Poole Kennart Road SPS | SPS | EPR/QB3993NE | Granted | Numerical | 2013-08-27 | Takes effect when granted. EPR/QB3993NE. PS EO management plan included. Spill monitoring required by 01/04/2016. | STORM/EMERGENCY | 12 | Standby Pumps | 2
15231 | Poole Sandbanks Pavilion SPS | SPS | 51303 | Granted | Numerical | 1987-10-15 | Immediate notification of EO operation also reqd to Local Food Authority / EHO from 30/04/2011. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 18 | Standby Pumps | 2
15232 | Poole Salterns Way SPS | SPS | 51302 | Granted | Descriptive | 1987-10-15 | Deemed determined Sep10 with generic text conditions | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15235 | Poole Shore Road SPS | SPS | 51290 | Granted | Numerical | 1987-10-15 | Original deemed consent. EA agreed to operational rules specified by WSX in Jul09 - see consent archive for full details and #878558. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 60 | Standby Pumps | 10
15236 | Poole Canford Heath Road SPS | SPS | 401619 | Granted | Numerical | 2004-11-09 |  | STORM/EMERGENCY | 44 | Standby Pumps | 4
15237 | Poole Magna Road SPS | SPS | 400714 | Granted | Numerical | 1999-08-18 | Takes effect when granted | STORM/EMERGENCY | 100 | Standby Pumps | 6
15239 | Poole Poole Park SPS | SPS | 400718 | Granted | Numerical | 2000-02-14 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
15240 | Poole Branksome Chine SPS | SPS | NPSWQD003865 | Granted | Numerical | 2008-11-28 | Takes effect 01/04/2009. Surfline site. See consent doc for full pass forward flow rules - updated schematic required before 31/03/2010. NPSWQD003865. | STORM/EMERGENCY | 58 | Standby Pumps | 5
15243 | Bridgwater East Quay SPS | SPS | 71343 | Granted | Numerical | 1991-02-27 |  | STORM/EMERGENCY | 179 | Standby Pumps | 9
15246 | Canford Magna Canford Main SPS | SPS | 40821 | Granted | Numerical | 1991-09-24 |  | STORM/EMERGENCY | 80 | Standby Pumps | 4
15247 | Poole Rectory / Ashmore Avenue SPS | SPS | 400849 | Granted | Numerical | 1999-12-22 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
15252 | Poole Egmont Road SPS | SPS | 402037 | Granted | Numerical | 2006-07-03 | Actually modifies 050678, PS EO management plan required | STORM/EMERGENCY | 10.6 | Standby Pumps | 2
15253 | Poole Fairview Road SPS | SPS | 401394 | Granted | Numerical | 2003-07-29 | Takes effect when granted | STORM/EMERGENCY | 13.3 | Standby Pumps | 2
15257 | Poole Poole Bridge Poole Quay SPS | SPS | 400719 | Granted | Numerical | 2000-02-14 | Immediate notification of EO operation also reqd to Local Food Authority / EHO from 31/03/2011 | STORM/EMERGENCY | 15 | Standby Pumps | 2
15258 | Poole Willis Way SPS | SPS | 401620 | Granted | Numerical | 2004-11-09 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15260 | Poole Esplanade Sterte SPS | SPS | 400742 | Granted | Numerical | 2000-01-04 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15262 | Poole Park Lake Road SPS | SPS | 400716 | Granted | Numerical | 2000-02-14 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15265 | Poole Canford School SPS | SPS | 401256 | Granted | Numerical | 2002-08-29 | Takes effect when granted; actually a modification of 40460 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15266 | Poole Merley Lane Merley SPS | SPS | 40459 | Granted | Numerical | 1988-09-26 | WWA MERLEY LANE PUMPING STATION POOLE 160287 | EMERGENCY OVERFLOW | #N/A | No | 2
15269 | Poole Blandford Road SPS | SPS | 400792 | Granted | Numerical | 2000-02-14 | Spills via Site 19848. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15270 | Poole Creekmoor Lane SPS | SPS | 401047 | Granted | Numerical | 2001-12-20 | TAKES EFFECT 31/3/2003 | STORM OVERFLOW | 120 | Standby Pumps | 2
15270 | Poole Creekmoor Lane SPS | SPS | 401047 | Granted | Numerical | 2001-12-20 | TAKES EFFECT 31/3/2003 | EMERGENCY OVERFLOW | 120 | Standby Pumps | 2
15271 | Poole King John Avenue SPS | SPS | 401279 | Granted | Numerical | 2002-08-01 | TAKES EFFECT WHEN GRANTED | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | SPS | 400793 | Granted | Numerical | 2000-02-14 |  | EMERGENCY OVERFLOW | 345 | Standby Pumps | 5
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | SPS | 400850 | Granted | Numerical | 2000-02-14 |  | STORM OVERFLOW | 345 | Standby Pumps | 5
15275 | Poole Hewitt Road SPS | SPS | 402038 | Granted | Numerical | 2006-07-03 |  | STORM/EMERGENCY | 15.8 | Standby Pumps | 2
15277 | Poole Wood Lane SPS | SPS | 401257 | Granted | Numerical | 2002-08-29 | Takes effect when granted; actually a modification of 50909 | STORM/EMERGENCY | 14.5 | Standby Pumps | 2
15278 | Long Sutton Bennetts Orchard SPS | SPS | 102399 | Granted | Numerical | 2003-12-10 | Takes effect 01/04/2004 | STORM/EMERGENCY | 7.8 | Standby Pumps | 2
15282 | Bradford Abbas Mill Lane SPS | SPS | 101782 | Granted | Numerical | 2002-05-09 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 14.3 | Standby Pumps | 2
15283 | Wincanton Bayford SPS | SPS | 402455 | Granted | Numerical | 2007-10-11 | Actually modifies/replaces 051085. Geny connection/link box required by 31/03/2008. | STORM/EMERGENCY | 5 | Standby Pumps | 2
15284 | Huish Episcopi Wagg Drove SPS | SPS | 71164 | Granted | Numerical | 1989-10-31 | Deemed determined Apr09: WAGG DROVE ST4350026800 WAGG RHYNE. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 3 | Standby Pumps | 2
15290 | Henstridge Marsh Lane (Henstridge No 2) SPS | SPS | 50882 | Granted | Numerical | 1989-08-30 |  | STORM OVERFLOW | 23 | No | 3
15297 | Drayton Ducks Lane SPS | SPS | 102400 | Granted | Numerical | 2004-01-07 | Takes effect 01/04/2004 | STORM/EMERGENCY | 45 | Standby Pumps | 2
15298 | Limington Main SPS | SPS | 102569 | Granted | Numerical | 2004-04-30 | Takes effect when granted | STORM/EMERGENCY | 4 | Standby Pumps | 2
15299 | Kingsdon . SPS | SPS | 101845 | Granted | Numerical | 2002-05-09 | TAKES EFFECT WHEN GRANTED. Modified / replaced Dec08. Geny connection / link box reqd by 31/03/2010. | STORM/EMERGENCY | 4.4 | Standby Pumps | 2
15304 | West Chinnock Garage SPS | SPS | 103720 | Granted | Numerical | 2007-09-21 | Takes effect 01/01/2008 | STORM/EMERGENCY | 8.8 | Standby Pumps | 4
15306 | Lower Somerton . SPS | SPS | 102063 | Granted | Numerical | 2003-08-14 | Takes effect when granted | EMERGENCY OVERFLOW | 19.8 | Standby Pumps | 2
15309 | Charlton Mackerell Rookery Farm SPS | SPS | 102064 | Granted | Numerical | 2003-08-14 | Takes effect when granted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15310 | Aller . SPS | SPS | 71143 | Granted | Numerical | 1989-10-31 | Storm/EO discharge via CSO at 16692 | STORM/EMERGENCY | #N/A | Standby Pumps | 3
15311 | Yeovil Mudford SPS | SPS | NPSWQD003764 | Granted | Numerical | 2008-09-10 | Geny connection / link box reqd by 30/09/2009: NPSWQD003764 | STORM/EMERGENCY | 9.3 | Standby Pumps | 2
15313 | Huish Episcopi Pibsbury SPS | SPS | 71157 | Granted | Descriptive | 1989-10-31 | Deemed determined Apr09: PIBSBURY FAR ST4386026340 RIVER YEO. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 1.4 | Standby Pumps | 2
15314 | Upton Nr Langport SPS | SPS | 102405 | Granted | Numerical | 2004-01-12 | Takes effect 01/04/2004 | STORM/EMERGENCY | 5 | Standby Pumps | 2
15315 | Huish Episcopi Wagg Bridge SPS | SPS | 71163 | Granted | Descriptive | 1989-10-31 | Deemed determined Apr09: WAGG BRIDGE ST4400027500 WAGG RHYNE. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 0.25 | Standby Pumps | 2
15316 | Barton St David Tootal Bridge SPS | SPS | 103177 | Granted | Numerical | 2007-03-16 |  | STORM/EMERGENCY | 2.4 | Standby Pumps | 2
15317 | Norton Sub Hamdon . SPS | SPS | 103178 | Granted | Numerical | 2007-03-16 |  | STORM/EMERGENCY | 15.4 | Standby Pumps | 2
15318 | Stoford Hillside Main SPS | SPS | 070149 | Granted | Numerical | 2022-05-13 | DOE REFERENCE COPA/1229 SEE 71704, 71159 | STORM OVERFLOW | 12 | No | 2
15319 | Chard Edwards SPS | SPS | 202687 | Granted | Numerical | 2003-02-24 | TAKES EFFECT 01/04/2003 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15320 | Long Sutton Knole SPS | SPS | 103179 | Granted | Numerical | 2007-03-16 |  | STORM/EMERGENCY | 2.8 | Standby Pumps | 2
15322 | Pitney . SPS | SPS | 103180 | Granted | Numerical | 2007-03-16 |  | STORM/EMERGENCY | 5.3 | Standby Pumps | 2
15325 | Keinton Mandeville . SPS | SPS | 103181 | Granted | Numerical | 2007-03-16 | "Geny connection" required by 31/10/2007 | STORM/EMERGENCY | 19.8 | Standby Pumps | 2
15327 | Ilminster Lord Nelson SPS | SPS | 102397 | Granted | Numerical | 2004-03-10 | Takes effect 01/04/2004 | STORM/EMERGENCY | 20 | Standby Pumps | 3
15330 | Chard Touches Meadow SPS | SPS | 102062 | Granted | Numerical | 2003-02-26 | TAKES EFFECT 01/04/2003 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15331 | Shepton Beauchamp . SPS | SPS | 102005 | Granted | Numerical | 2002-11-28 | TAKES EFFECT 31/3/03 | STORM/EMERGENCY | 12 | Standby Pumps | 2
15333 | Penselwood Penn Mill SPS | SPS | 402000 | Granted | Numerical | 2007-03-16 | "Geny connection" required by 31/10/2007 | STORM/EMERGENCY | 14 | Standby Pumps | 2
15334 | Charlton Adam . SPS | SPS | 101604 | Granted | Numerical | 2001-10-16 | Takes effect when granted | STORM/EMERGENCY | 21 | Standby Pumps | 3
15339 | Templecombe Slades Hill SPS | SPS | 401653 | Granted | Numerical | 2003-12-12 | Takes effect 01/04/2004 | STORM/EMERGENCY | 5.7 | Standby Pumps | 2
15370 | Westonzoyland Lakewall Road SPS | SPS | 101688 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | STORM OVERFLOW | 9 | No | 2
15371 | Cross Cross East SPS | SPS | 101667 | Granted | Numerical | 2002-01-25 | TAKES EFFECT 31/3/2002. See NoM, Sep08. Geny connection / link box reqd by 30/09/2009. | STORM/EMERGENCY | 5.5 | Standby Pumps | 2
15373 | Chedzoy Manor Drive SPS | SPS | 101684 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15378 | Pawlett Vicarage Lane SPS | SPS | 101710 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/02/2002 | STORM/EMERGENCY | 3 | Standby Pumps | 1
15381 | Wembdon Common SPS | SPS | 102688 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 52 | Standby Pumps | 2
15383 | Poole East Quay Perry Gardens SPS | SPS | NPSWQD007062 | Granted | Numerical | 2009-04-21 | Takes effect when granted, NPSWQD007062 | STORM/EMERGENCY | 202 | Standby Pumps | 5
15388 | Othery Rye Lane/ Summerhedge Road SPS | SPS | 101715 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/2002 | STORM/EMERGENCY | 13.5 | Standby Pumps | 2
15389 | Pawlett Main Road SPS | SPS | 102689 | Granted | Numerical | 2005-01-31 | TAKES EFFECT 31/03/2005 | STORM/EMERGENCY | 19.2 | Standby Pumps | 4 | 2
15391 | Westonzoyland Hamrod Lane SPS | SPS | 101712 | Granted | Numerical | 2002-08-12 | Spills via Site 16665. | STORM/EMERGENCY | 5 | Standby Pumps | 2
15393 | Bridgwater Taunton Road SPS | SPS | 102692 | Granted | Numerical | 2005-01-31 | TAKES EFFECT 31/03/2005. Telemetry alarm from 14378 must inhibit this site. | STORM/EMERGENCY | 70 | Standby Pumps | 11
15394 | Sutton Mallet . SPS | SPS | 101687 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02. See NoM, Sep08. Geny connection / link box reqd by 30/09/2009. | STORM/EMERGENCY | 5 | Standby Pumps | 2
15395 | Bason Bridge Church Road SPS | SPS | 101707 | Granted | Numerical | 2002-02-15 | TAKES EFFECT WHEN GRANTED | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15396 | Woolavington Meadow Farm SPS | SPS | 101713 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | STORM/EMERGENCY | 33 | Standby Pumps | 2 |  | Only 2 pumps - 1 is a screen pump
15397 | Stawell Ford Lane SPS | SPS | 101711 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | STORM/EMERGENCY | 3 | Standby Pumps | 2
15400 | Bridgwater West Quay Drawbridge SPS | SPS | 102693 | Granted | Numerical | 2005-01-31 | Takes effect 31/03/2005 | STORM/EMERGENCY | 206 | Standby Pumps | 13
15402 | Middlezoy Nethermoor Road SPS | SPS | 101686 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | STORM/EMERGENCY | 11 | Standby Pumps | 2
15410 | Horsey Chedzoy Lane Bridgwater SPS | SPS | 101709 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 1
15413 | Durleigh Enmore Road Reservoir SPS | SPS | 81931 | Granted | Numerical | 1984-10-29 | 081931 is Durleigh WTC permit, outlet E covers the SPS EO. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15414 | Bristol Central Trading Estate Bath Road SPS | SPS | 21635 | Granted | Numerical | 1984-03-22 |  | STORM/EMERGENCY | #N/A | No | 2
15415 | Bridgwater Colley Lane SPS | SPS | 71342 | Granted | Numerical | 1991-08-19 |  | STORM/EMERGENCY | 123 | Standby Pumps | 10
15435 | Bathpool Hyde Lane SPS | SPS | 103186 | Granted | Numerical | 2007-03-16 | "Geny connection" required by 01/05/2007 | STORM/EMERGENCY | 51 | Standby Pumps | 4
15436 | Ruishton Barton Lane SPS | SPS | NPSWQD001438 | Granted | Numerical | 2008-03-04 | Geny connection/link box required by 31/03/2009, NPSWQD001438 | STORM/EMERGENCY | 16 | Standby Pumps | 2
15439 | Henlade . SPS | SPS | NPSWQD001440 | Granted | Numerical | 2008-01-15 |  | STORM/EMERGENCY | 4.8 | Standby Pumps | 1
15440 | North Curry Main SPS | SPS | 101806 | Granted | Numerical | 2002-05-27 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 8.3 | Standby Pumps | 3
15443 | Taunton New Barn Queensway SPS | SPS | 103194 | Granted | Numerical | 2007-03-16 | Spills via Site 16734. | STORM OVERFLOW | 21 | No | 2
15446 | Hillcommon Hill Common SPS | SPS | NPSWQD003671 | Granted | Numerical | 2008-09-11 | Geny connection / link box reqd by 30/09/2009: NPSWQD003671 | STORM/EMERGENCY | 8.6 | Standby Pumps | 2
15447 | Taunton Mountway Bishops Hull SPS | SPS | 103408 | Granted | Numerical | 2007-03-16 | NB. Screw pumping station to lift spills into discharge pipe. Pass forward flow is by gravity sewer only. | STORM OVERFLOW | 120 | No | 2
15448 | Taunton Longacre Close SPS | SPS | 103187 | Granted | Numerical | 2007-03-16 | Geny connection required by 01/05/2007 - changeover panel fitted 12/06/2007 | STORM/EMERGENCY | 7 | Standby Pumps | 2
15449 | Meare Green Wrantage SPS | SPS | 70796 | Granted | Numerical | 1989-10-31 | Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 1 | Standby Pumps | 2
15450 | Norton Fitzwarren Langford Lane SPS | SPS | 101807 | Granted | Numerical | 2002-05-28 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 1.7 | Standby Pumps | 2
15454 | Creech St Michael North End SPS | SPS | 102019 | Granted | Numerical | 2002-10-16 | Replaces 100523 by modification from 31/3/03 | STORM/EMERGENCY | 26 | Standby Pumps | 2
15457 | Wellington Westford SPS | SPS | 100532 | Granted | Numerical | 1998-05-22 |  | STORM/EMERGENCY | 13.8 | Standby Pumps | 2
15458 | Stoke St Gregory Curload SPS | SPS | 102570 | Granted | Numerical | 2004-07-14 |  | STORM/EMERGENCY | 2.2 | Standby Pumps | 3
15459 | Rumwell . SPS | SPS | 82085 | Granted | Numerical | 1983-02-17 |  | STORM/EMERGENCY | 6.93 | No | 2
15460 | Meare Green Stoke St Gregory SPS | SPS | 70896 | Granted | Numerical | 1989-09-12 | Deemed determined Apr09: MEARE ELM ST3341026330 DITCH - SEDGEMOOR OLD RHYNE. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 0.4 | Standby Pumps | 2
15461 | Stoke St Gregory Woodhill SPS | SPS | 103188 | Granted | Numerical | 2007-03-16 | "Geny connection" to be installed by 01/05/2007 | STORM/EMERGENCY | 16 | Standby Pumps | 2
15463 | Bradford On Tone Tone Green SPS | SPS | 103189 | Granted | Numerical | 2007-03-16 | "Geny connection" to be installed by 01/05/2007 | STORM/EMERGENCY | 0.5 | Standby Pumps | 2
15465 | North Curry Stoke Road SPS | SPS | 103190 | Granted | Numerical | 2007-03-16 | "Geny connection" required by 01/05/2007 | STORM/EMERGENCY | 9 | No | 2
15467 | Nailsbourne . SPS | SPS | 103191 | Granted | Numerical | 2007-03-16 | Geny "connection" to be installed by 01/05/2007 | STORM/EMERGENCY | 16 | Standby Pumps | 3
15468 | Bradford On Tone Hockholler A38 SPS | SPS | 70798 | Granted | Numerical | 1989-10-31 | PSKPM: Overflow has two outlets to the same head wall, a gravity output and a pumped output which is used when the level in the receiving watercourse is above the gravity outlet. | STORM/EMERGENCY | 6 | Standby Pumps | 3
15469 | Leigh Frampton Farm SPS | SPS | 102977 | Granted | Numerical | 2005-06-02 | Takes effect when granted | STORM/EMERGENCY | 14 | Standby Pumps | 4
15481 | Bradpole Lee Lane SPS | SPS | 402029 | Granted | Numerical | 2007-03-16 |  | STORM/EMERGENCY | 33 | Standby Pumps | 2
15486 | West Bexington . SPS | SPS | 41125 | Granted | Numerical | 1989-10-31 | Deemed determined Apr09: WEST BEXINGT SY5300086700 SEA LAGOON CHESSEL BEACH. Deemed determined Sep10 with generic text conditions. | STORM/EMERGENCY | 1.5 | Standby Pumps | 2
15494 | Abbotsbury Church Street SPS | SPS | 401866 | Granted | Numerical | 2005-06-02 | Takes effect when granted | STORM/EMERGENCY | 9.3 | Standby Pumps | 2
15495 | Netherbury Beaminster SPS | SPS | 402106 | Granted | Numerical | 2006-10-03 |  | STORM/EMERGENCY | 3.8 | Standby Pumps | 2
15496 | Leigh Bridge Farm SPS | SPS | 102978 | Granted | Numerical | 2005-06-02 | Takes effect when granted | STORM/EMERGENCY | 11.8 | Standby Pumps | 2
15497 | Martinstown B3159 SPS | SPS | 401520 | Granted | Numerical | 2003-12-04 | Takes effect 31/03/2004 | STORM OVERFLOW | 10 | No | 7
15500 | Bradpole Fishweir Foul SPS | SPS | 402030 | Granted | Numerical | 2007-03-16 | Also called Fishweir Fields SPS, Bridport | STORM/EMERGENCY | 7 | Standby Pumps | 2
15504 | Dorchester Mellstock Avenue SPS | SPS | 400692 | Granted | Numerical | 2000-12-21 | PSKPM | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15505 | Symondsbury West Road Foundry SPS | SPS | 402031 | Granted | Numerical | 2007-03-16 |  | STORM/EMERGENCY | 6 | No | 2
15507 | Bridport West Bay Sluices SPS | SPS | 402047 | Granted | Numerical | 2006-07-14 | Takes effect when granted | STORM/EMERGENCY | 9.3 | Standby Pumps | 3
15508 | Wootton Courtenay . SPS | SPS | 102300 | Granted | Numerical | 2004-06-28 | Takes effect when granted. Requirement for telemetry by 31 August 2004. | STORM/EMERGENCY | 0.7 | Standby Pumps | 2
15511 | Monksilver B3188 SPS | SPS | 102301 | Granted | Numerical | 2004-06-26 | Takes effect when granted. Requirement for telemetry by 31 August 2004. | STORM/EMERGENCY | 2.5 | Standby Pumps | 3
15516 | Bilbrook . SPS | SPS | 101656 | Granted | Numerical | 2002-01-18 | Takes effect 31/3/2002 | STORM/EMERGENCY | 4 | Standby Pumps | 2
15519 | Watchet Market Street (Tunnel) SPS | SPS | 101270 | Granted | Numerical | 2000-07-17 | Takes effect 31/12/2000 | STORM/EMERGENCY | 120 | Standby Pumps | 3
15521 | Radstock Victoria Square SPS | SPS | 13131 | Granted | Numerical | 1996-09-30 | Takes effect when granted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15522 | Clutton Kings Oak Meadow SPS | SPS | 10313 | Granted | Numerical | 1990-06-22 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
15523 | Camerton Sunnyvale SPS | SPS | 21687 | Granted | Numerical | 1979-06-07 |  | STORM/EMERGENCY | 3.8 | No | 2
15527 | Dunkerton Brooklands SPS | SPS | 21688 | Granted | Numerical | 1979-06-07 |  | STORM/EMERGENCY | 3.8 | No | 2
15531 | Radstock Curtsons SPS | SPS | 13127 | Granted | Numerical | 1996-09-30 | Takes effect when granted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 1
15533 | Monkton Combe Mill Lane SPS | SPS | 100502 | Granted | Numerical | 1998-06-09 | AMP 4 FTS and SID variation takes effect 31/03/2011 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15535 | Peasedown St John New Buildings / Whitebrook Lane SPS | SPS | 103600 | Granted | Numerical | 2007-05-04 | Telemetry required by 30/09/2008 and "Geny connection" by 31/03/2008 | STORM/EMERGENCY | 3.9 | Standby Pumps | 2
15536 | Wellow Mill Hill SPS | SPS | 103601 | Granted | Numerical | 2007-05-04 | Telemetry required by 30/09/2008 and "Geny connection" by 31/03/2008 | STORM/EMERGENCY | 5 | Standby Pumps | 2
15537 | Shoscombe Single Hill SPS | SPS | 21446 | Granted | Numerical | 1973-12-01 | See NoM, Mar08 | STORM/EMERGENCY | 2 | Standby Pumps | 2
15538 | Keynsham Abbey Park SPS | SPS | 13094 | Granted | Numerical | 1996-09-30 | . | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15541 | Keynsham The Hams SPS | SPS | 13093 | Granted | Numerical | 1996-09-30 |  | STORM/EMERGENCY | 23 | Standby Pumps | 4
15542 | Keynsham Keynsham High Level SPS | SPS | 102126 | Granted | Numerical | 2003-07-31 | Takes effect 31/12/2003 | STORM/EMERGENCY | 112 | No | 3
15544 | Temple Cloud Temple Bridge SPS | SPS | 21357 | Granted | Numerical | 1971-12-24 |  | STORM OVERFLOW | 32 | No | 4
15547 | Saltford The Shallows SPS | SPS | 102123 | Granted | Numerical | 2003-07-31 | Takes effect 31/12/2003 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15548 | Keynsham Keynsham Low Level SPS | SPS | 102124 | Granted | Numerical | 2003-07-31 | Takes effect 31/12/2003 | STORM/EMERGENCY | 10 | Standby Pumps | 2
15551 | Weymouth Preston Fisherbridge Estate SPS | SPS | 401218 | Granted | Numerical | 2002-05-02 | TAKES EFFECT 31/03/2003 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 6
15552 | Weymouth Knightsdale Newstead Road SPS | SPS | 400892 | Granted | Numerical | 2000-10-20 | TAKES EFFECT SOONEST OF 31/3/2001 OR SCHEME COMPLETION. Spills via Site 16856. | STORM/EMERGENCY | 87 | Standby Pumps | 3
15553 | Portland Victoria Square SPS | SPS | 40206 | Granted | Numerical | 1986-05-01 | SPS at 15553 permitted for storm overflow under 40206. CSO at 16867 linked to SPS 15553 permitted for Storm/Emergency under permit 40634. | STORM OVERFLOW | 480 | No | 12
15554 | Weymouth Lodmoor Weymouth Bay Avenue SPS | SPS | 401217 | Granted | Numerical | 2002-05-02 | TAKES EFFECT 31/03/2003 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 4
15555 | Wyke Regis Hillcrest Road SPS | SPS | 402476 | Granted | Numerical | 2007-10-17 | Annual report (April to March) required to LFA and EA re operation of CSO, see consent for details. LFA and EA to be notified immediately on operation of the EO. NoM, Bathing and Shellfish waters monitoring and reporting required from 01/04/2010. | STORM/EMERGENCY | 150 | Standby Pumps | 4
15556 | Weymouth Radipole SPS | SPS | 401048 | Granted | Numerical | 2002-03-04 | TAKES EFFECT 01/08/2002 | STORM/EMERGENCY | 2200 | Standby Pumps | 11
15557 | Weymouth Overcombe SPS | SPS | 401194 | Granted | Numerical | 2002-03-19 | TAKES EFFECT 31/3/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15559 | Portland Pennsylvania Road SPS | SPS | 402253 | Granted | Numerical | 2007-04-05 | - | STORM/EMERGENCY | 5 | Standby Pumps | 2
15561 | Weymouth Ferrybridge Portland Road SPS | SPS | 402477 | Granted | Numerical | 2007-10-17 | From consent start date: Annual report (Apr to Mar) required to LFA and EA re operation of CSO, see consent for details; and LFA and EA to be notified immediately on operation of the EO. | STORM/EMERGENCY | 20 | Standby Pumps | 3
15569 | Portbury Drove SPS | SPS | 70828 | Granted | Numerical | 1989-10-31 | Deemed determined Apr09: PORTBURY DRO ST4995076050 M/H-DROVE RHYNE. Deemed determined Sep10 with generic text conditions. PSKPM: Overflow is located at manhole ST49769001 upstream of Portbury Drove SPS ID15569 | STORM/EMERGENCY | 92.3 | Standby Pumps | 2
15572 | Locking Locking Village SPS | SPS | 100524 | Granted | Numerical | 1998-05-22 |  | STORM/EMERGENCY | 46 | Standby Pumps | 2
15573 | Bleadon Purn SPS | SPS | 101663 | Granted | Numerical | 2001-12-20 | TAKES EFFECT 31/3/2002 | STORM/EMERGENCY | 17 | Standby Pumps | 2
15574 | Sandford Batch . SPS | SPS | 103602 | Granted | Numerical | 2007-05-04 | Telemetry required by 30/09/2008 and "Geny connection" by 31/03/2008 | STORM/EMERGENCY | 9.8 | Standby Pumps | 2
15577 | Sandford Sandmead Lane SPS | SPS | 103173 | Granted | Numerical | 2006-02-12 | Takes effect 01/04/2007 | STORM/EMERGENCY | 54 | Standby Pumps | 2
15580 | Langford Blackmoor Road SPS | SPS | 12883 | Granted | Numerical | 1997-01-10 |  | STORM/EMERGENCY | 40 | Standby Pumps | 2
15582 | Banwell Riverside SPS | SPS | 101664 | Granted | Numerical | 2002-01-25 | TAKES EFFECT 31/3/2002 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15592 | Portishead North Weston SPS | SPS | 100561 | Granted | Numerical | 1998-06-08 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15606 | Clevedon The Beach SPS | SPS | 100767 | Granted | Numerical | 1999-11-25 |  | STORM/EMERGENCY | 71 | Standby Pumps | 3
15606 | Clevedon The Beach SPS | SPS | 100767 | Granted | Numerical | 1999-11-25 |  | STORM/EMERGENCY | 71 | Standby Pumps | 3
15609 | Clapton In Gordano . SPS | SPS | 71397 | Granted | Numerical | 1991-02-08 | PUMPING STATION REPLACES STW | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15621 | Clevedon Ladye Bay SPS | SPS | 102489 | Granted | Numerical | 2004-06-25 | Spills via Site 16825. | STORM/EMERGENCY | 35.5 | Standby Pumps | 2
15622 | Clevedon Marine Parade SPS | SPS | 71176 | Granted | Numerical | 1990-11-07 |  | STORM/EMERGENCY | 42 | Standby Pumps | 2
15627 | Ilton Frost Lane SPS | SPS | 70693 | Granted | Numerical | 1989-08-25 | OLD SITE ID : 16714 - BETTER INFO JACQUI RODGERS. Was EO Only, replaced/modified Dec08. Geny connection / link box reqd by 31/03/2010. | STORM/EMERGENCY | 5.6 | Standby Pumps | 3
15629 | Hambridge . SPS | SPS | 71776 | Granted | Numerical | 1992-03-03 | TAKES EFFECT WHEN GRANTED. RTC in place to inhibit pumps when level at D/S SPS 15654 goes high. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 4
15630 | Chickerell Lower Way SPS | SPS | EPR/CB3990NR | Granted | Numerical | 2013-08-28 | Takes effect when granted. EPR/CB3990NR. PS EO management plan required. Spill monitoring required by 01/04/2015.Spills via 17342 | STORM/EMERGENCY | 15.5 | No | 2
15635 | Poole Cowslip Road Pine Springs SPS | SPS | 400150 | Granted | Numerical | 1997-05-30 | Formally transferred to WSX from developer | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15638 | Manningford No 4 Ps Pewsey SPS | SPS | 41874 | Granted | Numerical | 1991-09-24 | OLD SITE ID : 16461 - BETTER INFO JACQUI RODGERS | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15639 | Compton Dundon Moor Close SPS | SPS | 70674 | Granted | Numerical | 1989-08-30 | DOE REF: COPA NO. 20246 | EMERGENCY OVERFLOW | #N/A | No | 2
15641 | Salway Ash Old Stw SPS | SPS | 41991 | Granted | Numerical | 1991-09-24 | REPLACED SALWAY ASH STW | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
15642 | Poole Sterte F W Private SPS | SPS | 41005 | Granted | Numerical | 1991-01-31 | PSKPM. Adopted from DCC - consent transferred to WSX by modn 21/10/2005 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
15644 | Sutton Waldron . SPS | SPS | 41782 | Granted | Numerical | 1990-12-21 | OLD SITE ID 16554. Geny connection / link box reqd by 30/09/2009. | STORM/EMERGENCY | 6 | Standby Pumps | 2
15645 | Pill Avon Road SPS | SPS | 11673 | Granted | Numerical | 1991-09-24 | Spills via Site 16829. | STORM/EMERGENCY | 80 | Standby Pumps | 2
15646 | Pitcombe Vale Road SPS | SPS | 71498 | Granted | Numerical | 1991-03-25 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15648 | Portland Portland Bill SPS | SPS | 402219 | Granted | Numerical | 2007-04-05 | Modifies/replaces 40633. EO operating alarm to be fitted by 30/09/2007. Geny connection to be fitted by 31/03/2008. Immediate notification of EO operation also reqd to Local Food Authority / EHO from 30/04/2011. | STORM/EMERGENCY | 5.5 | Standby Pumps | 2
15649 | West Huntspill Rose Farm SPS | SPS | 101716 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15657 | West Huntspill White Cottage SPS | SPS | 101717 | Granted | Numerical | 2002-02-15 | TAKES EFFECT 31/3/02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15660 | Woodborough Ps1 . SPS | SPS | 41876 | Granted | Numerical | 1991-09-24 | [OLD SITE ID 16458] | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15673 | Portland Southwell SPS | SPS | 40686 | Granted | Numerical | 1991-11-08 | Immediate notification of EO operation also reqd to Local Food Authority / EHO from 30/04/2011 | STORM/EMERGENCY | 160 | Standby Pumps | 3
15674 | Eype Mount Lane SPS | SPS | 41948 | Granted | Numerical | 1991-09-18 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 4
15680 | Portishead Black Nore (Nautical School) SPS | SPS | 71587 | Granted | Numerical | 1991-08-19 |  | STORM/EMERGENCY | 26 | Standby Pumps | 2
15682 | Ashcott Bradley Lane (Taunton Road) SPS | SPS | 13534 | Granted | Numerical | 1996-07-10 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15683 | Burton Bradstock Annings Lane SPS | SPS | 8184 | Granted | Numerical | 2009-08-04 | Takes effect soonest of 31/03/2010 or commissioning. Telemetry rqd to inhibit Shipton Gorge SPS if Annings Lane fails. NPSWQD008184. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15689 | Hilcott Pumping Station No 3 SPS | SPS | 41875 | Granted | Numerical | 1991-09-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 1
15699 | Charmouth Newlands Bridge SPS | SPS | 42371 | Granted | Numerical | 1992-12-23 | OLD SITE ID : 16823 - BETTER INFO JACQUI RODGERS | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15702 | Rushall Pewsey Road SPS | SPS | 401641 | Granted | Numerical | 2004-03-25 | Takes effect 01/04/2004 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15703 | Babcary Orchard Cottage SPS | SPS | 71662 | Granted | Numerical | 1991-09-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15704 | Bottlesford . SPS | SPS | 41873 | Granted | Numerical | 1991-09-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15706 | Poole Delph Gardens SPS | SPS | 41356 | Granted | Numerical | 1990-04-30 | ADOPTED [CERT HOLDER RECEIVED 18/04/97]. Spills via Site 16617. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15714 | Poole Wentworth Drive SPS | SPS | 400745 | Granted | Numerical | 2000-02-14 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15715 | Bridgwater Horsey Bath Road SPS | SPS | 101841 | Granted | Numerical | 2002-09-18 | TAKES EFFECT WHEN GRANTED | STORM/EMERGENCY | 54 | Standby Pumps | 3
15720 | Norton Fitzwarren Stembridge Way SPS | SPS | 70281 | Granted | Numerical | 1995-10-30 | Takes effect when granted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15722 | Wellington Poole Brickyard SPS | SPS | 100533 | Granted | Numerical | 1998-05-22 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15723 | Tetbury Springfields SPS | SPS | 103899 | Granted | Numerical | 2007-11-26 |  | STORM/EMERGENCY | 4 | Standby Pumps | 2
15725 | Wiveliscombe Ford Road (Lion D'Angers) SPS | SPS | 71268 | Granted | Numerical | 1990-09-19 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15726 | Portishead Lake Grounds SPS | SPS | 101909 | Granted | Numerical | 2002-10-04 | Replaces 13462 by modification from 4/10/02 | STORM/EMERGENCY | 8 | Standby Pumps | 2
15728 | Taunton Killams Park SPS | SPS | 70171 | Granted | Numerical | 1987-03-01 | ADOPTED 13/12/1994 | EMERGENCY OVERFLOW | #N/A | No | 1
15734 | Wellington Lowmoor Trading Estate 1 SPS | SPS | 71615 | Granted | Numerical | 1995-01-18 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15772 | Peasedown St John Wellow Lane SPS | SPS | 103787 | Granted | Numerical | 2007-10-11 |  | STORM/EMERGENCY | 70 | Standby Pumps | 2
15775 | Broadstone Bryony Close SPS | SPS | 42769 | Granted | Numerical | 1994-11-30 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 1
15782 | Keynsham Dapps Hill SPS | SPS | 10216 | Granted | Numerical | 1990-01-01 | [CERT HOLDER RECEIVED 20/03/97] | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15791 | West Moors Gundrymor Industrial Estate SPS | SPS | 401146 | Granted | Numerical | 2002-02-18 | TAKES EFFECT 31/3/03 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15792 | Weston-Super-Mare Knightstone Road SPS | SPS | 72435 | Granted | Numerical | 1993-12-10 |  | STORM OVERFLOW | 443 | No | 3
15804 | Taunton Killams Lane SPS | SPS | 71224 | Granted | Numerical | 1990-09-19 | Adopted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15805 | Bridgwater Showground No1 SPS | SPS | 71219 | Granted | Numerical | 1991-04-08 | TAKES EFFECT WHEN GRANTED. Adopted by WW 04/12/1998. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15810 | Melksham Primrose Drive SPS | SPS | 12661 | Granted | Numerical | 1995-02-24 | From Persimmom Homes Ltd - WSX adoption ref A669C - also known as Lodge Farm SPS, Bowerhill (see consent) | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15887 | Bath Newton Road SPS | SPS | 13044 | Granted | Descriptive | 1995-12-04 | TAKES EFFECT SOONEST OF 1/9/1996 OR PSTN COMMISSIONING. Telemetry reqd by 01/09/1996. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15900 | Clutton Batch Farm SPS | SPS | 13077 | Granted | Numerical | 1996-11-14 | ADOPTED January 1998 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
15965 | Bristol St Georges Avenue Crews Hole Road SPS | SPS | 12819 | Granted | Numerical | 1995-09-26 | Adopted by WSX 01/02/2000 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
16050 | Bath Ea Depot SPS | SPS | 102275 | Granted | Numerical | 2004-07-28 | TAKES EFFECT 31/03/2005 | STORM OVERFLOW | 29.9 | No | 4
16057 | Bath Technology House SPS | SPS | 102276 | Granted | Numerical | 2004-07-28 | TAKES EFFECT 31/03/2005 | STORM OVERFLOW | 11 | No | 5
17027 | South Cadbury . SPS | SPS | 102161 | Granted | Numerical | 2003-12-02 | Takes effect 01/08/2004 | STORM/EMERGENCY | 6 | Standby Pumps | 2
17040 | Ringwood Windmill Lane SPS | SPS | 401220 | Granted | Numerical | 2002-02-27 | TAKES EFFECT 01/01/2003 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
17169 | Sturminster Newton Field Close SPS | SPS | 401101 | Granted | Numerical | 2001-09-28 | Takes effect 01/10/2001. Adopted by WSX from Bryant Homes (was previously held by Taywood Homes) 01/12/2006. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
17175 | Puriton Downend Terrace SPS | SPS | 102773 | Granted | Numerical | 2005-03-23 | Takes effect when granted | STORM/EMERGENCY | 5 | Standby Pumps | 2
17203 | Bristol Broad Quay SPS | SPS | 103054 | Granted | Numerical | 2005-07-27 | Takes effect 01/01/2006 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
17268 | Kingswood Station Road Storm Tank SPS | SPS | 103075 | Granted | Numerical | 2005-08-25 | Takes effect 01/04/2006 | STORM OVERFLOW | 30 | No | 2
17585 | Pymore Thread Mill Lane SPS | SPS | 400963 | Granted | Numerical | 2000-09-05 | Adopted/transferred to WSX 1st March 2012 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
17771 | Bowerhill Melksham Oak SPS | SPS | 100637 | Granted | Numerical | 1999-06-09 | Consent replaced/varied with effect 30/11/2009. Site 17771 replaced 14471 and came on line 03/06/2010. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
18710 | Bristol Royal Edward Dock St Andrews Road SPS | SPS | 12617 | Granted | Numerical | 1995-03-07 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
18716 | Buckhorn Weston Filley Brook Kington Magna Rd SPS | SPS | 400079 | Granted | Numerical | 1997-07-01 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
18718 | Chapmanslade Divers Bridge SPS | SPS | 10613 | Granted | Numerical | 1989-10-31 | - | STORM/EMERGENCY | 5.2 | Standby Pumps | 3
19035 | Kingsbury Episcopi . SPS | SPS | 13464 | Granted | Numerical | 1996-11-07 |  | STORM/EMERGENCY | 14 | Standby Pumps | 3
19047 | Wiveliscombe Nordens Meadows Taunton Road SPS | SPS | 13378 | Granted | Numerical | 1996-10-23 | ADOPTED Dec01 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19053 | Yeovil Alvington Triangle SPS | SPS | 12959 | Granted | Numerical | 1996-03-12 | Relaced/varied consent issued 21/10/2009 - may require new Site ID | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19056 | Weymouth Castle Cove Old Castle Road Wyke Regis SPS | SPS | EPR/AP3923KW | Granted | Numerical | 2010-08-05 | EPR/AP3923KW. Shellfish reporting for 1 Apr to 31 Mar; Bathing water reporting for 1 May to 30 Sep. | STORM/EMERGENCY | 30 | No | 3
19057 | Kington Magna Five Bridges SPS | SPS | 400080 | Granted | Numerical | 1997-07-01 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 4
19058 | Bristol Robertson Drive Bristol SPS | SPS | 103017 | Granted | Numerical | 2005-07-15 | Takes effect when granted | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19080 | Pensford Pensford Bridge SPS | SPS | 12381 | Granted | Numerical | 1994-03-01 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19082 | Wimborne Furzehill SPS | SPS | 400397 | Granted | Numerical | 1997-08-29 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19103 | Yeovil Marsh SPS | SPS | 72175 | Granted | Numerical | 1993-02-02 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19179 | North Petherton Baymead Lane SPS | SPS | 100239 | Granted | Numerical | 1997-05-09 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19272 | Alhampton Main SPS | SPS | 100651 | Granted | Numerical | 1998-09-16 | Start Date of 30/09/99 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19279 | Oake Saxon Close SPS | SPS | 100336 | Granted | Numerical | 1997-08-29 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19506 | Severn Beach Western Approach SPS | SPS | 100242 | Granted | Numerical | 1997-05-21 | Adopted by Wessex from ICI Estates 15/09/2010; Permit transferred formally 13/02/2014. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | #N/A
19542 | Avonmouth Cabot Park No.1 SPS | SPS | 100878 | Granted | Numerical | 1999-08-17 | "Lawrence Weston Rd PS No1". Takes effect soonest of 01/09/1999 or commissioning. Adopted by WSX 12/09/2007. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 3
19543 | Avonmouth Cabot Park No.2 SPS | SPS | 100906 | Granted | Numerical | 1999-08-17 | "Lawrence Weston Rd PS No2". Takes effect soonest of 01/09/1999 or commissioning. Adopted by WSX 12/09/2007. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19544 | Avonmouth Cabot Park No.3 SPS | SPS | 101155 | Granted | Numerical | 2000-04-14 | Takes effect when granted. Adopted by WSX 12/09/2007. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19663 | Blackford Blackford Moor Lane SPS | SPS | 101203 | Granted | Numerical | 2000-07-19 | TAKES EFFECT 31/12/2000 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19664 | Blackford Old Court Farm SPS | SPS | 101204 | Granted | Numerical | 2000-07-19 | Effective from 30/04/2001 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19699 | Bovington Lytchett Lane SPS | SPS | 401064 | Granted | Numerical | 2001-06-13 | Takes effect 1 Feb 2002 | STORM/EMERGENCY | 10 | Standby Pumps | 2
19712 | Litton . SPS | SPS | 101594 | Granted | Numerical | 2001-10-12 | Takes effect on 28/02/2002. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19725 | Kimmeridge . SPS | SPS | 401118 | Granted | Numerical | 2001-10-30 | Takes effect 30 Sep 02 | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19731 | Harmans Cross Transfer Station SPS | SPS | 401237 | Granted | Numerical | 2002-05-02 | TAKES EFFECT 31/3/03 | STORM/EMERGENCY | 7.5 | Standby Pumps | 2
19776 | Warmwell Bourne Leisure SPS | SPS | 401561 | Granted | Numerical | 2004-08-02 | Takes effect when granted - New SPS consent | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19787 | Stour Row . SPS | SPS | 401115 | Granted | Numerical | 2001-10-30 | Takes effect 28/02/2002 | STORM/EMERGENCY | 6 | Standby Pumps | 2
19817 | Sandford Orcas . SPS | SPS | 102522 | Granted | Numerical | 2004-08-18 | Takes effect 1 November 2005 | STORM/EMERGENCY | 6 | Standby Pumps | 2
19819 | Blagdon Hill Howleigh Lane SPS | SPS | 101891 | Granted | Numerical | 2002-10-16 | Takes effect soonest of 1/1/03 or AMP 3 scheme | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19820 | Pitminster Queens Arms SPS | SPS | 101892 | Granted | Numerical | 2002-10-16 | Takes effect soonest of 1/1/03 or AMP 3 scheme | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19821 | Pitminster Weir SPS | SPS | 101893 | Granted | Numerical | 2002-10-22 | Takes effect soonest of 1/1/03 or AMP 3 scheme | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19834 | Street Strawberry Hill SPS | SPS | 101472 | Granted | Numerical | 2001-06-04 | Transferred to WSX (adoption) 19 Dec05 - also known as Mendip View SPS | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19935 | Bradford-On-Avon Greenland Mills SPS | SPS | 100106 | Granted | Numerical | 1997-03-24 |  | EMERGENCY OVERFLOW | #N/A | Standby Pumps | 2
19948 | Warmley Poplar Farm Estate SPS | SPS | 100282 | Granted | Numerical | 1997-03-26 | Adopted from Britannia Construction Apr09. Consent transfer formally effective from 20/09/2010. | EMERGENCY OVERFLOW | #N/A | Standby Pumps | #N/A
19978 | Rooksbridge Bristol Road SPS | SPS | 101956 | Granted | Numerical | 2002-10-03 | TAKES EFFECT 1/4/04 | STORM/EMERGENCY | 8.5 | Standby Pumps | 2
15244 | Poole Elgin Road SPS | SPS | 51289 | Granted | Descriptive | 3206500% | Immediate notification of EO operation also reqd to Local Food Authority / EHO from 31/03/2013. Deemed determined Sep10 with generic text conditions. Spills via 16615. App made to EA 2016 but permit issue delayed due to Flow4 clauses. App details entered here and noted (plus most text conditions). See Permit PSKPM for storage detail. | EMERGENCY OVERFLOW | 650 | Standby Pumps | 4

## Estimated Flow requirements
Data taken from GIS records and is only a estimate, upsteam populations are dependent on correct catchment allocation. Pipe diameter, used in the velocity calcs, is the largest diameter in the GIS record for that sites rising main. If there is an error then the GIS record is incorrect. Currently the diameter does not differentiate between internal or external, so HDPE mains will have incorrect velocities calculated. RG
Site Id | Site | Pipe Diameter (Largest diameter from GIS record) | SPS Flow (SFA method, l/s) | Flow for 0.75m/s (l/s) | FFT Consent (l/s) | Flow Used in Calcs | RM Length* (m) | Pipe Diameter (m) | Velocity (m/s) | Catchment | Downstream Site | Population Served | V Head | R Number | Friction (m) | SPS Height | Discharge Height | Max Height | Max Height Chainage | RM Chainage | friction 2 | Driving Level at SPS | Running Pressure at SPS (m) | Static Head at SPS (m)
14027 | Bristol Saltmarsh Drive SPS | 1800 | 7077.4621 | 1908.5175 | - | 1908.5175 | 1413.1792 | 1.8 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Kingsweston Lane STW | 733793 | 0.028846 | 1035328.5183 | 0.36314 | 8.76 | 8.78 | 9.8 | 454 | 1414 | 0.36314 | 10.1631 | 1.4031 | 1.04
14016 | Bristol Ashton Avenue SPS | 2140 | 4520.986 | 2697.6071 | 2050 | 2050 | 34.548 | 2.14 | 0.5717 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 468737 | 0.016658 | 935394.0752 | 0.0042061 | 9.93 | 9.51 | 9.93 | 0 | 28 | 0.0042061 | 9.9342 | 0.0042061 | 0
14002 | Bath Midland Road Twerton SPS | 800 | 970.9702 | 376.9911 | 1050 | 1050 | 15224.8325 | 0.8 | 2.0953 | Saltford Mead Lane STW | Saltford Mead Lane STW | 100671 | 0.22377 | 1281603.9554 | 79.6632 | - | 20.5 | 28.15 | 3286 | 7278 | 79.6632 | 107.8132 | - | -
15588 | Worle North (Fw) SPS | 250 | 758.9105 | 36.8155 | - | 36.8155 | 1103.018 | 0.25 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 78684 | 0.028846 | 143795.6275 | 3.2924 | - | 5.85 | 6.3 | 50 | 564 | 3.2924 | 9.5924 | - | -
19130 | Bristol Dalby Ave SPS | 150 | 721.2948 | 13.2536 | - | 13.2536 | 4.5071 | 0.15 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 74784 | 0.028846 | 86277.3765 | 0.025928 | 8.78 | 8.84 | 8.84 | 4 | 4 | 0.025928 | 8.8659 | 0.085928 | 0.06
15244 | Poole Elgin Road SPS | 800 | 646.5959 | 376.9911 | - | 376.9911 | 2198.6722 | 0.8 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 67040 | 0.028846 | 460146.0081 | 1.5259 | 3.71 | 20.48 | 20.55 | 2186 | 2194 | 1.5259 | 22.0759 | 18.3659 | 16.84
15556 | Weymouth Radipole SPS | 1100 | 596.5728 | 712.7488 | 2200 | 2200 | 2527.0136 | 1.1 | 2.3221 | Weymouth . STW | Weymouth . STW | 61853 | 0.27482 | 1952920.313 | 10.9534 | - | 30.98 | 30.98 | 1756 | 1756 | 10.9534 | 41.9334 | - | -
14510 | Trowbridge Terminal At Bradford Road SPS | 533 | 516.0174 | 167.3422 | - | 167.3422 | 796.2534 | 0.533 | 0.7523 | Trowbridge Bradford Road STW | Trowbridge Bradford Road STW | 53501 | 0.028846 | 306572.2779 | 0.9151 | 43.8 | 44.06 | 44.06 | 796 | 796 | 0.9151 | 44.9751 | 1.1751 | 0.26
15019 | Bournemouth No 1 SPS | 525 | 425.9019 | 162.3565 | 750 | 750 | 386.0674 | 0.525 | 3.4752 | Holdenhurst Riverside Avenue STW | Holdenhurst Riverside Avenue STW | 44158 | 0.61555 | 1394943.0807 | 9.3043 | 7.43 | 24.4 | 24.4 | 386 | 386 | 9.3043 | 33.7043 | 26.2743 | 16.97
14013 | Clifton Low Level SPS | 300 | 422.3602 | 53.0144 | - | 53.0144 | 4.8425 | 0.3 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 43791 | 0.028846 | 172554.753 | 0.011465 | 13.25 | 12.21 | 13.25 | 0 | 4 | 0.011465 | 13.2615 | 0.011465 | 0
15233 | Poole Wilderton Road SPS | 600 | 374.7446 | 212.0575 | - | 212.0575 | 1869.6752 | 0.6 | 0.7523 | Poole Cabot Lane STW | Poole Elgin Road SPS | 38854 | 0.028846 | 345109.5061 | 1.8539 | 27.24 | 44.08 | 44.12 | - | 1870 | 1.8539 | 45.9739 | 18.7339 | 16.88
15013 | Southbourne Hengistbury Head SPS | 500 | 320.7169 | 147.2622 | 370 | 370 | 1417.0721 | 0.5 | 1.8902 | Holdenhurst Riverside Avenue STW | Holdenhurst Riverside Avenue STW | 33252 | 0.1821 | 722580.5158 | 10.8394 | 7.28 | 28.69 | 28.69 | - | 1418 | 10.8394 | 39.5294 | 32.2494 | 21.41
14384 | Bridgwater Chilton Street Saltlands SPS | 500 | 306.967 | 147.2622 | 242 | 242 | 681.2687 | 0.5 | 1.2363 | Chilton Trinity . STW | Chilton Trinity . STW | 31827 | 0.077898 | 472606.7157 | 2.2517 | 5.63 | 6.45 | 9.84 | 194 | 650 | 2.2517 | 12.0917 | 6.4617 | 4.21
15736 | Highbridge Highbridge South Alstone Road SPS | 100 | 299.166 | 5.8905 | - | 5.8905 | 7.1928 | 0.1 | 0.7523 | West Huntspill STW | West Huntspill STW | 31018 | 0.028846 | 57518.251 | 0.070222 | 6.94 | 6.58 | 6.94 | 0 | 8 | 0.070222 | 7.0102 | 0.070222 | 0
14374 | Highbridge Newton SPS | - | 295.9253 | - | 1950 | 1950 | 0 | - | - | West Huntspill STW | Highbridge Highbridge South Alstone Road SPS | 30682 | - | - | - | - | - | - | - | - | - | - | - | -
15078 | Ferndown A31 Tricketts Cross SPS | 600 | 287.0596 | 212.0575 | 218 | 218 | 3619.5059 | 0.6 | 0.77338 | Palmersford . STW | Palmersford . STW | 29763 | 0.030485 | 354780.5235 | 3.7888 | - | 12.18 | 20.3 | 524 | 1818 | 3.7888 | 24.0888 | - | -
13334 | Bridport West Bay SPS | 500 | 264.9763 | 147.2622 | 414 | 414 | 1121.251 | 0.5 | 2.1149 | Bridport Wych Farm STW | Bridport Wych Farm STW | 27473 | 0.22798 | 808509.0096 | 10.715 | - | 6.09 | 6.11 | 586 | 588 | 10.715 | 16.825 | - | -
14621 | Portishead Town Harbour Road SPS | 750 | 261.7124 | 331.3399 | 260 | 260 | 1603.0645 | 0.75 | 0.59032 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 27135 | 0.017761 | 338506.1876 | 0.74999 | 5.7 | 7.49 | 9.18 | 372 | 1604 | 0.74999 | 9.93 | 4.23 | 3.48
14492 | Kenn Kenn Pier SPS | - | 254.8606 | - | - | - | 0 | - | - | Kingston Seymour Back Lane STW | Kingston Seymour Back Lane STW | 26424 | - | - | - | - | - | - | - | - | - | - | - | -
14495 | Clevedon Clevedon Main SPS | 710 | 240.5319 | 296.9394 | 335 | 335 | 2262.371 | 0.71 | 0.84872 | Kingston Seymour Back Lane STW | Kingston Seymour Back Lane STW | 24939 | 0.036714 | 460724.1584 | 2.3058 | 8.23 | 6.1 | 8.36 | 2 | 2200 | 2.3058 | 10.6658 | 2.4358 | 0.13
15400 | Bridgwater West Quay Drawbridge SPS | 400 | 189.1431 | 94.2478 | 206 | 206 | 544.7958 | 0.4 | 1.6443 | Chilton Trinity . STW | Bridgwater West Quay Drawbridge SPS | 19611 | 0.13781 | 502876.9806 | 4.1832 | - | 7.49 | 8.93 | 226 | 504 | 4.1832 | 13.1132 | - | -
14122 | Spetisbury No 3 SPS | 350 | 172.2682 | 72.1585 | - | 72.1585 | 2310.1018 | 0.35 | 0.7523 | Tarrant Crawford . STW | Tarrant Crawford . STW | 17861 | 0.028846 | 201313.8786 | 4.5006 | 28.83 | 27.23 | 28.94 | 16 | 978 | 4.5006 | 33.4406 | 4.6106 | 0.11
14035 | Christchurch Somerford Bridge SPS | 350 | 171.4811 | 72.1585 | - | 72.1585 | 1908.8926 | 0.35 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 17780 | 0.028846 | 201313.8786 | 3.7189 | 7.28 | 3.2 | 8.84 | 622 | 1908 | 3.7189 | 12.5589 | 5.2789 | 1.56
15074 | West Moors The Forest SPS | 200 | 158.4487 | 23.5619 | - | 23.5619 | 27.0685 | 0.2 | 0.7523 | Palmersford . STW | Ferndown A31 Tricketts Cross SPS | 16428 | 0.028846 | 115036.502 | 0.10747 | 17.1 | 17.1 | 17.13 | 4 | 14 | 0.10747 | 17.2375 | 0.13747 | 0.03
15276 | Poole Recreation Road SPS | 600 | 156.8515 | 212.0575 | - | 212.0575 | 3063.7346 | 0.6 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 16263 | 0.028846 | 345109.5061 | 3.0379 | 33.16 | 57.96 | 59.49 | - | 3064 | 3.0379 | 62.5279 | 29.3679 | 26.33
15273 | Poole Turlin Main Blandford Road Turlin Moor SPS | 600 | 149.9997 | 212.0575 | 345 | 345 | 5657.7671 | 0.6 | 1.2239 | Poole Cabot Lane STW | Poole Cabot Lane STW | 15552 | 0.07635 | 561464.59 | 14.6058 | - | 7.16 | 10.67 | 1868 | 2894 | 14.6058 | 25.2758 | - | -
15417 | Burnham-On-Sea Ashcott Drive SPS | 1350 | 147.8006 | 1073.5411 | - | 1073.5411 | 6.0006 | 1.35 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 15324 | 0.028846 | 776496.3887 | 0.0021893 | 5.32 | 5.32 | 5.34 | - | 6 | 0.0021893 | 5.3422 | 0.022189 | 0.02
14082 | Street Main SPS | 450 | 142.7312 | 119.2823 | 190 | 190 | 1377.068 | 0.45 | 1.1983 | Glastonbury The Beckery SSTW | Glastonbury The Beckery SSTW | 14799 | 0.073187 | 412283.1772 | 4.8831 | 5.59 | 8.47 | 12.04 | 1152 | 1340 | 4.8831 | 16.9231 | 11.3331 | 6.45
15084 | Verwood Potterne Way SPS | 100 | 139.1664 | 5.8905 | 108 | 108 | 4.4048 | 0.1 | 13.7931 | Palmersford . STW | West Moors The Forest SPS | 14429 | 9.6967 | 1054576.969 | 13.7645 | 23.28 | 23.57 | 23.57 | 24 | 24 | 13.7645 | 37.3345 | 14.0545 | 0.29
15206 | Blandford Langton Road (Blandford No 1) SPS | 350 | 138.333 | 72.1585 | 89 | 89 | 1326.305 | 0.35 | 0.92788 | Tarrant Crawford . STW | Spetisbury No 3 SPS | 14343 | 0.043882 | 248299.8684 | 3.8994 | - | 39.89 | 39.98 | - | 1320 | 3.8994 | 43.8794 | - | -
14416 | Minehead Mart Road SPS | 600 | 135.9488 | 212.0575 | - | 212.0575 | 1598.0107 | 0.6 | 0.7523 | Minehead Headworks STW | Minehead Headworks STW | 14096 | 0.028846 | 345109.5061 | 1.5846 | 6.66 | 5.32 | 8.51 | 108 | 1598 | 1.5846 | 10.0946 | 3.4346 | 1.85
14498 | Uphill . SPS | 450 | 130.9025 | 119.2823 | - | 119.2823 | 1621.2192 | 0.45 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Weston-Super-Mare Accommodation Road Bleadon STW | 13572 | 0.028846 | 258832.1296 | 2.3026 | 6.79 | 5.44 | 15.17 | 560 | 1622 | 2.3026 | 17.4726 | 10.6826 | 8.38
14378 | Bridgwater Blake Gardens SPS | 560 | 130.3238 | 184.7256 | 90 | 90 | 183.2822 | 0.56 | 0.36653 | Chilton Trinity . STW | Bridgwater West Quay Drawbridge SPS | 13512 | 0.0068472 | 156931.0966 | 0.048851 | - | 7.82 | 8.22 | 148 | 174 | 0.048851 | 8.2689 | - | -
15553 | Portland Victoria Square SPS | 700 | 122.2914 | 288.6338 | 480 | 480 | 3741.9465 | 0.7 | 1.2511 | Weymouth . STW | Weymouth . STW | 12680 | 0.079775 | 669572.6787 | 8.33 | - | 20.32 | 21.74 | 3516 | 3608 | 8.33 | 30.07 | - | -
16920 | Bradford-On-Avon Barton Farm Terminal P Stn SPS | 315 | 115.3933 | 58.4483 | - | 58.4483 | 585.0775 | 0.315 | 0.7523 | Bradford-On-Avon . STW | Bradford-On-Avon . STW | 11964 | 0.028846 | 181182.4907 | 1.3022 | - | 41.65 | 46.08 | 92 | 150 | 1.3022 | 47.3822 | - | -
15037 | Christchurch Quomps No 2 SPS | 400 | 115.2312 | 94.2478 | - | 94.2478 | 1635.7342 | 0.4 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 11948 | 0.028846 | 230073.0041 | 2.6934 | - | 2.14 | 6.37 | 756 | 1634 | 2.6934 | 9.0634 | - | -
14095 | Glastonbury Porchestall SPS | 400 | 114.1201 | 94.2478 | 200 | 200 | 408.2768 | 0.4 | 1.5964 | Glastonbury The Beckery SSTW | Glastonbury The Beckery SSTW | 11832 | 0.1299 | 488230.0783 | 2.957 | - | 8.08 | 8.08 | 392 | 392 | 2.957 | 11.037 | - | -
15542 | Keynsham Keynsham High Level SPS | 320 | 111.8748 | 60.3186 | 112 | 112 | 209.1391 | 0.32 | 1.3969 | Keynsham . STW | Keynsham . STW | 11600 | 0.099452 | 341761.0548 | 1.5413 | 12.4 | 23.98 | 23.98 | 210 | 210 | 1.5413 | 25.5213 | 13.1213 | 11.58
15386 | Bridgwater Wylds Road Surface Water SPS | - | 111.3887 | - | - | - | 0 | - | - | Chilton Trinity . STW | Chilton Trinity . STW | 11549 | - | - | - | - | - | - | - | - | - | - | - | -
15243 | Bridgwater East Quay SPS | 560 | 111.1803 | 184.7256 | 179 | 179 | 1419.5099 | 0.56 | 0.72898 | Chilton Trinity . STW | Bridgwater Wylds Road Surface Water SPS | 11528 | 0.027085 | 312118.5143 | 1.4421 | - | 7.08 | 8.69 | 186 | 782 | 1.4421 | 10.1321 | - | -
15519 | Watchet Market Street (Tunnel) SPS | 300 | 109.2359 | 53.0144 | 120 | 120 | 949.8705 | 0.3 | 1.7029 | Watchet . STW | Watchet . STW | 11326 | 0.14779 | 390584.0626 | 11.2356 | 8.46 | 17.14 | 18.73 | 518 | 950 | 11.2356 | 29.9656 | 21.5056 | 10.27
14385 | Bridgwater Bristol Road SPS | 475 | 100.6248 | 132.9041 | 100 | 100 | 550.6757 | 0.475 | 0.56605 | Chilton Trinity . STW | Chilton Trinity . STW | 10433 | 0.016331 | 205570.5593 | 0.41919 | - | 6.2 | 8.5 | 100 | 370 | 0.41919 | 8.9192 | - | -
14323 | Amesbury Flower Lane SPS | 300 | 99.7452 | 53.0144 | 120 | 120 | 279.4057 | 0.3 | 1.7029 | 13008amesbury Off Church Street STW | 13008amesbury Off Church Street STW | 10342 | 0.14779 | 390584.0626 | 3.305 | 67.99 | 71.69 | 71.69 | 280 | 280 | 3.305 | 74.995 | 7.005 | 3.7
15235 | Poole Shore Road SPS | 355 | 99.0276 | 74.2349 | 60 | 60 | 2902.0426 | 0.355 | 0.60804 | Poole Cabot Lane STW | Poole Elgin Road SPS | 10268 | 0.018844 | 165035.5194 | 3.6628 | - | 2.9 | 18.11 | 1296 | 2866 | 3.6628 | 21.7728 | - | -
15383 | Poole East Quay Perry Gardens SPS | 760 | 98.5878 | 340.2345 | 202 | 202 | 8055.0184 | 0.76 | 0.44664 | Poole Cabot Lane STW | Poole Cabot Lane STW | 10222 | 0.010168 | 259532.8311 | 2.154 | - | 4.34 | 10.71 | 1668 | 3594 | 2.154 | 12.864 | - | -
15393 | Bridgwater Taunton Road SPS | 315 | 91.1109 | 58.4483 | 70 | 70 | 72.8346 | 0.315 | 0.90098 | Chilton Trinity . STW | Bridgwater Blake Gardens SPS | 9447 | 0.041374 | 216991.1459 | 0.23089 | - | 6.58 | 6.58 | 62 | 62 | 0.23089 | 6.8109 | - | -
14133 | Ringwood Bickerley SPS | 300 | 90.7406 | 53.0144 | - | 53.0144 | 1305.252 | 0.3 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Hampshire Hatches Lane STW | 9408 | 0.028846 | 172554.753 | 3.0903 | 13.53 | 12.77 | 15.46 | 1150 | 1302 | 3.0903 | 18.5503 | 5.0203 | 1.93
15080 | Ferndown Dugdell Close SPS | 350 | 87.4535 | 72.1585 | 173 | 173 | 1223.1537 | 0.35 | 1.8036 | Palmersford . STW | Palmersford . STW | 9068 | 0.1658 | 482650.3059 | 13.342 | 18.62 | 11.75 | 24.59 | 260 | 1224 | 13.342 | 37.932 | 19.312 | 5.97
14439 | Warminster Calveswater SPS | 355 | 87.4304 | 74.2349 | 95 | 95 | 755.5846 | 0.355 | 0.96273 | Warminster . STW | Warminster . STW | 9065 | 0.04724 | 261306.2391 | 2.346 | 108.25 | 113.29 | 113.29 | 756 | 756 | 2.346 | 115.636 | 7.386 | 5.04
14493 | Kingston Bridge SPS | 780 | 83.7035 | 358.3772 | - | 358.3772 | 50.1347 | 0.78 | 0.7523 | Kingston Seymour Back Lane STW | Kingston Seymour Back Lane STW | 8679 | 0.028846 | 448642.3579 | 0.035902 | 6.37 | 7.16 | 7.69 | 68 | 80 | 0.035902 | 7.7259 | 1.3559 | 1.32
15274 | Poole Woodlands Avenue SPS | 100 | 83.5646 | 5.8905 | - | 5.8905 | 6.8944 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Turlin Main Blandford Road Turlin Moor SPS | 8664 | 0.028846 | 57518.251 | 0.067308 | 3.29 | 3.45 | 3.46 | 4 | 6 | 0.067308 | 3.5273 | 0.23731 | 0.17
15247 | Poole Rectory / Ashmore Avenue SPS | 355 | 80.9721 | 74.2349 | - | 74.2349 | 1560.9136 | 0.355 | 0.7523 | Poole Cabot Lane STW | Poole Woodlands Avenue SPS | 8396 | 0.028846 | 204189.7911 | 2.9871 | 3.35 | 3.99 | 5.37 | 1180 | 1562 | 2.9871 | 8.3571 | 5.0071 | 2.02
14290 | Langport Westover SPS | 350 | 80.1619 | 72.1585 | - | 72.1585 | 902.7873 | 0.35 | 0.7523 | Langport Portfield Lane STW | Langport Portfield Lane STW | 8312 | 0.028846 | 201313.8786 | 1.7588 | - | 16.66 | 17.59 | 424 | 472 | 1.7588 | 19.3488 | - | -
14125 | Gillingham Buckingham Road SPS | 250 | 77.3378 | 36.8155 | 149 | 149 | 625.718 | 0.25 | 3.0447 | Gillingham Common Mead Lane STW | Gillingham Common Mead Lane STW | 8019 | 0.47249 | 581970.2533 | 29.5247 | 71.22 | 75.03 | 75.03 | 626 | 626 | 29.5247 | 104.5547 | 33.3347 | 3.81
15038 | Christchurch Avon Mill Lane SPS | 400 | 77.1989 | 94.2478 | - | 94.2478 | 1275.1073 | 0.4 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 8004 | 0.028846 | 230073.0041 | 2.0996 | 2.71 | 3.2 | 4.35 | - | 1272 | 2.0996 | 6.4496 | 3.7396 | 1.64
14363 | Durrington Nags Head SPS | 400 | 75.6943 | 94.2478 | - | 94.2478 | 1901.9717 | 0.4 | 0.7523 | Ratfyn . STW | Ratfyn . STW | 7848 | 0.028846 | 230073.0041 | 3.1318 | 72.52 | 75.41 | 78.9 | 254 | 710 | 3.1318 | 82.0318 | 9.5118 | 6.38
15415 | Bridgwater Colley Lane SPS | 600 | 74.5137 | 212.0575 | 123 | 123 | 581.4874 | 0.6 | 0.43636 | Chilton Trinity . STW | Bridgwater East Quay SPS | 7726 | 0.0097047 | 200174.3321 | 0.19933 | - | 7.3 | 7.52 | - | 548 | 0.19933 | 7.7193 | - | -
15554 | Weymouth Lodmoor Weymouth Bay Avenue SPS | 355 | 73.1017 | 74.2349 | - | 74.2349 | 784.0145 | 0.355 | 0.7523 | Weymouth . STW | Weymouth Radipole SPS | 7580 | 0.028846 | 204189.7911 | 1.5003 | - | 3.27 | 11.51 | - | 402 | 1.5003 | 13.0103 | - | -
14036 | Christchurch Scotts Hill Lane SPS | 450 | 72.9397 | 119.2823 | - | 119.2823 | 541.2788 | 0.45 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 7563 | 0.028846 | 258832.1296 | 0.76876 | 1.93 | 3.2 | 3.49 | - | 542 | 0.76876 | 4.2588 | 2.3288 | 1.56
15240 | Poole Branksome Chine SPS | 300 | 71.0415 | 53.0144 | 130 | 130 | 1830.1935 | 0.3 | 1.8448 | Poole Cabot Lane STW | Poole Wilderton Road SPS | 7366 | 0.17345 | 423132.7345 | 25.3639 | 7.59 | 26.7 | 28.35 | 932 | 1830 | 25.3639 | 53.7139 | 46.1239 | 20.76
15012 | Bournemouth Kinson Main Millhams Road SPS | 250 | 67.3147 | 36.8155 | - | 36.8155 | 1472.0004 | 0.25 | 0.7523 | Kinson New Road Northbourne STW | Kinson New Road Northbourne STW | 6980 | 0.028846 | 143795.6275 | 4.3937 | 13.81 | 9.76 | 14.33 | 352 | 1472 | 4.3937 | 18.7237 | 4.9137 | 0.52
14130 | Ringwood Hightown Crow Lane SPS | 300 | 66.8286 | 53.0144 | - | 53.0144 | 1519.3743 | 0.3 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Hampshire Hatches Lane STW | 6929 | 0.028846 | 172554.753 | 3.5972 | 19.55 | 12.15 | 19.85 | 42 | 1520 | 3.5972 | 23.4472 | 3.8972 | 0.3
15411 | Burnham-On-Sea Rectory Drive SPS | 750 | 66.736 | 331.3399 | - | 331.3399 | 25.6744 | 0.75 | 0.7523 | West Huntspill STW | Burnham-On-Sea Ashcott Drive SPS | 6920 | 0.028846 | 431386.8826 | 0.0193 | 6 | 5.73 | 6 | 0 | 26 | 0.0193 | 6.0193 | 0.0193 | 0
15007 | Bournemouth Iford Lane Tuckton SPS | 400 | 65.2082 | 94.2478 | 65 | 65 | 1379.782 | 0.4 | 0.51884 | Holdenhurst Riverside Avenue STW | Southbourne Hengistbury Head SPS | 6761 | 0.01372 | 158674.7754 | 1.0999 | - | 28.64 | 28.64 | 1244 | 1244 | 1.0999 | 29.7399 | - | -
14147 | Chippenham Westmead SPS | 300 | 63.9813 | 53.0144 | 155 | 155 | 509.0791 | 0.3 | 2.1995 | Chippenham Blackwell Hams STW | Chippenham Blackwell Hams STW | 6634 | 0.24658 | 504504.4142 | 9.996 | 43.77 | 46.9 | 46.94 | 504 | 510 | 9.996 | 56.936 | 13.166 | 3.17
15041 | Christchurch Lodge Road SPS | 300 | 63.9582 | 53.0144 | - | 53.0144 | 1128.3199 | 0.3 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Avon Mill Lane SPS | 6632 | 0.028846 | 172554.753 | 2.6714 | 4.3 | 7.59 | 8.18 | 580 | 1128 | 2.6714 | 10.8514 | 6.5514 | 3.88
14046 | Pewsey Swan SPS | 170 | 63.1712 | 17.0235 | 53 | 53 | 1401.512 | 0.17 | 2.3422 | Pewsey Salisbury Road STW | Pewsey Salisbury Road STW | 6550 | 0.2796 | 304425.8135 | 64.3776 | 107.09 | 106.88 | 110.08 | 658 | 1398 | 64.3776 | 174.4576 | 67.3676 | 2.99
15070 | Wimborne Hayes Lane Colehill SPS | 400 | 61.5276 | 94.2478 | 100 | 100 | 2601.3493 | 0.4 | 0.79821 | Wimborne Brook Road STW | Wimborne Brook Road STW | 6380 | 0.032474 | 244115.0391 | 4.8107 | - | 17.04 | 18.15 | 800 | 1310 | 4.8107 | 22.9607 | - | -
15068 | St Leonards Wayside Road No 1 SPS | 300 | 60.3934 | 53.0144 | 40 | 40 | 2002.9294 | 0.3 | 0.56762 | Palmersford . STW | Palmersford . STW | 6262 | 0.016421 | 130194.6875 | 2.7352 | 15.66 | 13.21 | 17.01 | 1280 | 2002 | 2.7352 | 19.7452 | 4.0852 | 1.35
14390 | Taunton Silk Mills SPS | 350 | 59.398 | 72.1585 | - | 72.1585 | 1263.6153 | 0.35 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 6159 | 0.028846 | 201313.8786 | 2.4618 | - | 19.15 | 21.31 | 30 | 1218 | 2.4618 | 23.7718 | - | -
15079 | Wimborne Poole Road SPS | 300 | 58.7036 | 53.0144 | 55 | 55 | 220.9521 | 0.3 | 0.78047 | Wimborne Brook Road STW | Wimborne Brook Road STW | 6087 | 0.031047 | 179017.6954 | 0.56219 | 17.46 | 18.52 | 18.52 | 220 | 220 | 0.56219 | 19.0822 | 1.6222 | 1.06
15053 | Ferndown Golf Links Road SPS | 250 | 58.0323 | 36.8155 | 80 | 80 | 1492.5855 | 0.25 | 1.6347 | Kinson New Road Northbourne STW | Kinson New Road Northbourne STW | 6017 | 0.13621 | 312467.2501 | 20.5283 | - | 27.02 | 27.02 | 898 | 898 | 20.5283 | 47.5483 | - | -
15109 | North Tidworth The Ram SPS | 160 | 56.6203 | 15.0796 | - | 15.0796 | 106.3574 | 0.16 | 0.7523 | - | - | 5871 | 0.028846 | 92029.2016 | 0.56283 | 110.05 | 117.94 | 117.94 | 106 | 106 | 0.56283 | 118.5028 | 8.4528 | 7.89
14551 | Bridgwater Bradney Bridge SPS | 475 | 56.0184 | 132.9041 | - | 132.9041 | 3926.547 | 0.475 | 0.7523 | Chilton Trinity . STW | Chilton Trinity . STW | 5808 | 0.028846 | 273211.6923 | 5.2115 | 6.27 | 6.2 | 8.35 | 3578 | 3922 | 5.2115 | 13.5615 | 7.2915 | 2.08
15582 | Banwell Riverside SPS | 375 | 55.4628 | 82.835 | - | 82.835 | 1750.9659 | 0.375 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Uphill . SPS | 5751 | 0.028846 | 215693.4413 | 3.1271 | 5.51 | 24.43 | 26.18 | 1696 | 1750 | 3.1271 | 29.3071 | 23.7971 | 20.67
15043 | Mudeford Mudeford Gardens SPS | 225 | 55.3934 | 29.8206 | 90 | 90 | 446.6753 | 0.225 | 2.2705 | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 5744 | 0.26274 | 390584.0626 | 13.466 | 2.46 | 6.68 | 6.87 | 370 | 446 | 13.466 | 20.336 | 17.876 | 4.41
15246 | Canford Magna Canford Main SPS | 200 | 55.3008 | 23.5619 | 80 | 80 | 436.9624 | 0.2 | 2.5543 | Wimborne Brook Road STW | Wimborne Brook Road STW | 5734 | 0.33254 | 390584.0626 | 19.3455 | 15.65 | 17.33 | 17.8 | 262 | 436 | 19.3455 | 37.1455 | 21.4955 | 2.15
14185 | Malmesbury St Johns Street SPS | 270 | 55.023 | 42.9416 | 60 | 60 | 990.8817 | 0.27 | 1.0511 | Malmesbury . STW | Malmesbury . STW | 5705 | 0.056315 | 216991.1459 | 5.1711 | 70.21 | 73.25 | 73.25 | 992 | 992 | 5.1711 | 78.4211 | 8.2111 | 3.04
15270 | Poole Creekmoor Lane SPS | 450 | 54.9073 | 119.2823 | 120 | 120 | 971.1777 | 0.45 | 0.75682 | Poole Cabot Lane STW | Poole Cabot Lane STW | 5693 | 0.029194 | 260389.3751 | 1.3956 | 2.32 | 5.82 | 8.06 | 710 | 930 | 1.3956 | 9.4556 | 7.1356 | 5.74
15071 | St Leonards Craigside Road SPS | 300 | 53.8888 | 53.0144 | 73 | 73 | 510.4652 | 0.3 | 1.0359 | Palmersford . STW | St Leonards Wayside Road No 1 SPS | 5588 | 0.054694 | 237605.3047 | 2.2646 | 17.03 | 24.68 | 24.96 | 502 | 510 | 2.2646 | 27.2246 | 10.1946 | 7.93
14265 | Upton Moorlands Way SPS | 315 | 53.5879 | 58.4483 | 45 | 45 | 1092.5019 | 0.315 | 0.5792 | Lytchett Minster Lytchett Bay STW | Lytchett Minster Lytchett Bay STW | 5556 | 0.017099 | 139494.3081 | 1.4588 | - | 2.56 | 3.24 | 212 | 982 | 1.4588 | 4.6988 | - | -
15435 | Bathpool Hyde Lane SPS | 225 | 53.3101 | 29.8206 | 51 | 51 | 403.6779 | 0.225 | 1.2866 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 5528 | 0.08437 | 221330.9688 | 3.9574 | 10.51 | 11.13 | 12.26 | 114 | 404 | 3.9574 | 16.2174 | 5.7074 | 1.75
15715 | Bridgwater Horsey Bath Road SPS | 100 | 52.4767 | 5.8905 | 54 | 54 | 101.4149 | 0.1 | 6.8966 | Chilton Trinity . STW | Bridgwater Bristol Road SPS | 5441 | 2.4242 | 527288.4845 | 79.514 | 6.53 | 6.45 | 7.01 | 86 | 102 | 79.514 | 86.524 | 79.994 | 0.48
13093 | Doniford . SPS | 315 | 52.0138 | 58.4483 | 60 | 60 | 1042.1323 | 0.315 | 0.77227 | Watchet . STW | Watchet Market Street (Tunnel) SPS | 5393 | 0.030397 | 185992.4108 | 2.4416 | 7.85 | 30.45 | 30.66 | 984 | 1002 | 2.4416 | 33.1016 | 25.2516 | 22.81
15347 | Woolavington Causeway SPS | 400 | 50.5786 | 94.2478 | - | 94.2478 | 5213.2347 | 0.4 | 0.7523 | West Huntspill STW | West Huntspill STW | 5244 | 0.028846 | 230073.0041 | 8.5841 | 4.99 | 4.9 | 7.01 | 2902 | 5214 | 8.5841 | 15.5941 | 10.6041 | 2.02
15082 | Wimborne Brook Road No 1 SPS | 350 | 50.5555 | 72.1585 | 130 | 130 | 1049.5245 | 0.35 | 1.3553 | Wimborne Brook Road STW | Wimborne Brook Road STW | 5242 | 0.093625 | 362685.201 | 6.5077 | - | 17.33 | 18.75 | 332 | 524 | 6.5077 | 25.2577 | - | -
15409 | Bridgwater Bower Lane Bower Manor SPS | 200 | 50.1851 | 23.5619 | - | 23.5619 | 1098.6293 | 0.2 | 0.7523 | Chilton Trinity . STW | Bridgwater Horsey Bath Road SPS | 5204 | 0.028846 | 115036.502 | 4.362 | - | 6.37 | 8.31 | 472 | 778 | 4.362 | 12.672 | - | -
15027 | Christchurch Avenue Road SPS | 225 | 48.773 | 29.8206 | - | 29.8206 | 8.201 | 0.225 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Quomps No 2 SPS | 5057 | 0.028846 | 129416.0648 | 0.028002 | 7.43 | 7.34 | 7.43 | - | 8 | 0.028002 | 7.458 | 0.028002 | 0
15090 | West Parley Church Lane SPS | 350 | 48.0786 | 72.1585 | 118 | 118 | 1467.1666 | 0.35 | 1.2302 | Kinson New Road Northbourne STW | Kinson New Road Northbourne STW | 4985 | 0.077138 | 329206.567 | 7.5151 | - | 9.87 | 10.36 | 52 | 746 | 7.5151 | 17.8751 | - | -
14502 | Bristol Whitby Road B Co-Op Depot Arnos Vale SPS | 200 | 47.4999 | 23.5619 | 30 | 30 | 301.3443 | 0.2 | 0.95785 | Avonmouth Kingsweston Lane STW | Bristol Dalby Ave SPS | 4925 | 0.046763 | 146469.0235 | 1.9215 | 9.99 | 12.64 | 13.48 | 114 | 292 | 1.9215 | 15.4015 | 5.4115 | 3.49
14501 | Bristol Whitby Road St Annes SPS | 400 | 46.111 | 94.2478 | 92.1 | 92.1 | 697.7251 | 0.4 | 0.73515 | Avonmouth Kingsweston Lane STW | Bristol Whitby Road B Co-Op Depot Arnos Vale SPS | 4781 | 0.027546 | 224829.951 | 1.0982 | 10.97 | 16.35 | 16.35 | 692 | 692 | 1.0982 | 17.4482 | 6.4782 | 5.38
14259 | Wareham South East SPS | 375 | 45.7638 | 82.835 | 54 | 54 | 1128.5509 | 0.375 | 0.49042 | Wareham Keysworth Drive STW | Wareham Keysworth Drive STW | 4745 | 0.012259 | 140610.2625 | 0.87454 | 2.31 | 2.63 | 5.05 | 526 | 1128 | 0.87454 | 5.9245 | 3.6145 | 2.74
15606 | Clevedon The Beach SPS | 250 | 45.6018 | 36.8155 | - | 36.8155 | 91.0411 | 0.25 | 0.7523 | Kingston Seymour Back Lane STW | Clevedon Clevedon Main SPS | 4728 | 0.028846 | 143795.6275 | 0.27175 | 10.6 | 16.29 | 16.36 | - | 90 | 0.27175 | 16.6317 | 6.0317 | 5.76
17367 | Cokers Frome . SPS | 200 | 44.3055 | 23.5619 | - | 23.5619 | 1192.8119 | 0.2 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 4594 | 0.028846 | 115036.502 | 4.7359 | 52.48 | 55.84 | 57.56 | 800 | 1192 | 4.7359 | 62.2959 | 9.8159 | 5.08
14132 | Bransgore Wiltshire Gardens SPS | 300 | 43.8425 | 53.0144 | 115 | 115 | 4427.4574 | 0.3 | 1.6319 | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 4546 | 0.13573 | 374309.7267 | 48.1426 | 13.43 | 2.49 | 14.93 | 488 | 4428 | 48.1426 | 63.0726 | 49.6426 | 1.5
15341 | Burnham-On-Sea Lynton Road SPS | 600 | 43.7499 | 212.0575 | - | 212.0575 | 914.702 | 0.6 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 4536 | 0.028846 | 345109.5061 | 0.907 | 6.33 | 5.79 | 6.65 | 120 | 914 | 0.907 | 7.557 | 1.227 | 0.32
14301 | Stalbridge . SPS | 250 | 43.0786 | 36.8155 | 61 | 61 | 2521.6805 | 0.25 | 1.2465 | Marnhull Common STW | Marnhull Common STW | 4467 | 0.079191 | 238256.2782 | 20.304 | 60.96 | 56.59 | 60.96 | - | 2522 | 20.304 | 81.264 | 20.304 | 0
15555 | Wyke Regis Hillcrest Road SPS | 450 | 42.4305 | 119.2823 | 150 | 150 | 426.0189 | 0.45 | 0.94603 | Weymouth . STW | Weymouth . STW | 4400 | 0.045615 | 325486.7188 | 0.94858 | 8.18 | 23.42 | 23.42 | 426 | 426 | 0.94858 | 24.3686 | 16.1886 | 15.24
17122 | Waytown Slape Mill Park SPS | 78 | 42.3147 | 3.5838 | - | 3.5838 | 241.7105 | 0.078 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 4388 | 0.028846 | 44864.2358 | 3.2761 | 30.49 | 30.97 | 31.1 | 238 | 242 | 3.2761 | 34.3761 | 3.8861 | 0.61
14317 | Hurdcott . SPS | 250 | 41.736 | 36.8155 | 60 | 60 | 681.8724 | 0.25 | 1.2261 | Hurdcott . STW | Hurdcott . STW | 4328 | 0.076616 | 234350.4376 | 5.3142 | 61.17 | 60.98 | 61.26 | 4 | 682 | 5.3142 | 66.5742 | 5.4042 | 0.09
15495 | Netherbury Beaminster SPS | 78 | 41.736 | 3.5838 | 3.8 | 3.8 | 52.2625 | 0.078 | 0.79769 | Bridport Wych Farm STW | Waytown Slape Mill Park SPS | 4328 | 0.032431 | 47571.1358 | 0.79436 | 36.06 | 36.24 | 36.24 | 52 | 52 | 0.79436 | 37.0344 | 0.97436 | 0.18
15645 | Pill Avon Road SPS | 300 | 41.5277 | 53.0144 | 80 | 80 | 994.9379 | 0.3 | 1.1352 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 4306 | 0.065686 | 260389.3751 | 5.2857 | 8.75 | 9.14 | 9.66 | 16 | 994 | 5.2857 | 14.9457 | 6.1957 | 0.91
14414 | Charminster North Street SPS | 250 | 40.7175 | 36.8155 | 45 | 45 | 1830.7486 | 0.25 | 0.91954 | Dorchester Louds Mill St Georges Road STW | Cokers Frome . SPS | 4222 | 0.043097 | 175762.8282 | 8.1006 | 81 | 66.99 | 81.49 | 74 | 1830 | 8.1006 | 89.5906 | 8.5906 | 0.49
16050 | Bath Ea Depot SPS | 200 | 40.6712 | 23.5619 | 29.9 | 29.9 | 28.6198 | 0.2 | 0.95466 | Saltford Mead Lane STW | Saltford Mead Lane STW | 4217 | 0.046452 | 145980.7934 | 0.1813 | 17.21 | 17.62 | 17.67 | 26 | 28 | 0.1813 | 17.8513 | 0.6413 | 0.46
14127 | Gillingham Brickyard Lane SPS | 175 | 40.0925 | 18.0396 | 65 | 65 | 381.7774 | 0.175 | 2.7107 | Gillingham Common Mead Lane STW | Gillingham Common Mead Lane STW | 4157 | 0.3745 | 362685.201 | 22.5754 | 70.03 | 75.03 | 75.15 | 380 | 382 | 22.5754 | 97.7254 | 27.6954 | 5.12
14033 | Christchurch Purewell SPS | 300 | 40.0694 | 53.0144 | - | 53.0144 | 766.7127 | 0.3 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 4155 | 0.028846 | 172554.753 | 1.8153 | 2.15 | 3.15 | 3.46 | - | 766 | 1.8153 | 5.2753 | 3.1253 | 1.31
14570 | Amesbury Ratfyn Lane SPS | 250 | 39.9536 | 36.8155 | - | 36.8155 | 988.6718 | 0.25 | 0.7523 | Ratfyn . STW | Ratfyn . STW | 4143 | 0.028846 | 143795.6275 | 2.9511 | 73.63 | 75.14 | 84.78 | 392 | 988 | 2.9511 | 87.7311 | 14.1011 | 11.15
14145 | Malmesbury Tanners Bridge SPS | 120 | 39.5138 | 8.4823 | 18 | 18 | 7.5827 | 0.12 | 1.5964 | Malmesbury . STW | Malmesbury . STW | 4097 | 0.1299 | 146469.0235 | 0.25612 | 70.45 | 70.08 | 70.45 | 0 | 8 | 0.25612 | 70.7061 | 0.25612 | 0
15447 | Taunton Mountway Bishops Hull SPS | 150 | 38.8888 | 13.2536 | 120 | 120 | 3.9349 | 0.15 | 6.8114 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 4032 | 2.3647 | 781168.1252 | 1.7751 | - | - | - | - | - | 1.7751 | - | - | -
15680 | Portishead Black Nore (Nautical School) SPS | 225 | 38.6573 | 29.8206 | 26 | 26 | 1945.5778 | 0.225 | 0.65591 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 4008 | 0.021928 | 112835.3959 | 5.0809 | 10.32 | 21.79 | 24.07 | - | 1946 | 5.0809 | 29.1509 | 18.8309 | 13.75
14577 | Ford Green Lane SPS | 225 | 38.4258 | 29.8206 | - | 29.8206 | 880.0252 | 0.225 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 3984 | 0.028846 | 129416.0648 | 3.0048 | - | 57.49 | 63.7 | 298 | 558 | 3.0048 | 66.7048 | - | -
14404 | Beaminster Southgate SPS | 315 | 38.1481 | 58.4483 | 31 | 31 | 9591.7628 | 0.315 | 0.39901 | Bridport Wych Farm STW | Netherbury Beaminster SPS | 3956 | 0.0081144 | 96096.0789 | 6.2108 | 33.52 | 33.52 | 68.96 | 3956 | 9584 | 6.2108 | 75.1708 | 41.6508 | 35.44
15237 | Poole Magna Road SPS | 500 | 38.0555 | 147.2622 | 100 | 100 | 5648.8027 | 0.5 | 0.51086 | Poole Cabot Lane STW | Poole Cabot Lane STW | 3946 | 0.013301 | 195292.0313 | 3.3023 | 32.64 | 25.82 | 52.98 | 560 | 5648 | 3.3023 | 56.2823 | 23.6423 | 20.34
15060 | West Moors Pennington Copse SPS | 200 | 37.8471 | 23.5619 | 50 | 50 | 420.4868 | 0.2 | 1.5964 | Palmersford . STW | Ferndown A31 Tricketts Cross SPS | 3924 | 0.1299 | 244115.0391 | 7.3385 | 14.69 | 17.73 | 17.73 | 420 | 420 | 7.3385 | 25.0685 | 10.3785 | 3.04
14220 | Lytchett Matravers Bulbury Lane SPS | 200 | 36.6203 | 23.5619 | 26 | 26 | 4811.2697 | 0.2 | 0.83014 | Blackheath . STW | Blackheath . STW | 3797 | 0.035124 | 126939.8203 | 23.1667 | 33.44 | 27.77 | 36.75 | - | 4812 | 23.1667 | 59.9167 | 26.4767 | 3.31
19830 | Worle Moor Lane SPS | 250 | 35.8564 | 36.8155 | - | 36.8155 | 2215.3522 | 0.25 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 3718 | 0.028846 | 143795.6275 | 6.6126 | - | 5.86 | 6.66 | - | 1584 | 6.6126 | 13.2726 | - | -
14447 | Keevil The Street SPS | 170 | 35.5323 | 17.0235 | 37 | 37 | 466.4902 | 0.17 | 1.6351 | Keevil . STW | Keevil . STW | 3684 | 0.13627 | 212523.6811 | 10.5184 | 50.25 | 53.08 | 53.25 | 448 | 468 | 10.5184 | 63.7684 | 13.5184 | 3
15075 | Corfe Mullen Pardys Hill SPS | 250 | 35.1851 | 36.8155 | 42 | 42 | 718.7682 | 0.25 | 0.85824 | Corfe Mullen Dorchester Road STW | Corfe Mullen Dorchester Road STW | 3648 | 0.037542 | 164045.3063 | 2.7776 | 30.47 | 65.76 | 65.79 | 718 | 722 | 2.7776 | 68.5676 | 38.0976 | 35.32
15051 | Corfe Mullen Rushcombe Bottom SPS | 200 | 34.9999 | 23.5619 | 25 | 25 | 351.1615 | 0.2 | 0.79821 | Corfe Mullen Dorchester Road STW | Corfe Mullen Dorchester Road STW | 3629 | 0.032474 | 122057.5196 | 1.5658 | 56.16 | 75.57 | 75.57 | - | 352 | 1.5658 | 77.1358 | 20.9758 | 19.41
14496 | Congresbury South SPS | 350 | 34.2592 | 72.1585 | - | 72.1585 | 3860.214 | 0.35 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 3552 | 0.028846 | 201313.8786 | 7.5205 | 5.64 | 5.86 | 6.94 | 484 | 3860 | 7.5205 | 14.4605 | 8.8205 | 1.3
15792 | Weston-Super-Mare Knightstone Road SPS | 250 | 34.2129 | 36.8155 | 443 | 443 | 238.641 | 0.25 | 9.0524 | Weston-Super-Mare Accommodation Road Bleadon STW | Weston-Super-Mare Accommodation Road Bleadon STW | 3548 | 4.1766 | 1730287.3973 | 98.5877 | 7.86 | 7.94 | 8.04 | - | 238 | 98.5877 | 106.6277 | 98.7677 | 0.18
15147 | Pilning Pill Head SPS | 200 | 34.0509 | 23.5619 | - | 23.5619 | 167.1478 | 0.2 | 0.7523 | Redwick . STW | Redwick . STW | 3531 | 0.028846 | 115036.502 | 0.66364 | 7.3 | 6.73 | 7.69 | 14 | 170 | 0.66364 | 8.3536 | 1.0536 | 0.39
15669 | Melksham Western Way SPS | 250 | 33.9583 | 36.8155 | - | 36.8155 | 722.3202 | 0.25 | 0.7523 | Bowerhill Shails Lane STW | Bowerhill Shails Lane STW | 3521 | 0.028846 | 143795.6275 | 2.156 | 38.34 | 38.6 | 43.09 | 618 | 722 | 2.156 | 45.246 | 6.906 | 4.75
15658 | Bridgwater Whitfield Road SPS | 375 | 33.5647 | 82.835 | - | 82.835 | 135.0746 | 0.375 | 0.7523 | Chilton Trinity . STW | Bridgwater Bower Lane Bower Manor SPS | 3480 | 0.028846 | 215693.4413 | 0.24123 | 6.54 | 6.2 | 6.58 | 2 | 136 | 0.24123 | 6.8212 | 0.28123 | 0.04
14394 | Wellington Mitchells Pool SPS | 180 | 33.4259 | 19.0852 | 70 | 70 | 1419.6825 | 0.18 | 2.7593 | Wellington Tone STW | Wellington Tone STW | 3466 | 0.38805 | 379734.5053 | 83.8676 | 58.84 | 58.84 | 66.05 | 644 | 1420 | 83.8676 | 149.9176 | 91.0776 | 7.21
15587 | Sandford Mead Lane SPS | 100 | 33.0323 | 5.8905 | - | 5.8905 | 150.8476 | 0.1 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Banwell Riverside SPS | 3425 | 0.028846 | 57518.251 | 1.4727 | 15.84 | 21.58 | 21.58 | 150 | 150 | 1.4727 | 23.0527 | 7.2127 | 5.74
15042 | Burton Stony Lane SPS | 315 | 32.986 | 58.4483 | 35 | 35 | 1384.5937 | 0.315 | 0.45049 | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 3420 | 0.010344 | 108495.5729 | 1.1341 | 3.44 | 3.29 | 10.14 | 1202 | 1384 | 1.1341 | 11.2741 | 7.8341 | 6.7
15577 | Sandford Sandmead Lane SPS | 250 | 32.6851 | 36.8155 | 54 | 54 | 2760.3392 | 0.25 | 1.1034 | Weston-Super-Mare Accommodation Road Bleadon STW | Sandford Mead Lane SPS | 3389 | 0.062059 | 210915.3938 | 17.4806 | - | 5.26 | 21.26 | 730 | 2748 | 17.4806 | 38.7406 | - | -
14196 | Malmesbury Noahs Ark SPS | 300 | 31.9907 | 53.0144 | 39 | 39 | 2443.8775 | 0.3 | 0.55343 | Malmesbury . STW | Malmesbury Tanners Bridge SPS | 3317 | 0.015611 | 126939.8203 | 3.1767 | 78.01 | 73.25 | 87.24 | - | 2444 | 3.1767 | 90.4167 | 12.4067 | 9.23
14435 | Warminster Boreham Road SPS | 200 | 31.7129 | 23.5619 | - | 23.5619 | 2017.4899 | 0.2 | 0.7523 | Warminster . STW | Warminster . STW | 3288 | 0.028846 | 115036.502 | 8.0102 | 103.07 | 113.38 | 113.44 | 2014 | 2018 | 8.0102 | 121.4502 | 18.3802 | 10.37
14430 | Chew Magna Dumpers Lane SPS | 355 | 31.6897 | 74.2349 | 94 | 94 | 1242.3167 | 0.355 | 0.9526 | Chew Stoke Walley Court Road STW | Chew Stoke Walley Court Road STW | 3286 | 0.046251 | 258555.6471 | 3.7779 | 41.1 | 44.77 | 51 | 974 | 1228 | 3.7779 | 54.7779 | 13.6779 | 9.9
14371 | Cheddar Froglands SPS | 250 | 31.4351 | 36.8155 | 48 | 48 | 1428.1964 | 0.25 | 0.98084 | Cheddar . STW | Cheddar . STW | 3260 | 0.049034 | 187480.35 | 7.1738 | 8.35 | 12.27 | 12.27 | 1428 | 1428 | 7.1738 | 19.4438 | 11.0938 | 3.92
14583 | Bristol West Town Road SPS | 170 | 31.2499 | 17.0235 | 40 | 40 | 27.5502 | 0.17 | 1.7677 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 3240 | 0.15926 | 229755.3309 | 0.72475 | 9.55 | 9.16 | 9.55 | 0 | 28 | 0.72475 | 10.2748 | 0.72475 | 0
15396 | Woolavington Meadow Farm SPS | 300 | 31.2036 | 53.0144 | 33 | 33 | 960.7775 | 0.3 | 0.46828 | West Huntspill STW | Woolavington Causeway SPS | 3236 | 0.011177 | 107410.6172 | 0.90253 | 5.57 | 4.99 | 5.57 | 0 | 960 | 0.90253 | 6.4725 | 0.90253 | 0
14266 | Wareham Sandford Lane SPS | 200 | 31.2036 | 23.5619 | 60 | 60 | 1841.8217 | 0.2 | 1.9157 | Wareham Keysworth Drive STW | Wareham Keysworth Drive STW | 3236 | 0.18705 | 292938.047 | 46.1045 | 2.39 | 6.25 | 9.68 | 1170 | 1842 | 46.1045 | 55.7845 | 53.3945 | 7.29
14248 | East Burton Cross Roads SPS | 150 | 31.0416 | 13.2536 | 22 | 22 | 1102.1492 | 0.15 | 1.2488 | Wool . STW | Wool . STW | 3219 | 0.07948 | 143214.1563 | 17.1572 | 16.58 | 24.49 | 25.43 | 1072 | 1102 | 17.1572 | 42.5872 | 26.0072 | 8.85
14528 | Carlingcott Stoneage Lane SPS | 250 | 30.8564 | 36.8155 | 50 | 50 | 539.0586 | 0.25 | 1.0217 | Cam Valley Dunkerton STW | Cam Valley Dunkerton STW | 3200 | 0.053206 | 195292.0313 | 2.934 | 60.89 | 66.74 | 66.74 | - | 506 | 2.934 | 69.674 | 8.784 | 5.85
14381 | Westonzoyland . SPS | 305 | 30.7407 | 54.7962 | - | 54.7962 | 4935.6433 | 0.305 | 0.7523 | Chilton Trinity . STW | Bridgwater Bradney Bridge SPS | 3188 | 0.028846 | 175430.6656 | 11.4433 | 5.05 | 6.27 | 7.63 | 4688 | 4936 | 11.4433 | 19.0733 | 14.0233 | 2.58
15524 | Batheaston Elmhurst SPS | 225 | 29.8842 | 29.8206 | - | 29.8206 | 156.2033 | 0.225 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 3099 | 0.028846 | 129416.0648 | 0.53335 | 22.16 | 24.5 | 24.54 | 154 | 156 | 0.53335 | 25.0734 | 2.9134 | 2.38
15072 | Ferndown Ameysford Road SPS | 250 | 29.7453 | 36.8155 | 50 | 50 | 875.3146 | 0.25 | 1.0217 | Palmersford . STW | Ferndown Dugdell Close SPS | 3084 | 0.053206 | 195292.0313 | 4.7642 | - | 30.85 | 31.16 | 822 | 872 | 4.7642 | 35.9242 | - | -
19709 | Hilperton Cornbrash Rise SPS | 180 | 29.6527 | 19.0852 | - | 19.0852 | 23.5952 | 0.18 | 0.7523 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 3075 | 0.028846 | 103532.8518 | 0.10727 | 40.33 | 40.11 | 40.38 | 4 | 24 | 0.10727 | 40.4873 | 0.15727 | 0.05
14202 | Hankerton Hankerton Bridge SPS | 200 | 29.4675 | 23.5619 | 42 | 42 | 3070.58 | 0.2 | 1.341 | Malmesbury . STW | Malmesbury Noahs Ark SPS | 3056 | 0.091655 | 205056.6329 | 37.9783 | 88.98 | 90.42 | 94.69 | 1070 | 2374 | 37.9783 | 132.6683 | 43.6883 | 5.71
13014 | Axbridge Old Stw Site SPS | 250 | 29.3518 | 36.8155 | 53.5 | 53.5 | 2755.3402 | 0.25 | 1.0932 | Cheddar . STW | Cheddar . STW | 3044 | 0.060915 | 208962.4735 | 17.1323 | 6.66 | 12.26 | 12.66 | 2736 | 2754 | 17.1323 | 29.7923 | 23.1323 | 6
15541 | Keynsham The Hams SPS | 200 | 29.2823 | 23.5619 | 23 | 23 | 1032.9951 | 0.2 | 0.73436 | Keynsham . STW | Keynsham . STW | 3036 | 0.027486 | 112292.918 | 3.9121 | 11.37 | 23.56 | 23.93 | 974 | 1032 | 3.9121 | 27.8421 | 16.4721 | 12.56
19827 | St Georges Brimbleworth Farm SPS | 150 | 28.449 | 13.2536 | - | 13.2536 | 9.4019 | 0.15 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 2950 | 0.028846 | 86277.3765 | 0.054086 | 5.91 | 5.93 | 5.93 | 10 | 10 | 0.054086 | 5.9841 | 0.074086 | 0.02
15349 | Burnham-On-Sea Braithwaite Place Off Berrow Road SPS | 100 | 28.449 | 5.8905 | - | 5.8905 | 5.5921 | 0.1 | 0.7523 | West Huntspill STW | Burnham-On-Sea Rectory Drive SPS | 2950 | 0.028846 | 57518.251 | 0.054594 | 5.77 | 5.66 | 5.77 | - | 6 | 0.054594 | 5.8246 | 0.054594 | 0
15088 | Alderholt Sandleheath Road SPS | 205 | 28.1481 | 24.7548 | - | 24.7548 | 1421.705 | 0.205 | 0.7523 | Fordingbridge Frog Lane STW | Fordingbridge Frog Lane STW | 2919 | 0.028846 | 117912.4146 | 5.4687 | 41.59 | 45.99 | 55.19 | 432 | 1422 | 5.4687 | 60.6587 | 19.0687 | 13.6
14273 | Wool Railway Cottages SPS | 150 | 28.0786 | 13.2536 | 21 | 21 | 734.8307 | 0.15 | 1.192 | Wool . STW | East Burton Cross Roads SPS | 2912 | 0.072419 | 136704.4219 | 10.4372 | 15.24 | 17.48 | 17.59 | 732 | 734 | 10.4372 | 28.0272 | 12.7872 | 2.35
15219 | Fordingbridge Green Lane SPS | 100 | 27.8472 | 5.8905 | - | 5.8905 | 15.8778 | 0.1 | 0.7523 | Fordingbridge Frog Lane STW | Fordingbridge Frog Lane STW | 2888 | 0.028846 | 57518.251 | 0.15501 | 29.91 | 29.53 | 29.91 | 0 | 16 | 0.15501 | 30.065 | 0.15501 | 0
15647 | Bridgwater Pollard Way SPS | 150 | 27.7546 | 13.2536 | - | 13.2536 | 153.6852 | 0.15 | 0.7523 | Chilton Trinity . STW | Bridgwater Whitfield Road SPS | 2878 | 0.028846 | 86277.3765 | 0.88411 | 6.18 | 6.05 | 6.24 | 2 | 154 | 0.88411 | 7.1241 | 0.94411 | 0.06
14249 | Bloxworth Fox Pound SPS | 150 | 27.3379 | 13.2536 | - | 13.2536 | 2358.7696 | 0.15 | 0.7523 | Blackheath . STW | Blackheath . STW | 2835 | 0.028846 | 86277.3765 | 13.5693 | 30.72 | 28.5 | 32.22 | - | 2364 | 13.5693 | 45.7893 | 15.0693 | 1.5
15342 | Brent Knoll Forge House Brent Street SPS | 315 | 27.2453 | 58.4483 | - | 58.4483 | 3031.0562 | 0.315 | 0.7523 | West Huntspill STW | Burnham-On-Sea Ashcott Drive SPS | 2825 | 0.028846 | 181182.4907 | 6.7462 | 5.49 | 5.62 | 6.45 | 1784 | 1918 | 6.7462 | 13.1962 | 7.7062 | 0.96
15236 | Poole Canford Heath Road SPS | 200 | 27.2222 | 23.5619 | 44 | 44 | 477.1158 | 0.2 | 1.4049 | Poole Cabot Lane STW | Poole Cabot Lane STW | 2823 | 0.10059 | 214821.2344 | 6.4686 | 9.66 | 15.51 | 15.52 | 468 | 478 | 6.4686 | 21.9886 | 12.3286 | 5.86
15374 | Bridgwater Late Heal SPS | 75 | 27.1064 | 3.3134 | - | 3.3134 | 223.7258 | 0.075 | 0.7523 | Chilton Trinity . STW | Bridgwater Taunton Road SPS | 2811 | 0.028846 | 43138.6883 | 3.1944 | 5.82 | 6.74 | 6.8 | 214 | 224 | 3.1944 | 9.9944 | 4.1744 | 0.98
17562 | Bridgwater Stockmoor Village SPS | 200 | 26.8981 | 23.5619 | - | 23.5619 | 358.3168 | 0.2 | 0.7523 | Chilton Trinity . STW | Bridgwater Late Heal SPS | 2789 | 0.028846 | 115036.502 | 1.4227 | - | - | - | - | - | 1.4227 | - | - | -
15810 | Melksham Primrose Drive SPS | 160 | 26.6666 | 15.0796 | - | 15.0796 | 364.2594 | 0.16 | 0.7523 | Bowerhill Shails Lane STW | Melksham Western Way SPS | 2765 | 0.028846 | 92029.2016 | 1.9276 | 37.28 | 39.56 | 39.72 | 350 | 356 | 1.9276 | 41.6476 | 4.3676 | 2.44
14388 | Berkeley Park View Road SPS | 320 | 26.5972 | 60.3186 | 40 | 40 | 2622.6341 | 0.32 | 0.49888 | Sharpness . STW | Sharpness . STW | 2758 | 0.012685 | 122057.5196 | 2.5671 | 10.1 | 7.64 | 13.66 | 1728 | 2622 | 2.5671 | 16.2271 | 6.1271 | 3.56
14078 | Wells Haybridge SPS | 300 | 26.4351 | 53.0144 | - | 53.0144 | 1102.2707 | 0.3 | 0.7523 | Wells . STW | Wells . STW | 2741 | 0.028846 | 172554.753 | 2.6097 | 34.53 | 25.35 | 52.71 | - | 1102 | 2.6097 | 55.3197 | 20.7897 | 18.18
14269 | Bere Regis Court Farm Southbrook SPS | 225 | 25.6249 | 29.8206 | - | 29.8206 | 4082.5314 | 0.225 | 0.7523 | Blackheath . STW | Bloxworth Fox Pound SPS | 2657 | 0.028846 | 129416.0648 | 13.9397 | 33.21 | 37.23 | 39.45 | - | 4086 | 13.9397 | 53.3897 | 20.1797 | 6.24
14427 | Hallatrow . SPS | 225 | 25.4629 | 29.8206 | 52 | 52 | 1737.7926 | 0.225 | 1.3118 | Paulton . STW | Paulton . STW | 2640 | 0.087711 | 225670.7917 | 17.7015 | 81.82 | 77.59 | 89.17 | 886 | 1940 | 17.7015 | 106.8715 | 25.0515 | 7.35
19129 | Weston-Super-Mare Diamond Batch SPS | 450 | 25.2777 | 119.2823 | - | 119.2823 | 4948.8719 | 0.45 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 2621 | 0.028846 | 258832.1296 | 7.0287 | - | 6.83 | 6.98 | 792 | 4936 | 7.0287 | 14.0087 | - | -
14353 | Downton South Lane SPS | 200 | 25.1851 | 23.5619 | - | 23.5619 | 911.9326 | 0.2 | 0.7523 | Downton Moot Lane STW | Downton Moot Lane STW | 2612 | 0.028846 | 115036.502 | 3.6207 | 35.24 | 39.81 | 39.92 | 910 | 912 | 3.6207 | 43.5407 | 8.3007 | 4.68
14329 | Salisbury Petersfinger SPS | 225 | 25.1388 | 29.8206 | - | 29.8206 | 1079.6521 | 0.225 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 2607 | 0.028846 | 129416.0648 | 3.6864 | 43.15 | 42.75 | 43.94 | 126 | 1080 | 3.6864 | 47.6264 | 4.4764 | 0.79
14174 | Box Mill Lane SPS | 170 | 24.1203 | 17.0235 | 27.3 | 27.3 | 168.9193 | 0.17 | 1.2064 | Box Mill Lane STW | Box Middle Hill SPS | 2501 | 0.074183 | 156808.0134 | 2.0901 | 33.75 | 42.58 | 42.63 | - | 168 | 2.0901 | 44.7201 | 10.9701 | 8.88
15297 | Drayton Ducks Lane SPS | 250 | 23.6574 | 36.8155 | 45 | 45 | 1667.3048 | 0.25 | 0.91954 | Langport Portfield Lane STW | Langport Westover SPS | 2453 | 0.043097 | 175762.8282 | 7.3774 | 10.38 | 27.5 | 29.91 | 1608 | 1668 | 7.3774 | 37.2874 | 26.9074 | 19.53
15309 | Charlton Mackerell Rookery Farm SPS | 250 | 23.5185 | 36.8155 | - | 36.8155 | 3548.3385 | 0.25 | 0.7523 | Somerton Barpool Lane STW | Somerton Barpool Lane STW | 2439 | 0.028846 | 143795.6275 | 10.5914 | 15.45 | 27.37 | 27.37 | 3548 | 3548 | 10.5914 | 37.9614 | 22.5114 | 11.92
14064 | Kingswood Willsbridge SPS | 320 | 23.449 | 60.3186 | 30 | 30 | 101.0541 | 0.32 | 0.37416 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 2432 | 0.0071354 | 91543.1397 | 0.056647 | 13.45 | 28.87 | 28.87 | 102 | 102 | 0.056647 | 28.9266 | 15.4766 | 15.42
14337 | Alderbury Home Farm SPS | 200 | 23.125 | 23.5619 | 22.8 | 22.8 | 2236.0935 | 0.2 | 0.72797 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger SPS | 2398 | 0.02701 | 111316.4578 | 8.325 | 41.53 | 43.15 | 43.15 | - | 2236 | 8.325 | 51.475 | 9.945 | 1.62
15551 | Weymouth Preston Fisherbridge Estate SPS | 400 | 23.0092 | 94.2478 | - | 94.2478 | 3997.2205 | 0.4 | 0.7523 | Weymouth . STW | Weymouth Radipole SPS | 2386 | 0.028846 | 230073.0041 | 6.5818 | - | 15.04 | 45.05 | 2232 | 4046 | 6.5818 | 51.6318 | - | -
15487 | Bridport East Road SPS | 200 | 22.9629 | 23.5619 | - | 23.5619 | 12.4652 | 0.2 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 2381 | 0.028846 | 115036.502 | 0.049491 | - | 8 | 8 | - | 8 | 0.049491 | 8.0495 | - | -
13326 | Warmwell Crossways Of B3390 SPS | 280 | 22.8472 | 46.1814 | - | 46.1814 | 7680.7455 | 0.28 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 2369 | 0.028846 | 161051.1028 | 19.8482 | 48.26 | 55.97 | 62.1 | 5354 | 7682 | 19.8482 | 81.9482 | 33.6882 | 13.84
19285 | Yate Brimsham Park SPS | 100 | 22.824 | 5.8905 | - | 5.8905 | 242.8378 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 2367 | 0.028846 | 57518.251 | 2.3708 | 68.59 | 70.96 | 71.05 | 120 | 124 | 2.3708 | 73.4208 | 4.8308 | 2.46
19152 | Devizes Cannings Lock ( Le Marchant: Barrack) SPS | 200 | 22.5462 | 23.5619 | - | 23.5619 | 1375.1229 | 0.2 | 0.7523 | Potterne . STW | Potterne . STW | 2338 | 0.028846 | 115036.502 | 5.4597 | 128.92 | 156.07 | 156.84 | - | 1376 | 5.4597 | 162.2997 | 33.3797 | 27.92
15673 | Portland Southwell SPS | 400 | 22.4537 | 94.2478 | 160 | 160 | 1727.3235 | 0.4 | 1.2771 | Weymouth . STW | Weymouth . STW | 2328 | 0.083134 | 390584.0626 | 8.0514 | 35.22 | 73.4 | 73.4 | 1728 | 1728 | 8.0514 | 81.4514 | 46.2314 | 38.18
19459 | Norton Fitzwarren Cotford St Luke No.2 (Tone Vale Interstage) SPS | 225 | 22.3611 | 29.8206 | - | 29.8206 | 2023.7378 | 0.225 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Silk Mills SPS | 2319 | 0.028846 | 129416.0648 | 6.91 | - | 20.82 | 26.49 | 58 | 1936 | 6.91 | 33.4 | - | -
15134 | Severn Beach . SPS | 300 | 22.2685 | 53.0144 | - | 53.0144 | 1969.2554 | 0.3 | 0.7523 | Redwick . STW | Pilning Pill Head SPS | 2309 | 0.028846 | 172554.753 | 4.6624 | - | 6.82 | 11.01 | 1632 | 1808 | 4.6624 | 15.6724 | - | -
15318 | Stoford Hillside Main SPS | 150 | 21.8287 | 13.2536 | 36 | 36 | 2483.3009 | 0.15 | 2.0434 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Sherborne Road (Pen Mill) STW | 2264 | 0.21282 | 234350.4376 | 102.3057 | 34.39 | 34.72 | 45.58 | - | 2484 | 102.3057 | 147.8857 | 113.4957 | 11.19
19487 | Cotford St Luke Cotford St Luke No 1 SPS | 225 | 21.7824 | 29.8206 | - | 29.8206 | 1387.887 | 0.225 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Norton Fitzwarren Cotford St Luke No.2 (Tone Vale Interstage) SPS | 2259 | 0.028846 | 129416.0648 | 4.7389 | - | 38.08 | 40.93 | - | 1376 | 4.7389 | 45.6689 | - | -
14581 | Bristol Victoria Road SPS | 300 | 21.5509 | 53.0144 | 111 | 111 | 584.7975 | 0.3 | 1.5751 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 2235 | 0.12646 | 361290.2579 | 5.929 | 9.57 | 8.8 | 9.57 | 0 | 584 | 5.929 | 15.499 | 5.929 | 0
14397 | Beer Hackett . SPS | 200 | 21.4814 | 23.5619 | 29 | 29 | 2366.021 | 0.2 | 0.92593 | Thornford Bridge Halt STW | Thornford Bridge Halt STW | 2228 | 0.043697 | 141586.7227 | 14.115 | - | 42.88 | 49.68 | - | 1210 | 14.115 | 63.795 | - | -
14312 | Shrewton Homanton SPS | 225 | 21.4583 | 29.8206 | - | 29.8206 | 1477.0815 | 0.225 | 0.7523 | Shrewton . STW | Shrewton . STW | 2225 | 0.028846 | 129416.0648 | 5.0435 | 85.92 | 85.96 | 86 | 4 | 1474 | 5.0435 | 91.0435 | 5.1235 | 0.08
14289 | Ilchester Ilchester Main SPS | 200 | 21.2963 | 23.5619 | 45 | 45 | 649.4659 | 0.2 | 1.4368 | Ilchester Pill Bridge Lane STW | Ilchester Pill Bridge Lane STW | 2208 | 0.10522 | 219703.5352 | 9.2048 | 12.84 | 12.07 | 13.55 | 506 | 650 | 9.2048 | 22.7548 | 9.9148 | 0.71
14417 | Dunster Dunster Beach SPS | 120 | 21.0879 | 8.4823 | - | 8.4823 | 427.6065 | 0.12 | 0.7523 | Minehead Headworks STW | Minehead Headworks STW | 2187 | 0.028846 | 69021.9012 | 3.2879 | 6.97 | 6.82 | 6.97 | 0 | 408 | 3.2879 | 10.2579 | 3.2879 | 0
15152 | Patchway Brookfield Road SPS | 150 | 21.0648 | 13.2536 | - | 13.2536 | 19.3131 | 0.15 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 2184 | 0.028846 | 86277.3765 | 0.1111 | 62.2 | 61.91 | 62.35 | 4 | 20 | 0.1111 | 62.4611 | 0.2611 | 0.15
14305 | Salisbury Old Sarum Airfield (Partridge Way) SPS | 100 | 20.8333 | 5.8905 | - | 5.8905 | 261.0492 | 0.1 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Ford Green Lane SPS | 2160 | 0.028846 | 57518.251 | 2.5486 | 75 | 77.5 | 79.7 | 188 | 262 | 2.5486 | 82.2486 | 7.2486 | 4.7
19053 | Yeovil Alvington Triangle SPS | 200 | 20.8101 | 23.5619 | - | 23.5619 | 432.2519 | 0.2 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Sherborne Road (Pen Mill) STW | 2158 | 0.028846 | 115036.502 | 1.7162 | 56.24 | 64.51 | 64.51 | 432 | 432 | 1.7162 | 66.2262 | 9.9862 | 8.27
15544 | Temple Cloud Temple Bridge SPS | 150 | 20.787 | 13.2536 | 32 | 32 | 991.156 | 0.15 | 1.8164 | Paulton . STW | Hallatrow . SPS | 2156 | 0.16816 | 208311.5001 | 32.3404 | 89.08 | 102.19 | 102.35 | 980 | 986 | 32.3404 | 134.6904 | 45.6104 | 13.27
14437 | Warminster Portway SPS | 400 | 20.4861 | 94.2478 | - | 94.2478 | 2444.9393 | 0.4 | 0.7523 | Warminster . STW | Warminster . STW | 2124 | 0.028846 | 230073.0041 | 4.0258 | 111.89 | 114.36 | 116.79 | 276 | 2444 | 4.0258 | 120.8158 | 8.9258 | 4.9
15269 | Poole Blandford Road SPS | 150 | 20.4629 | 13.2536 | - | 13.2536 | 321.6782 | 0.15 | 0.7523 | Poole Cabot Lane STW | Poole Rectory / Ashmore Avenue SPS | 2122 | 0.028846 | 86277.3765 | 1.8505 | 3.25 | 3.4 | 3.4 | - | 320 | 1.8505 | 5.2505 | 2.0005 | 0.15
15271 | Poole King John Avenue SPS | 150 | 20.2314 | 13.2536 | - | 13.2536 | 121.4547 | 0.15 | 0.7523 | Poole Cabot Lane STW | Poole Magna Road SPS | 2098 | 0.028846 | 86277.3765 | 0.69869 | 25.72 | 33.2 | 33.2 | 122 | 122 | 0.69869 | 33.8987 | 8.1787 | 7.48
15614 | Portbury Dock SPS | 400 | 20.1388 | 94.2478 | - | 94.2478 | 1480.6401 | 0.4 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portbury Wharf The Drove Portbury STW | 2088 | 0.028846 | 230073.0041 | 2.438 | 9.14 | 8.44 | 10.55 | - | 1480 | 2.438 | 12.988 | 3.848 | 1.41
14270 | Bovington Terminal SPS | 315 | 19.9074 | 58.4483 | 55 | 55 | 1892.0083 | 0.315 | 0.70791 | Wool . STW | Wool . STW | 2064 | 0.025542 | 170493.0432 | 3.7385 | 19.28 | 23.73 | 24.27 | 1706 | 1710 | 3.7385 | 28.0085 | 8.7285 | 4.99
14205 | Malmesbury Flying Monk SPS | 280 | 19.8379 | 46.1814 | - | 46.1814 | 1455.7342 | 0.28 | 0.7523 | Malmesbury . STW | Malmesbury . STW | 2057 | 0.028846 | 161051.1028 | 3.7618 | 71.69 | 93.51 | 93.73 | 1416 | 1456 | 3.7618 | 97.4918 | 25.8018 | 22.04
14459 | Southwick Chantry Gardens SPS | 150 | 19.7916 | 13.2536 | 35 | 35 | 639.9152 | 0.15 | 1.9867 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 2052 | 0.20116 | 227840.7032 | 24.9323 | 43.04 | 48.22 | 48.65 | - | 640 | 24.9323 | 73.5823 | 30.5423 | 5.61
15569 | Portbury Drove SPS | 400 | 19.3981 | 94.2478 | 92.3 | 92.3 | 1974.174 | 0.4 | 0.73675 | Portbury Wharf The Drove Portbury STW | Portbury Dock SPS | 2012 | 0.027666 | 225318.1811 | 3.1204 | 6.59 | 8.89 | 10.62 | 1334 | 1974 | 3.1204 | 13.7404 | 7.1504 | 4.03
14648 | Chilton Polden Main SPS | 225 | 19.375 | 29.8206 | 36 | 36 | 4638.3199 | 0.225 | 0.90819 | West Huntspill STW | Woolavington Causeway SPS | 2009 | 0.042039 | 156233.625 | 22.9107 | 11.26 | 4.99 | 12.54 | 1862 | 4638 | 22.9107 | 35.4507 | 24.1907 | 1.28
15399 | Puriton Rye SPS | 225 | 19.074 | 29.8206 | - | 29.8206 | 2147.2237 | 0.225 | 0.7523 | West Huntspill STW | West Huntspill STW | 1978 | 0.028846 | 129416.0648 | 7.3316 | - | 4.68 | 6.59 | - | 2128 | 7.3316 | 13.9216 | - | -
14338 | Netheravon Camp Road SPS | 150 | 18.8888 | 13.2536 | - | 13.2536 | 554.0549 | 0.15 | 0.7523 | Netheravon . STW | Netheravon . STW | 1959 | 0.028846 | 86277.3765 | 3.1873 | 81.54 | 91.03 | 91.33 | 528 | 554 | 3.1873 | 94.5173 | 12.9773 | 9.79
15073 | Wimborne Pilford Heath SPS | 315 | 18.8657 | 58.4483 | 47 | 47 | 817.1677 | 0.315 | 0.60494 | Wimborne Brook Road STW | Wimborne Hayes Lane Colehill SPS | 1956 | 0.018652 | 145694.0551 | 1.1877 | 41.12 | 65.94 | 67.31 | 490 | 818 | 1.1877 | 68.4977 | 27.3777 | 26.19
15572 | Locking Locking Village SPS | 150 | 18.3796 | 13.2536 | 46 | 46 | 633.553 | 0.15 | 2.611 | Weston-Super-Mare Accommodation Road Bleadon STW | Uphill . SPS | 1906 | 0.34748 | 299447.7813 | 42.4332 | 5.7 | 5.62 | 13.69 | 220 | 634 | 42.4332 | 56.1232 | 50.4232 | 7.99
15580 | Langford Blackmoor Road SPS | 250 | 18.287 | 36.8155 | 40 | 40 | 3336.2009 | 0.25 | 0.81737 | Weston-Super-Mare Accommodation Road Bleadon STW | Sandford Sandmead Lane SPS | 1896 | 0.034052 | 156233.625 | 11.7157 | 18.74 | 31.26 | 34.99 | - | 3336 | 11.7157 | 46.7057 | 27.9657 | 16.25
15035 | Christchurch Queens Road SPS | 125 | 18.2407 | 9.2039 | - | 9.2039 | 231.2448 | 0.125 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Purewell SPS | 1892 | 0.028846 | 71897.8138 | 1.6858 | 2.91 | 4.39 | 4.41 | 228 | 232 | 1.6858 | 6.0958 | 3.1858 | 1.5
15089 | St Leonards Lions Lane Ashley Heath SPS | 175 | 18.2176 | 18.0396 | - | 18.0396 | 548.4945 | 0.175 | 0.7523 | Palmersford . STW | St Leonards Craigside Road SPS | 1889 | 0.028846 | 100656.9393 | 2.5856 | 20.97 | 22.54 | 23.92 | 262 | 548 | 2.5856 | 26.5056 | 5.5356 | 2.95
15091 | Ferndown Aldridge Road SPS | 200 | 18.0555 | 23.5619 | 28 | 28 | 981.0695 | 0.2 | 0.894 | Kinson New Road Northbourne STW | West Parley Church Lane SPS | 1872 | 0.040736 | 136704.4219 | 5.4631 | - | 27.52 | 27.95 | - | 346 | 5.4631 | 33.4131 | - | -
14467 | Holt The Star SPS | 200 | 17.9398 | 23.5619 | 101 | 101 | 1633.0645 | 0.2 | 2.0639 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 1860 | 0.2171 | 394489.9032 | 35.6275 | 34.51 | 42.27 | 42.27 | 1634 | 1634 | 35.6275 | 77.8975 | 43.3875 | 7.76
15306 | Lower Somerton . SPS | 200 | 17.7777 | 23.5619 | - | 23.5619 | 953.634 | 0.2 | 0.7523 | Somerton Barpool Lane STW | Somerton Barpool Lane STW | 1844 | 0.028846 | 115036.502 | 3.7863 | 18.68 | 27.37 | 30.46 | 286 | 954 | 3.7863 | 34.2463 | 15.5663 | 11.78
15405 | Bridgwater Bower Manor 3a SPS | 150 | 17.7314 | 13.2536 | - | 13.2536 | 47.8827 | 0.15 | 0.7523 | Chilton Trinity . STW | Bridgwater Pollard Way SPS | 1839 | 0.028846 | 86277.3765 | 0.27546 | 5.97 | 5.93 | 6.03 | 10 | 48 | 0.27546 | 6.3055 | 0.33546 | 0.06
19714 | Royal Wootton Bassett Templars Firs SPS | 100 | 17.2453 | 5.8905 | - | 5.8905 | 28.8664 | 0.1 | 0.7523 | Royal Wootton Bassett . STW | Royal Wootton Bassett . STW | 1788 | 0.028846 | 57518.251 | 0.28181 | 94.26 | 94.88 | 94.88 | - | 14 | 0.28181 | 95.1618 | 0.90181 | 0.62
15621 | Clevedon Ladye Bay SPS | 200 | 17.199 | 23.5619 | 35.5 | 35.5 | 399.8866 | 0.2 | 1.1335 | Kingston Seymour Back Lane STW | Clevedon The Beach SPS | 1784 | 0.065481 | 173321.6778 | 3.5507 | 20.85 | 39.89 | 39.92 | 398 | 400 | 3.5507 | 43.4707 | 22.6207 | 19.07
14221 | Upton Frenchs Farm SPS | 200 | 17.1759 | 23.5619 | - | 23.5619 | 361.6718 | 0.2 | 0.7523 | Lytchett Minster Lytchett Bay STW | Lytchett Minster Lytchett Bay STW | 1781 | 0.028846 | 115036.502 | 1.436 | 4.82 | 9.38 | 9.44 | 332 | 362 | 1.436 | 10.876 | 6.056 | 4.62
14406 | Maiden Newton Frome Lane SPS | 50 | 17.1527 | 1.4726 | - | 1.4726 | 1670.3245 | 0.05 | 0.7523 | Maiden Newton Dorchester Road STW | Maiden Newton Dorchester Road STW | 1779 | 0.028846 | 28759.1255 | 41.0747 | 105.02 | 105.14 | 107.89 | 1654 | 1670 | 41.0747 | 148.9647 | 43.9447 | 2.87
15317 | Norton Sub Hamdon . SPS | 150 | 17.1527 | 13.2536 | 15.4 | 15.4 | 3563.2626 | 0.15 | 0.87413 | South Petherton North Street STW | South Petherton North Street STW | 1779 | 0.038945 | 100249.9094 | 27.5067 | 26.52 | 45.16 | 45.37 | - | 3524 | 27.5067 | 72.8767 | 46.3567 | 18.85
14387 | Sharpness Docks West SPS | 220 | 17.1064 | 28.51 | - | 28.51 | 748.3736 | 0.22 | 0.7523 | Sharpness . STW | Sharpness . STW | 1774 | 0.028846 | 126540.1522 | 2.6298 | 11.9 | 7.63 | 12.38 | - | 746 | 2.6298 | 15.0098 | 3.1098 | 0.48
14409 | Burton Bradstock Burton Freshwater SPS | 200 | 17.0833 | 23.5619 | - | 23.5619 | 1269.016 | 0.2 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 1772 | 0.028846 | 115036.502 | 5.0385 | 6.44 | 11.11 | 31.34 | - | 1270 | 5.0385 | 36.3785 | 29.9385 | 24.9
15024 | Christchurch Hoborne Farm SPS | 225 | 17.0139 | 29.8206 | - | 29.8206 | 236.9591 | 0.225 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Somerford Bridge SPS | 1764 | 0.028846 | 129416.0648 | 0.80909 | 7.99 | 8.31 | 8.91 | - | 236 | 0.80909 | 9.7191 | 1.7291 | 0.92
14326 | Stoford . SPS | 125 | 16.9907 | 9.2039 | - | 9.2039 | 401.6917 | 0.125 | 0.7523 | Wishford Wilton Road STW | Wishford Wilton Road STW | 1762 | 0.028846 | 71897.8138 | 2.9285 | 58.33 | 58.04 | 58.89 | 80 | 402 | 2.9285 | 61.8185 | 3.4885 | 0.56
15056 | Shapwick Shapwick Cross SPS | 100 | 16.6435 | 5.8905 | - | 5.8905 | 183.881 | 0.1 | 0.7523 | Tarrant Crawford . STW | Tarrant Crawford . STW | 1726 | 0.028846 | 57518.251 | 1.7952 | 25.51 | 25.23 | 25.6 | 72 | 184 | 1.7952 | 27.3952 | 1.8852 | 0.09
15290 | Henstridge Marsh Lane (Henstridge No 2) SPS | 150 | 16.2731 | 13.2536 | 23 | 23 | 3237.7273 | 0.15 | 1.3055 | Marnhull Common STW | Stalbridge . SPS | 1688 | 0.08687 | 149723.8907 | 55.0185 | 64.59 | 64.59 | 64.72 | - | 3238 | 55.0185 | 119.7385 | 55.1485 | 0.13
15190 | Milborne St Andrew Manor Farm SPS | 200 | 16.2268 | 23.5619 | 47 | 47 | 353.307 | 0.2 | 1.5006 | Milborne St Andrew . STW | Milborne St Andrew . STW | 1683 | 0.11478 | 229468.1368 | 5.4564 | 76.9 | 76.88 | 76.9 | 0 | 344 | 5.4564 | 82.3564 | 5.4564 | 0
19169 | Bradley Stoke Ellan Hay Road SPS | 150 | 15.9027 | 13.2536 | - | 13.2536 | 184.1485 | 0.15 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 1649 | 0.028846 | 86277.3765 | 1.0594 | 54.81 | 59.36 | 59.45 | 116 | 184 | 1.0594 | 60.5094 | 5.6994 | 4.64
14309 | Donhead St Andrew . SPS | 150 | 15.787 | 13.2536 | - | 13.2536 | 6382.1155 | 0.15 | 0.7523 | Tisbury Higher Chicksgrove STW | Tisbury Higher Chicksgrove STW | 1637 | 0.028846 | 86277.3765 | 36.7145 | 106.51 | 88.58 | 130.51 | - | 6382 | 36.7145 | 167.2245 | 60.7145 | 24
19453 | Weston-Super-Mare Ebdon Grounds SPS | 200 | 15.7407 | 23.5619 | - | 23.5619 | 1885.4746 | 0.2 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 1632 | 0.028846 | 115036.502 | 7.486 | 6.04 | 5.71 | 6.76 | 30 | 1898 | 7.486 | 14.246 | 8.206 | 0.72
15481 | Bradpole Lee Lane SPS | 200 | 15.7176 | 23.5619 | 33 | 33 | 364.2457 | 0.2 | 1.0536 | Bridport Wych Farm STW | Bridport West Bay SPS | 1630 | 0.056583 | 161115.9258 | 2.8013 | 13.57 | 13.49 | 14.47 | 116 | 364 | 2.8013 | 17.2713 | 3.7013 | 0.9
14582 | Bristol Riverside St Annes SPS | - | 15.7176 | - | - | - | 392.1694 | - | - | Avonmouth Kingsweston Lane STW | Bristol Whitby Road St Annes SPS | 1630 | - | - | - | 9.84 | 9.31 | 10.9 | 132 | 392 | - | - | - | 1.06
14497 | Kewstoke Sand Road SPS | 280 | 15.6944 | 46.1814 | - | 46.1814 | 3554.4465 | 0.28 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 1628 | 0.028846 | 161051.1028 | 9.1852 | 5.25 | 6.17 | 6.56 | - | 3554 | 9.1852 | 15.7452 | 10.4952 | 1.31
14146 | Lyneham Pound Close SPS | 180 | 15.625 | 19.0852 | - | 19.0852 | 557.9991 | 0.18 | 0.7523 | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham B Site (Main Stw) Raf Lyneham STW | 1620 | 0.028846 | 103532.8518 | 2.5367 | 126.32 | 131.22 | 131.33 | 508 | 512 | 2.5367 | 133.8667 | 7.5467 | 5.01
14632 | Taunton Maidenbrook SPS | 300 | 15.6018 | 53.0144 | 82.1 | 82.1 | 360.4042 | 0.3 | 1.165 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 1618 | 0.06918 | 267224.5962 | 2.015 | - | 11.81 | 14.32 | 76 | 318 | 2.015 | 16.335 | - | -
14276 | Corfe Castle Studland Road SPS | 190 | 15.5092 | 21.2647 | 17 | 17 | 636.9888 | 0.19 | 0.60142 | Corfe Castle Wytch Farm Road STW | Corfe Castle Wytch Farm Road STW | 1608 | 0.018436 | 87367.4877 | 1.7445 | 10.25 | 13.96 | 21.76 | 234 | 636 | 1.7445 | 23.5045 | 13.2545 | 11.51
14434 | Edington Inmead SPS | 200 | 15.4398 | 23.5619 | - | 23.5619 | 744.035 | 0.2 | 0.7523 | Keevil . STW | Edington Tinhead Lower BayntINT | 1601 | 0.028846 | 115036.502 | 2.9541 | 71.67 | 75.64 | 76 | 718 | 736 | 2.9541 | 78.9541 | 7.2841 | 4.33
13197 | Mark . SPS | 200 | 15.324 | 23.5619 | - | 23.5619 | 6380.0763 | 0.2 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 1589 | 0.028846 | 115036.502 | 25.3313 | 5.54 | 5.28 | 8.58 | 5286 | 6368 | 25.3313 | 33.9113 | 28.3713 | 3.04
15394 | Sutton Mallet . SPS | 120 | 15.2546 | 8.4823 | 5 | 5 | 72.1092 | 0.12 | 0.44345 | Chilton Trinity . STW | Bridgwater Bradney Bridge SPS | 1582 | 0.010023 | 40685.8399 | 0.1982 | 6 | 5.1 | 6 | 0 | 62 | 0.1982 | 6.1982 | 0.1982 | 0
15379 | Highbridge Paddock Drive SPS | 100 | 15.1852 | 5.8905 | - | 5.8905 | 80.6705 | 0.1 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 1575 | 0.028846 | 57518.251 | 0.78756 | 5.38 | 5.63 | 5.63 | 80 | 80 | 0.78756 | 6.4176 | 1.0376 | 0.25
15630 | Chickerell Lower Way SPS | 150 | 15.1852 | 13.2536 | 15.5 | 15.5 | 247.3464 | 0.15 | 0.87981 | Weymouth . STW | Weymouth Radipole SPS | 1575 | 0.039453 | 100900.8828 | 1.9338 | - | 33.37 | 33.37 | 246 | 246 | 1.9338 | 35.3038 | - | -
15231 | Poole Sandbanks Pavilion SPS | 280 | 15.1389 | 46.1814 | 18 | 18 | 87.5162 | 0.28 | 0.29322 | Poole Cabot Lane STW | Poole Shore Road SPS | 1570 | 0.0043822 | 62772.4386 | 0.036354 | 2.02 | 4.21 | 4.22 | 86 | 88 | 0.036354 | 4.2564 | 2.2364 | 2.2
15064 | Shapwick Stewards Lane SPS | 315 | 15.1157 | 58.4483 | - | 58.4483 | 3023.8213 | 0.315 | 0.7523 | Tarrant Crawford . STW | Shapwick Shapwick Cross SPS | 1568 | 0.028846 | 181182.4907 | 6.7301 | - | 35.18 | 46.88 | 2552 | 3012 | 6.7301 | 53.6101 | - | -
14627 | Wickwar Inlet P.S SPS | 170 | 15.0694 | 17.0235 | - | 17.0235 | 107.0679 | 0.17 | 0.7523 | Wickwar . STW | Wickwar . STW | 1563 | 0.028846 | 97781.0267 | 0.52394 | 40.25 | 42.59 | 44.67 | 82 | 108 | 0.52394 | 45.1939 | 4.9439 | 4.42
19505 | Locking Raf SPS | 250 | 15.0231 | 36.8155 | - | 36.8155 | 370.3859 | 0.25 | 0.7523 | Wick St Lawrence . STW | Worle North (Fw) SPS | 1558 | 0.028846 | 143795.6275 | 1.1056 | 5.38 | 6.22 | 6.35 | 358 | 362 | 1.1056 | 7.4556 | 2.0756 | 0.97
15063 | Sturminster Marshall Newton Road SPS | 250 | 14.9537 | 36.8155 | - | 36.8155 | 2129.2063 | 0.25 | 0.7523 | Tarrant Crawford . STW | Shapwick Stewards Lane SPS | 1551 | 0.028846 | 143795.6275 | 6.3554 | 25.35 | 25.22 | 37.36 | 714 | 2130 | 6.3554 | 43.7154 | 18.3654 | 12.01
15069 | Wimborne East Borough Road SPS | 100 | 14.6296 | 5.8905 | - | 5.8905 | 77.7815 | 0.1 | 0.7523 | Wimborne Brook Road STW | Wimborne Poole Road SPS | 1517 | 0.028846 | 57518.251 | 0.75936 | 20.01 | 19.63 | 20.17 | 50 | 78 | 0.75936 | 20.9294 | 0.91936 | 0.16
14227 | Studland Wadmore Lane SPS | 150 | 14.5833 | 13.2536 | 11 | 11 | 967.2727 | 0.15 | 0.62438 | Studland Ferry Road STW | Studland Ferry Road STW | 1512 | 0.01987 | 71607.0781 | 3.8663 | 12.72 | 7.42 | 23.93 | 170 | 964 | 3.8663 | 27.7963 | 15.0763 | 11.21
15422 | Sharpness Old Minster Road SPS | 200 | 14.5602 | 23.5619 | - | 23.5619 | 173.1256 | 0.2 | 0.7523 | Sharpness . STW | Sharpness Docks West SPS | 1510 | 0.028846 | 115036.502 | 0.68737 | 13.74 | 13.41 | 13.76 | 6 | 168 | 0.68737 | 14.4474 | 0.70737 | 0.02
14252 | Studland Coombe SPS | 150 | 14.3981 | 13.2536 | 16.2 | 16.2 | 329.7157 | 0.15 | 0.91954 | Studland Ferry Road STW | Studland Wadmore Lane SPS | 1493 | 0.043097 | 105457.6969 | 2.8112 | 13.52 | 24.32 | 24.32 | 330 | 330 | 2.8112 | 27.1312 | 13.6112 | 10.8
14128 | Burley Esdaile Lane SPS | 250 | 14.375 | 36.8155 | - | 36.8155 | 8175.8971 | 0.25 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Hampshire Hatches Lane STW | 1491 | 0.028846 | 143795.6275 | 24.4041 | 54.87 | 12.19 | 64.44 | - | 8176 | 24.4041 | 88.8441 | 33.9741 | 9.57
15251 | Poole Cabot Lane SPS | 100 | 14.3518 | 5.8905 | - | 5.8905 | 5 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 1488 | 0.028846 | 57518.251 | 0.048813 | 5.72 | 5.74 | 5.74 | 6 | 6 | 0.048813 | 5.7888 | 0.068813 | 0.02
17625 | Chelston West Park SPS | 180 | 14.2592 | 19.0852 | - | 19.0852 | 930.65 | 0.18 | 0.7523 | Wellington Tone STW | Wellington Tone STW | 1479 | 0.028846 | 103532.8518 | 4.2308 | 50.75 | 65.44 | 65.72 | 900 | 928 | 4.2308 | 69.9508 | 19.2008 | 14.97
14431 | Bishop Sutton . SPS | 150 | 14.2129 | 13.2536 | 19.6 | 19.6 | 2481.4981 | 0.15 | 1.1125 | Chew Stoke Walley Court Road STW | Chew Stoke Walley Court Road STW | 1474 | 0.063085 | 127590.7938 | 30.7687 | 57.84 | 43.68 | 62.53 | 1630 | 2472 | 30.7687 | 93.2987 | 35.4587 | 4.69
14376 | Moorlinch Right Drove SPS | 305 | 14.1435 | 54.7962 | - | 54.7962 | 4225.0709 | 0.305 | 0.7523 | Chilton Trinity . STW | Sutton Mallet . SPS | 1467 | 0.028846 | 175430.6656 | 9.7958 | 8.14 | 3.78 | 21.26 | 1960 | 4218 | 9.7958 | 31.0558 | 22.9158 | 13.12
14474 | Melksham Semington Roundabout SPS | 100 | 14.074 | 5.8905 | 19 | 19 | 2.6358 | 0.1 | 2.4266 | Melksham . STW | Melksham . STW | 1460 | 0.30011 | 185527.4297 | 0.25887 | 38.43 | 38.57 | 38.57 | 2 | 2 | 0.25887 | 38.8289 | 0.39887 | 0.14
14050 | Collingbourne Ducis . SPS | 170 | 13.9352 | 17.0235 | 20 | 20 | 810.6716 | 0.17 | 0.88383 | Collingbourne Ducis . STW | Collingbourne Ducis . STW | 1445 | 0.039815 | 114877.6655 | 5.4401 | 126.43 | 126.47 | 126.79 | 12 | 810 | 5.4401 | 132.2301 | 5.8001 | 0.36
13033 | Bradford Peverell Giles Cross SPS | 225 | 13.7963 | 29.8206 | - | 29.8206 | 1181.1132 | 0.225 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Charminster North Street SPS | 1431 | 0.028846 | 129416.0648 | 4.0329 | - | 61.93 | 65.93 | - | 1170 | 4.0329 | 69.9629 | - | -
15203 | Shillingstone Haywards Bridge SPS | 200 | 13.75 | 23.5619 | 8.5 | 8.5 | 740.2123 | 0.2 | 0.27139 | Shillingstone . STW | Shillingstone . STW | 1426 | 0.003754 | 41499.5567 | 0.40782 | 42.22 | 60.88 | 61.41 | 722 | 740 | 0.40782 | 61.8178 | 19.5978 | 19.19
15334 | Charlton Adam . SPS | 150 | 13.75 | 13.2536 | 21 | 21 | 690.6935 | 0.15 | 1.192 | Somerton Barpool Lane STW | Charlton Mackerell Rookery Farm SPS | 1426 | 0.072419 | 136704.4219 | 9.8103 | 28.12 | 36.13 | 36.4 | 680 | 686 | 9.8103 | 46.2103 | 18.0903 | 8.28
14198 | Calne Colemans Farm SPS | 225 | 13.7268 | 29.8206 | - | 29.8206 | 233.2682 | 0.225 | 0.7523 | Calne . STW | Calne . STW | 1424 | 0.028846 | 129416.0648 | 0.79649 | 69.94 | 70.85 | 71.63 | 178 | 234 | 0.79649 | 72.4265 | 2.4865 | 1.69
14391 | Stoke St Gregory No 1 Lane End SPS | 100 | 13.6574 | 5.8905 | 27 | 27 | 557.1292 | 0.1 | 3.4483 | Stoke St Gregory . STW | Stoke St Gregory . STW | 1416 | 0.60605 | 263644.2423 | 109.9269 | 23.9 | 23.52 | 23.9 | 0 | 558 | 109.9269 | 133.8269 | 109.9269 | 0
14097 | Baltonsborough Baltonsborough Main SPS | 180 | 13.6111 | 19.0852 | 47 | 47 | 2225.668 | 0.18 | 1.8526 | Butleigh . STW | Butleigh . STW | 1412 | 0.17494 | 254964.5964 | 59.6929 | - | 14.34 | 14.47 | 2198 | 2218 | 59.6929 | 74.1629 | - | -
15655 | Dorchester Weymouth Avenue SPS | 200 | 13.449 | 23.5619 | - | 23.5619 | 889.1531 | 0.2 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 1395 | 0.028846 | 115036.502 | 3.5303 | 61.31 | 80.82 | 80.83 | - | 890 | 3.5303 | 84.3603 | 23.0503 | 19.52
14365 | Salisbury Netherhampton Road SPS | 100 | 13.4027 | 5.8905 | - | 5.8905 | 21.0294 | 0.1 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 1390 | 0.028846 | 57518.251 | 0.2053 | 46.49 | 46.26 | 46.51 | - | 22 | 0.2053 | 46.7153 | 0.2253 | 0.02
17588 | West Wick Wolvers Hill Road SPS | 280 | 13.4027 | 46.1814 | - | 46.1814 | 2119.4104 | 0.28 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 1390 | 0.028846 | 161051.1028 | 5.4769 | 5.56 | 5.92 | 6.85 | 1420 | 1846 | 5.4769 | 12.3269 | 6.7669 | 1.29
14412 | Puddletown Blandford Road SPS | 180 | 13.3796 | 19.0852 | - | 19.0852 | 826.6204 | 0.18 | 0.7523 | Puddletown Piddlehinton Road STW | Puddletown Piddlehinton Road STW | 1388 | 0.028846 | 103532.8518 | 3.7579 | 56.48 | 66.48 | 68.3 | 822 | 826 | 3.7579 | 72.0579 | 15.5779 | 11.82
15361 | West Huntspill Crossways Withy Road SPS | 400 | 13.3565 | 94.2478 | - | 94.2478 | 1421.5163 | 0.4 | 0.7523 | West Huntspill STW | West Huntspill STW | 1385 | 0.028846 | 230073.0041 | 2.3407 | 5.44 | 4.9 | 7.24 | 560 | 1422 | 2.3407 | 9.5807 | 4.1407 | 1.8
15260 | Poole Esplanade Sterte SPS | 200 | 13.3565 | 23.5619 | - | 23.5619 | 251.0404 | 0.2 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 1385 | 0.028846 | 115036.502 | 0.99672 | 1.47 | 2.37 | 2.39 | 244 | 248 | 0.99672 | 3.3867 | 1.9167 | 0.92
14206 | Hankerton Hankerton East SPS | 80 | 13.287 | 3.7699 | - | 3.7699 | 521.4701 | 0.08 | 0.7523 | Malmesbury . STW | Hankerton Hankerton Bridge SPS | 1378 | 0.028846 | 46014.6008 | 6.8345 | 88.88 | 91.49 | 91.58 | 500 | 522 | 6.8345 | 98.4145 | 9.5345 | 2.7
15381 | Wembdon Common SPS | 225 | 13.2639 | 29.8206 | 52 | 52 | 514.2079 | 0.225 | 1.3118 | Chilton Trinity . STW | Bridgwater Chilton Street Saltlands SPS | 1376 | 0.087711 | 225670.7917 | 5.2378 | 6.15 | 6.3 | 7.2 | 212 | 514 | 5.2378 | 12.4378 | 6.2878 | 1.05
14408 | Bradford Peverell Mr Softies SPS | 600 | 13.2407 | 212.0575 | - | 212.0575 | 535.6078 | 0.6 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Bradford Peverell Giles Cross SPS | 1373 | 0.028846 | 345109.5061 | 0.5311 | 66.16 | 69.87 | 69.87 | 536 | 536 | 0.5311 | 70.4011 | 4.2411 | 3.71
14553 | Ilford Ilford Bridges SPS | 200 | 13.1713 | 23.5619 | - | 23.5619 | 2553.9601 | 0.2 | 0.7523 | Ilminster Ashwell STW | Ilminster Ashwell STW | 1366 | 0.028846 | 115036.502 | 10.1402 | - | 26.78 | 26.9 | 2548 | 2550 | 10.1402 | 37.0402 | - | -
15497 | Martinstown B3159 SPS | 127 | 12.9861 | 9.5008 | 10 | 10 | 2450.0501 | 0.127 | 0.79183 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 1347 | 0.031957 | 76886.6265 | 19.3406 | 76.65 | 107.45 | 110.28 | 2410 | 2450 | 19.3406 | 129.6206 | 52.9706 | 33.63
15618 | Christchurch Christchurch Airfield SPS | 200 | 12.9629 | 23.5619 | - | 23.5619 | 576.9516 | 0.2 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Somerford Bridge SPS | 1344 | 0.028846 | 115036.502 | 2.2907 | 6.52 | 7.61 | 7.62 | 568 | 574 | 2.2907 | 9.9107 | 3.3907 | 1.1
14456 | Bratton Trowbridge Road SPS | 170 | 12.6157 | 17.0235 | 18 | 18 | 1476.2753 | 0.17 | 0.79545 | Keevil . STW | Edington Inmead SPS | 1308 | 0.03225 | 103389.8989 | 8.0578 | 72 | 72.52 | 76.82 | 246 | 1474 | 8.0578 | 84.8778 | 12.8778 | 4.82
17234 | Portishead Forth Avenue SPS | 160 | 12.5231 | 15.0796 | - | 15.0796 | 400.3813 | 0.16 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 1299 | 0.028846 | 92029.2016 | 2.1188 | 8.38 | 9.56 | 9.57 | 398 | 400 | 2.1188 | 11.6888 | 3.3088 | 1.19
14199 | Upper Minety Flisteridge SPS | 180 | 12.4074 | 19.0852 | 12.5 | 12.5 | 3755.0123 | 0.18 | 0.49272 | Malmesbury . STW | Hankerton Hankerton East SPS | 1287 | 0.012374 | 67809.7331 | 7.4803 | 95.41 | 88.98 | 99.5 | 1492 | 3756 | 7.4803 | 106.9803 | 11.5703 | 4.09
15057 | Ferndown Thames Close SPS | 150 | 12.3842 | 13.2536 | 14 | 14 | 184.2821 | 0.15 | 0.79466 | Palmersford . STW | Ferndown A31 Tricketts Cross SPS | 1284 | 0.032186 | 91136.2813 | 1.1802 | 15.32 | 21.93 | 21.93 | 184 | 184 | 1.1802 | 23.1102 | 7.7902 | 6.61
14585 | Edington Broadmead Lane (Som) SPS | 200 | 12.2916 | 23.5619 | 14 | 14 | 921.1152 | 0.2 | 0.447 | West Huntspill STW | Chilton Polden Main SPS | 1275 | 0.010184 | 68352.211 | 1.3265 | 9.51 | 11.26 | 12.21 | - | 922 | 1.3265 | 13.5365 | 4.0265 | 2.7
14059 | Rowde Tower View SPS | 120 | 12.1296 | 8.4823 | 7.7 | 7.7 | 768.3189 | 0.12 | 0.68291 | Rowde . STW | Rowde . STW | 1258 | 0.02377 | 62656.1934 | 4.8896 | - | 62.56 | 63.51 | 44 | 754 | 4.8896 | 68.3996 | - | -
15215 | Ringwood Seymour Road SPS | 125 | 12.0602 | 9.2039 | - | 9.2039 | 435.6942 | 0.125 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Hightown Crow Lane SPS | 1251 | 0.028846 | 71897.8138 | 3.1763 | 21.89 | 23.14 | 23.48 | 414 | 436 | 3.1763 | 26.6563 | 4.7663 | 1.59
15377 | East Brent Chestnut Farm SPS | 250 | 12.0602 | 36.8155 | - | 36.8155 | 1809.5332 | 0.25 | 0.7523 | West Huntspill STW | Brent Knoll Forge House Brent Street SPS | 1251 | 0.028846 | 143795.6275 | 5.4012 | 6.1 | 5.8 | 6.21 | 36 | 1810 | 5.4012 | 11.6112 | 5.5112 | 0.11
15039 | Christchurch Beaconsfield Road SPS | 125 | 12.0602 | 9.2039 | - | 9.2039 | 366.698 | 0.125 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Quomps No 2 SPS | 1251 | 0.028846 | 71897.8138 | 2.6733 | 3.16 | 3.58 | 6.28 | 146 | 366 | 2.6733 | 8.9533 | 5.7933 | 3.12
15366 | Berrow Barton Road In Between 60 Barton Road & Boner Cottage SPS | 150 | 11.7361 | 13.2536 | - | 13.2536 | 449.1635 | 0.15 | 0.7523 | West Huntspill STW | Burnham-On-Sea Braithwaite Place Off Berrow Road SPS | 1217 | 0.028846 | 86277.3765 | 2.5839 | 6.01 | 5.57 | 6.05 | 334 | 428 | 2.5839 | 8.6339 | 2.6239 | 0.04
14386 | Greinton Moor Drive SPS | 250 | 11.7129 | 36.8155 | 34 | 34 | 1557.31 | 0.25 | 0.69476 | Chilton Trinity . STW | Moorlinch Right Drove SPS | 1215 | 0.024602 | 132798.5813 | 3.9783 | 14.83 | 7.7 | 21.65 | 666 | 1558 | 3.9783 | 25.6283 | 10.7983 | 6.82
14069 | Street Houndwood Drove SPS | 150 | 11.6898 | 13.2536 | 31.4 | 31.4 | 382.1636 | 0.15 | 1.7823 | Glastonbury The Beckery SSTW | Street Main SPS | 1212 | 0.16191 | 204405.6594 | 12.0113 | 9.03 | 11.6 | 11.74 | 362 | 382 | 12.0113 | 23.7513 | 14.7213 | 2.71
15576 | Congresbury North SPS | 150 | 11.6898 | 13.2536 | - | 13.2536 | 538.1473 | 0.15 | 0.7523 | Wick St Lawrence . STW | Congresbury South SPS | 1212 | 0.028846 | 86277.3765 | 3.0958 | 6.93 | 6.04 | 8.26 | 320 | 426 | 3.0958 | 11.3558 | 4.4258 | 1.33
14302 | Idmiston . SPS | 250 | 11.6203 | 36.8155 | 14.5 | 14.5 | 800.7347 | 0.25 | 0.2963 | Hurdcott . STW | Hurdcott . SPS | 1205 | 0.0044746 | 56634.6891 | 0.39211 | 66.5 | 68.69 | 69.08 | - | 708 | 0.39211 | 69.4721 | 2.9721 | 2.58
15106 | Poulshot Townsend SPS | 180 | 11.574 | 19.0852 | 17 | 17 | 2832.1363 | 0.18 | 0.6701 | Potterne . STW | Potterne . STW | 1200 | 0.022887 | 92221.237 | 10.2683 | 50.62 | 65.85 | 66.36 | 2790 | 2830 | 10.2683 | 76.6283 | 26.0083 | 15.74
19504 | Ilminster Canal Road SPS | 225 | 11.5278 | 29.8206 | - | 29.8206 | 323.7621 | 0.225 | 0.7523 | Ilminster Ashwell STW | Ilminster Ashwell STW | 1196 | 0.028846 | 129416.0648 | 1.1055 | 32.76 | 34.53 | 34.53 | - | 324 | 1.1055 | 35.6355 | 2.8755 | 1.77
15164 | Tytherington Stidcott SPS | 175 | 11.5046 | 18.0396 | - | 18.0396 | 1491.6227 | 0.175 | 0.7523 | Cromhall . STW | Cromhall . STW | 1193 | 0.028846 | 100656.9393 | 7.0315 | 51.89 | 56.66 | 66.04 | 902 | 1492 | 7.0315 | 73.0715 | 21.1815 | 14.15
14092 | Glastonbury Wells Road SPS | 180 | 11.4815 | 19.0852 | 12.8 | 12.8 | 1528.43 | 0.18 | 0.50455 | Glastonbury The Beckery SSTW | Glastonbury Porchestall SPS | 1191 | 0.012975 | 69437.1667 | 3.1883 | 6.75 | 16.56 | 16.56 | - | 1528 | 3.1883 | 19.7483 | 12.9983 | 9.81
15200 | Marnhull Sodom Lane SPS | 225 | 11.412 | 29.8206 | 19 | 19 | 1740.5775 | 0.225 | 0.47932 | Marnhull Common STW | Marnhull Common STW | 1184 | 0.01171 | 82456.6354 | 2.4679 | 58.54 | 82.83 | 83.11 | 1708 | 1740 | 2.4679 | 85.5779 | 27.0379 | 24.57
14425 | Clutton Greenbrook SPS | 200 | 11.3889 | 23.5619 | 30.9 | 30.9 | 1645.8204 | 0.2 | 0.98659 | Paulton . STW | Paulton . STW | 1181 | 0.049611 | 150863.0942 | 11.1222 | 104.33 | 139.81 | 140.33 | 1560 | 1588 | 11.1222 | 151.4522 | 47.1222 | 36
15465 | North Curry Stoke Road SPS | 125 | 11.3889 | 9.2039 | 9 | 9 | 535.7408 | 0.125 | 0.73563 | Stoke St Gregory . STW | Stoke St Gregory No 1 Lane End SPS | 1181 | 0.027582 | 70305.1313 | 3.7383 | 19.73 | 27.23 | 27.96 | 518 | 534 | 3.7383 | 31.6983 | 11.9683 | 8.23
15547 | Saltford The Shallows SPS | 250 | 11.2963 | 36.8155 | - | 36.8155 | 1458.8064 | 0.25 | 0.7523 | Keynsham . STW | Keynsham . STW | 1172 | 0.028846 | 143795.6275 | 4.3544 | - | 35.18 | 37.5 | - | 1404 | 4.3544 | 41.8544 | - | -
14400 | Broadmayne Broadmayne SPS | 180 | 11.1805 | 19.0852 | - | 19.0852 | 381.7507 | 0.18 | 0.7523 | Broadmayne West Knighton Road STW | Broadmayne West Knighton Road STW | 1160 | 0.028846 | 103532.8518 | 1.7355 | 47.07 | 48.56 | 48.56 | - | 382 | 1.7355 | 50.2955 | 3.2255 | 1.49
15414 | Bristol Central Trading Estate Bath Road SPS | 200 | 11.1805 | 23.5619 | - | 23.5619 | 696.5374 | 0.2 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Dalby Ave SPS | 1160 | 0.028846 | 115036.502 | 2.7655 | 8.96 | 12.64 | 14.31 | 380 | 694 | 2.7655 | 17.0755 | 8.1155 | 5.35
15228 | Poole Rockley Road SPS | 150 | 11.1574 | 13.2536 | - | 13.2536 | 69.3028 | 0.15 | 0.7523 | Poole Cabot Lane STW | Poole Rectory / Ashmore Avenue SPS | 1157 | 0.028846 | 86277.3765 | 0.39868 | 2.01 | 2.54 | 2.56 | 62 | 70 | 0.39868 | 2.9587 | 0.94868 | 0.55
15573 | Bleadon Purn SPS | 100 | 11.1111 | 5.8905 | 17 | 17 | 1805.5943 | 0.1 | 2.1711 | Weston-Super-Mare Accommodation Road Bleadon STW | Uphill . SPS | 1152 | 0.24026 | 165998.2266 | 142.2498 | 7.21 | 17.57 | 17.62 | 1804 | 1806 | 142.2498 | 159.8698 | 152.6598 | 10.41
15272 | Poole Seacombe Road SPS | 170 | 10.9491 | 17.0235 | - | 17.0235 | 373.561 | 0.17 | 0.7523 | Poole Cabot Lane STW | Poole Sandbanks Pavilion SPS | 1136 | 0.028846 | 97781.0267 | 1.828 | 1.4 | 3.72 | 3.72 | 368 | 368 | 1.828 | 5.548 | 4.148 | 2.32
14407 | Stratton Stratton Bridge SPS | 100 | 10.8565 | 5.8905 | - | 5.8905 | 977.4811 | 0.1 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Bradford Peverell Mr Softies SPS | 1126 | 0.028846 | 57518.251 | 9.5429 | 68.15 | 64.83 | 68.31 | - | 978 | 9.5429 | 77.8529 | 9.7029 | 0.16
14236 | Upton Gorse Lane SPS | 100 | 10.8333 | 5.8905 | - | 5.8905 | 788.9089 | 0.1 | 0.7523 | Lytchett Minster Lytchett Bay STW | Upton Moorlands Way SPS | 1124 | 0.028846 | 57518.251 | 7.7019 | 20.58 | 18.48 | 20.58 | 0 | 788 | 7.7019 | 28.2819 | 7.7019 | 0
17232 | Portishead Marina Boatyard SPS | 150 | 10.8333 | 13.2536 | - | 13.2536 | 228.3671 | 0.15 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portbury Wharf The Drove Portbury STW | 1124 | 0.028846 | 86277.3765 | 1.3137 | 8.71 | 8.3 | 8.95 | 112 | 228 | 1.3137 | 10.2637 | 1.5537 | 0.24
15146 | Frampton Cotterell Church Road SPS | 225 | 10.8102 | 29.8206 | - | 29.8206 | 568.8869 | 0.225 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 1121 | 0.028846 | 129416.0648 | 1.9425 | 56.43 | 70.15 | 70.21 | 566 | 568 | 1.9425 | 72.1525 | 15.7225 | 13.78
15616 | Barrington West End View SPS | 150 | 10.787 | 13.2536 | - | 13.2536 | 645.5674 | 0.15 | 0.7523 | Ilminster Ashwell STW | Ilford Ilford Bridges SPS | 1119 | 0.028846 | 86277.3765 | 3.7138 | 18.71 | 40.44 | 40.62 | - | 646 | 3.7138 | 44.3338 | 25.6238 | 21.91
15085 | St Ives Avon Castle SPS | 225 | 10.787 | 29.8206 | - | 29.8206 | 1275.3844 | 0.225 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Bickerley SPS | 1119 | 0.028846 | 129416.0648 | 4.3548 | 14.54 | 13.41 | 18.49 | 116 | 1274 | 4.3548 | 22.8448 | 8.3048 | 3.95
15275 | Poole Hewitt Road SPS | 120 | 10.7176 | 8.4823 | 15.8 | 15.8 | 162.2622 | 0.12 | 1.4013 | Poole Cabot Lane STW | Poole Turlin Main Blandford Road Turlin Moor SPS | 1112 | 0.10008 | 128567.2539 | 4.2368 | 2.8 | 3.68 | 3.87 | 136 | 162 | 4.2368 | 8.1068 | 5.3068 | 1.07
14261 | Studland Watery Lane SPS | 100 | 10.625 | 5.8905 | 2.5 | 2.5 | 398.9162 | 0.1 | 0.31928 | Studland Ferry Road STW | Studland Coombe SPS | 1102 | 0.0051959 | 24411.5039 | 0.7397 | 10.38 | 26.46 | 28.57 | 342 | 398 | 0.7397 | 29.3097 | 18.9297 | 18.19
15158 | Olveston The Common SPS | 150 | 10.6018 | 13.2536 | 21 | 21 | 919.4406 | 0.15 | 1.192 | Tockington Moor Lane STW | Tockington Moor Lane STW | 1100 | 0.072419 | 136704.4219 | 13.0593 | 7.09 | 29.12 | 29.13 | 918 | 920 | 13.0593 | 42.1893 | 35.0993 | 22.04
19535 | Portishead Quays SPS | 180 | 10.6018 | 19.0852 | - | 19.0852 | 160.2667 | 0.18 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 1100 | 0.028846 | 103532.8518 | 0.72858 | 6.51 | 6.66 | 7.11 | 52 | 160 | 0.72858 | 7.8386 | 1.3286 | 0.6
14375 | Pedwell . SPS | 200 | 10.5555 | 23.5619 | 16 | 16 | 1202.213 | 0.2 | 0.51086 | Chilton Trinity . STW | Greinton Moor Drive SPS | 1095 | 0.013301 | 78116.8125 | 2.2435 | 8.73 | 14.83 | 17.8 | - | 1202 | 2.2435 | 20.0435 | 11.3135 | 9.07
14054 | Pewsey Jubilee SPS | 180 | 10.5092 | 19.0852 | - | 19.0852 | 1496.8941 | 0.18 | 0.7523 | Pewsey Salisbury Road STW | Pewsey Salisbury Road STW | 1090 | 0.028846 | 103532.8518 | 6.805 | 115.24 | 107.61 | 127.62 | 714 | 1494 | 6.805 | 134.425 | 19.185 | 12.38
17128 | Poole Tatnam Road SPS | 225 | 10.1852 | 29.8206 | - | 29.8206 | 1039.5755 | 0.225 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 1056 | 0.028846 | 129416.0648 | 3.5496 | - | 2.39 | 6.74 | 344 | 1032 | 3.5496 | 10.2896 | - | -
15436 | Ruishton Barton Lane SPS | 100 | 10.162 | 5.8905 | 16 | 16 | 59.415 | 0.1 | 2.0434 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 1054 | 0.21282 | 156233.625 | 4.1512 | - | 7.43 | 10.28 | 4 | 46 | 4.1512 | 14.4312 | - | -
14423 | Blue Anchor Pill Bridge SPS | 250 | 10.1157 | 36.8155 | 18 | 18 | 2028.3125 | 0.25 | 0.36782 | Minehead Headworks STW | Minehead Headworks STW | 1049 | 0.0068954 | 70305.1313 | 1.5057 | 6.77 | 15.53 | 15.53 | 2028 | 2028 | 1.5057 | 17.0357 | 10.2657 | 8.76
15602 | Kewstoke Crooks Lane SPS | 150 | 10.1157 | 13.2536 | - | 13.2536 | 367.6013 | 0.15 | 0.7523 | Wick St Lawrence . STW | Kewstoke Sand Road SPS | 1049 | 0.028846 | 86277.3765 | 2.1147 | 5.7 | 7.89 | 7.89 | 368 | 368 | 2.1147 | 10.0047 | 4.3047 | 2.19
14041 | Sixpenny Handley . SPS | 100 | 9.9305 | 5.8905 | - | 5.8905 | 141.6644 | 0.1 | 0.7523 | Sixpenny Handley . STW | Sixpenny Handley . STW | 1030 | 0.028846 | 57518.251 | 1.383 | 73.95 | 82.54 | 82.54 | - | 136 | 1.383 | 83.923 | 9.973 | 8.59
15389 | Pawlett Main Road SPS | 125 | 9.6759 | 9.2039 | 19.2 | 19.2 | 1784.2529 | 0.125 | 1.5693 | West Huntspill STW | West Huntspill STW | 1004 | 0.12553 | 149984.28 | 55.2453 | 10.09 | 5.96 | 10.91 | - | 1784 | 55.2453 | 66.1553 | 56.0653 | 0.82
15419 | Brean Sunnyside Warren Farm SPS | 150 | 9.6528 | 13.2536 | - | 13.2536 | 367.0258 | 0.15 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Weston-Super-Mare Accommodation Road Bleadon STW | 1001 | 0.028846 | 86277.3765 | 2.1114 | 6.91 | 5.99 | 7.1 | 34 | 368 | 2.1114 | 9.2114 | 2.3014 | 0.19
15325 | Keinton Mandeville . SPS | 150 | 9.6065 | 13.2536 | 19.8 | 19.8 | 890.1625 | 0.15 | 1.1239 | Somerton Barpool Lane STW | Charlton Adam . SPS | 996 | 0.064379 | 128892.7407 | 11.2601 | - | 33.44 | 36.86 | 546 | 884 | 11.2601 | 48.1201 | - | -
10517 | Calne Abberd Lane SPS | 170 | 9.5139 | 17.0235 | - | 17.0235 | 840.4584 | 0.17 | 0.7523 | Compton Bassett . STW | Compton Bassett . STW | 987 | 0.028846 | 97781.0267 | 4.1128 | 72.38 | 96.99 | 97.42 | - | 806 | 4.1128 | 101.5328 | 29.1528 | 25.04
14115 | Frome Leonards Mill SPS | 170 | 9.5139 | 17.0235 | - | 17.0235 | 458.1954 | 0.17 | 0.7523 | Frome Welshmill Lane STW | Frome Welshmill Lane STW | 987 | 0.028846 | 97781.0267 | 2.2422 | 62.03 | 69.26 | 69.28 | 442 | 458 | 2.2422 | 71.5222 | 9.4922 | 7.25
15149 | Hawkesbury Upton Britain Bottom SPS | 150 | 9.4676 | 13.2536 | - | 13.2536 | 1615.727 | 0.15 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 982 | 0.028846 | 86277.3765 | 9.2948 | 161.16 | 193.82 | 193.82 | - | 1608 | 9.2948 | 203.1148 | 41.9548 | 32.66
15412 | East Huntspill Withy Road SPS | 168 | 9.3981 | 16.6253 | - | 16.6253 | 1657.5895 | 0.168 | 0.7523 | West Huntspill STW | West Huntspill STW | 975 | 0.028846 | 96630.6617 | 8.2362 | 5.35 | 4.77 | 5.66 | 1248 | 1656 | 8.2362 | 13.8962 | 8.5462 | 0.31
14124 | Stourpaine . SPS | 125 | 9.375 | 9.2039 | - | 9.2039 | 439.6135 | 0.125 | 0.7523 | Stourpaine . STW | Stourpaine . STW | 972 | 0.028846 | 71897.8138 | 3.2049 | 37.01 | 41.42 | 41.53 | 432 | 438 | 3.2049 | 44.7349 | 7.7249 | 4.52
15470 | Cerne Abbas Barn SPS | 127 | 9.3055 | 9.5008 | - | 9.5008 | 834.1347 | 0.127 | 0.7523 | Cerne Abbas A352 Dorchester Road STW | Cerne Abbas A352 Dorchester Road STW | 965 | 0.028846 | 73048.1788 | 5.9566 | 115.6 | 122.21 | 122.53 | - | 834 | 5.9566 | 128.4866 | 12.8866 | 6.93
15313 | Huish Episcopi Pibsbury SPS | 70 | 9.2361 | 2.8863 | 1.4 | 1.4 | 7.3588 | 0.07 | 0.3649 | Langport Portfield Lane STW | Langport Westover SPS | 958 | 0.0067864 | 19529.2031 | 0.028306 | 8.61 | 8.49 | 8.62 | 2 | 4 | 0.028306 | 8.6483 | 0.038306 | 0.01
14593 | Devizes Matilda Way (Sandcliffe Fm) SPS | 150 | 9.2129 | 13.2536 | - | 13.2536 | 388.2062 | 0.15 | 0.7523 | Potterne . STW | Potterne . STW | 956 | 0.028846 | 86277.3765 | 2.2332 | 133.74 | 148.07 | 148.07 | - | 388 | 2.2332 | 150.3032 | 16.5632 | 14.33
19080 | Pensford Pensford Bridge SPS | 100 | 9.1898 | 5.8905 | - | 5.8905 | 2086.6482 | 0.1 | 0.7523 | Stanton Drew . STW | Stanton Drew . STW | 953 | 0.028846 | 57518.251 | 20.3714 | 32.17 | 37.91 | 42.61 | 628 | 2086 | 20.3714 | 62.9814 | 30.8114 | 10.44
15454 | Creech St Michael North End SPS | 200 | 9.1666 | 23.5619 | 26 | 26 | 1683.6926 | 0.2 | 0.83014 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 951 | 0.035124 | 126939.8203 | 8.1071 | 13.75 | 8.35 | 16.59 | - | 1686 | 8.1071 | 24.6971 | 10.9471 | 2.84
14188 | Lower Stanton St Quintin . SPS | 225 | 9.1435 | 29.8206 | 27.7 | 27.7 | 4637.0776 | 0.225 | 0.6988 | Sutton Benger . STW | Sutton Benger . STW | 948 | 0.024889 | 120213.0948 | 13.7053 | 80.32 | 49.17 | 96.61 | 678 | 4558 | 13.7053 | 110.3153 | 29.9953 | 16.29
15504 | Dorchester Mellstock Avenue SPS | 100 | 9.1435 | 5.8905 | - | 5.8905 | 225.595 | 0.1 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 948 | 0.028846 | 57518.251 | 2.2024 | 55.49 | 62.24 | 62.24 | 226 | 226 | 2.2024 | 64.4424 | 8.9524 | 6.75
15704 | Bottlesford . SPS | 100 | 9.1204 | 5.8905 | - | 5.8905 | 2901.3244 | 0.1 | 0.7523 | Pewsey Salisbury Road STW | Pewsey Salisbury Road STW | 946 | 0.028846 | 57518.251 | 28.3248 | 109.19 | 100.96 | 116.45 | - | 2902 | 28.3248 | 144.7748 | 35.5848 | 7.26
14466 | Semington Semington Brook SPS | 180 | 9.0741 | 19.0852 | 18 | 18 | 2013.0434 | 0.18 | 0.70952 | Bowerhill Shails Lane STW | Bowerhill Shails Lane STW | 941 | 0.025659 | 97646.0157 | 8.1612 | 34.31 | 38.54 | 42.16 | 898 | 2014 | 8.1612 | 50.3212 | 16.0112 | 7.85
14067 | Bitton . SPS | 220 | 9.0509 | 28.51 | 14.85 | 14.85 | 1288.4656 | 0.22 | 0.39185 | Avonmouth Kingsweston Lane STW | Kingswood Willsbridge SPS | 939 | 0.007826 | 65911.0606 | 1.2727 | 13.26 | 25.2 | 25.28 | 1208 | 1288 | 1.2727 | 26.5527 | 13.2927 | 12.02
15180 | Pilning Redwick Road SPS | 150 | 9.0046 | 13.2536 | - | 13.2536 | 279.6993 | 0.15 | 0.7523 | Redwick . STW | Pilning Pill Head SPS | 934 | 0.028846 | 86277.3765 | 1.609 | 6.47 | 6.54 | 6.93 | 134 | 280 | 1.609 | 8.539 | 2.069 | 0.46
15002 | Boscombe No 1 SPS | 200 | 9.0046 | 23.5619 | 45 | 45 | 372.6661 | 0.2 | 1.4368 | Holdenhurst Riverside Avenue STW | Holdenhurst Riverside Avenue STW | 934 | 0.10522 | 219703.5352 | 5.2817 | - | 28.7 | 28.73 | - | 362 | 5.2817 | 34.0117 | - | -
14568 | Colerne Southwood Doe Housing Estate SPS | 150 | 8.9815 | 13.2536 | - | 13.2536 | 1343.9173 | 0.15 | 0.7523 | Colerne . STW | Colerne . STW | 932 | 0.028846 | 86277.3765 | 7.7312 | 145.34 | 165.79 | 166.17 | 1280 | 1344 | 7.7312 | 173.9012 | 28.5612 | 20.83
14330 | Little Langford . SPS | 150 | 8.9815 | 13.2536 | - | 13.2536 | 5445.7481 | 0.15 | 0.7523 | Wishford Wilton Road STW | Stoford . SPS | 932 | 0.028846 | 86277.3765 | 31.3278 | 65.51 | 61.52 | 65.53 | 32 | 5446 | 31.3278 | 96.8578 | 31.3478 | 0.02
15589 | Portishead Poacher Hotel (Anchor Hotel) SPS | 150 | 8.8889 | 13.2536 | - | 13.2536 | 33.1834 | 0.15 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 922 | 0.028846 | 86277.3765 | 0.19089 | 6.73 | 6.64 | 6.81 | 8 | 34 | 0.19089 | 7.0009 | 0.27089 | 0.08
19861 | Burnham-On-Sea Wallace Wells Road SPS | 100 | 8.8657 | 5.8905 | - | 5.8905 | 245.7866 | 0.1 | 0.7523 | West Huntspill STW | Highbridge Paddock Drive SPS | 920 | 0.028846 | 57518.251 | 2.3995 | 5.66 | 5.19 | 5.73 | 52 | 246 | 2.3995 | 8.1295 | 2.4695 | 0.07
14315 | Amesbury Gleesons Estate SPS | 150 | 8.8426 | 13.2536 | - | 13.2536 | 667.4108 | 0.15 | 0.7523 | Ratfyn . STW | Amesbury Ratfyn Lane SPS | 917 | 0.028846 | 86277.3765 | 3.8394 | 95.8 | 107.96 | 110.93 | 454 | 668 | 3.8394 | 114.7694 | 18.9694 | 15.13
15196 | Sturminster Newton The Bridge SPS | 150 | 8.8426 | 13.2536 | 13.7 | 13.7 | 296.5535 | 0.15 | 0.77764 | Sturminster Newton Opp Rixon Close STW | Sturminster Newton Opp Rixon Close STW | 917 | 0.030821 | 89183.361 | 1.8203 | 47.35 | 53.15 | 53.26 | 290 | 296 | 1.8203 | 55.0803 | 7.7303 | 5.91
14184 | Royal Wootton Bassett Green Park SPS | 125 | 8.7963 | 9.2039 | - | 9.2039 | 402.5481 | 0.125 | 0.7523 | Royal Wootton Bassett . STW | Royal Wootton Bassett . STW | 912 | 0.028846 | 71897.8138 | 2.9347 | 124.97 | 132 | 132.05 | 398 | 400 | 2.9347 | 134.9847 | 10.0147 | 7.08
15700 | Bridgwater Dawes Park No 3 SPS | 100 | 8.7963 | 5.8905 | - | 5.8905 | 297.9036 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Taunton Road SPS | 912 | 0.028846 | 57518.251 | 2.9083 | 6.23 | 7.21 | 7.21 | 298 | 298 | 2.9083 | 10.1183 | 3.8883 | 0.98
14299 | North Cheriton Grove Lane SPS | 150 | 8.7731 | 13.2536 | - | 13.2536 | 1659.9975 | 0.15 | 0.7523 | Wincanton . STW | Wincanton . STW | 910 | 0.028846 | 86277.3765 | 9.5495 | 69.96 | 69.13 | 74.88 | 412 | 1660 | 9.5495 | 84.4295 | 14.4695 | 4.92
14142 | Minety Station Road SPS | 180 | 8.75 | 19.0852 | 6.5 | 6.5 | 2810.9619 | 0.18 | 0.25622 | Malmesbury . STW | Upper Minety Flisteridge SPS | 908 | 0.0033459 | 35261.0612 | 1.5893 | 88.95 | 99.53 | 107.13 | 1890 | 2810 | 1.5893 | 108.7193 | 19.7693 | 18.18
15136 | Patchway Sycamore Drive SPS | 125 | 8.7037 | 9.2039 | - | 9.2039 | 407.6317 | 0.125 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Kingsweston Lane STW | 903 | 0.028846 | 71897.8138 | 2.9718 | 79.55 | 81.42 | 81.42 | - | 408 | 2.9718 | 84.3918 | 4.8418 | 1.87
14328 | Hanging Langford . SPS | 125 | 8.7037 | 9.2039 | 12 | 12 | 1590.9928 | 0.125 | 0.98084 | Wishford Wilton Road STW | Little Langford . SPS | 903 | 0.049034 | 93740.175 | 19.5117 | 66.76 | 65.39 | 70.43 | 776 | 1590 | 19.5117 | 89.9417 | 23.1817 | 3.67
17473 | Portishead Sandeling Place SPS | 150 | 8.7037 | 13.2536 | - | 13.2536 | 209.7216 | 0.15 | 0.7523 | Portbury Wharf The Drove Portbury STW | Studland Watery Lane SPS | 903 | 0.028846 | 86277.3765 | 1.2065 | - | - | - | - | - | 1.2065 | - | - | -
14429 | Chew Stoke Bilbie Road SPS | 150 | 8.6574 | 13.2536 | 12.3 | 12.3 | 996.5722 | 0.15 | 0.69817 | Chew Stoke Walley Court Road STW | Chew Stoke Walley Court Road STW | 898 | 0.024844 | 80069.7328 | 4.9541 | 50.31 | 44.72 | 50.98 | 104 | 994 | 4.9541 | 55.9341 | 5.6241 | 0.67
14096 | Coxley Mill Lane SPS | 150 | 8.6574 | 13.2536 | 10.8 | 10.8 | 1540.2095 | 0.15 | 0.61303 | Wells . STW | Wells . STW | 898 | 0.019154 | 70305.1313 | 5.94 | 13.4 | 25.46 | 25.46 | 1526 | 1526 | 5.94 | 31.4 | 18 | 12.06
17124 | Higher Woodsford Park Drive SPS | 200 | 8.6342 | 23.5619 | - | 23.5619 | 1231.1404 | 0.2 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 896 | 0.028846 | 115036.502 | 4.8881 | 50.46 | 59.91 | 62.22 | 940 | 1232 | 4.8881 | 67.1081 | 16.6481 | 11.76
15282 | Bradford Abbas Mill Lane SPS | 170 | 8.5416 | 17.0235 | 14.3 | 14.3 | 2033.8662 | 0.17 | 0.63194 | Yeovil Sherborne Road (Pen Mill) STW | Stoford Hillside Main SPS | 886 | 0.020354 | 82137.5308 | 7.0793 | 36.07 | 38.54 | 51.26 | - | 2034 | 7.0793 | 58.3393 | 22.2693 | 15.19
17569 | Throop . SPS | 110 | 8.4954 | 7.1275 | - | 7.1275 | 725.7591 | 0.11 | 0.7523 | Blackheath . STW | Bere Regis Court Farm Southbrook SPS | 881 | 0.028846 | 63270.0761 | 6.2527 | 32.71 | 34.88 | 36.69 | 712 | 726 | 6.2527 | 42.9427 | 10.2327 | 3.98
14051 | Upavon Andover Road SPS | 100 | 8.4491 | 5.8905 | - | 5.8905 | 752.0177 | 0.1 | 0.7523 | Upavon . STW | Upavon . STW | 876 | 0.028846 | 57518.251 | 7.3417 | 91.82 | 97.49 | 97.49 | 752 | 752 | 7.3417 | 104.8317 | 13.0117 | 5.67
14176 | Kington Langley . SPS | 150 | 8.3796 | 13.2536 | 7 | 7 | 332.9745 | 0.15 | 0.39733 | Sutton Benger . STW | Sutton Benger . STW | 869 | 0.0080465 | 45568.1406 | 0.55353 | 83.27 | 101.03 | 101.03 | - | 328 | 0.55353 | 101.5835 | 18.3135 | 17.76
14285 | Misterton . SPS | 150 | 8.3796 | 13.2536 | 19.8 | 19.8 | 543.8187 | 0.15 | 1.1239 | Crewkerne Trading Estate Crewkerne East STW | Crewkerne Trading Estate Crewkerne East STW | 869 | 0.064379 | 128892.7407 | 6.879 | 55.4 | 60.22 | 60.29 | 528 | 530 | 6.879 | 67.169 | 11.769 | 4.89
14222 | East Knighton Blacknoll SPS | 160 | 8.3565 | 15.0796 | 11 | 11 | 3422.8857 | 0.16 | 0.54877 | Wool . STW | Wool . STW | 867 | 0.015349 | 67131.6358 | 9.7873 | - | 24.1 | 48.98 | 1012 | 3408 | 9.7873 | 58.7673 | - | -
15592 | Portishead North Weston SPS | 150 | 8.2639 | 13.2536 | - | 13.2536 | 581.6309 | 0.15 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 857 | 0.028846 | 86277.3765 | 3.346 | 6.07 | 6.65 | 8.47 | - | 582 | 3.346 | 11.816 | 5.746 | 2.4
15385 | Brean Merry Bee South Road SPS | 280 | 8.2639 | 46.1814 | - | 46.1814 | 2985.4312 | 0.28 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Brean Sunnyside Warren Farm SPS | 857 | 0.028846 | 161051.1028 | 7.7148 | - | 6.37 | 8.47 | 2560 | 2824 | 7.7148 | 16.1848 | - | -
15331 | Shepton Beauchamp . SPS | 150 | 8.2176 | 13.2536 | 12 | 12 | 1274.2048 | 0.15 | 0.68114 | South Petherton North Street STW | South Petherton North Street STW | 852 | 0.023647 | 78116.8125 | 6.0359 | 40.44 | 51.63 | 52.24 | - | 1276 | 6.0359 | 58.2759 | 17.8359 | 11.8
14272 | Briantspuddle . SPS | 125 | 8.1713 | 9.2039 | 6 | 6 | 2733.7026 | 0.125 | 0.49042 | Blackheath . STW | Throop . SPS | 848 | 0.012259 | 46870.0875 | 8.6582 | 35.02 | 74.51 | 81.04 | 2348 | 2502 | 8.6582 | 89.6982 | 54.6782 | 46.02
19829 | St Georges Willow Close SPS | 200 | 8.1481 | 23.5619 | - | 23.5619 | 463.4088 | 0.2 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 845 | 0.028846 | 115036.502 | 1.8399 | 5.88 | 5.24 | 6.02 | 102 | 464 | 1.8399 | 7.8599 | 1.9799 | 0.14
15689 | Hilcott Pumping Station No 3 SPS | 100 | 8.125 | 5.8905 | - | 5.8905 | 474.1068 | 0.1 | 0.7523 | Pewsey Salisbury Road STW | Bottlesford . SPS | 843 | 0.028846 | 57518.251 | 4.6286 | 108.19 | 112.14 | 112.48 | 456 | 474 | 4.6286 | 117.1086 | 8.9186 | 4.29
19823 | Longham Bridge House SPS | 180 | 8.0324 | 19.0852 | - | 19.0852 | 1099.8658 | 0.18 | 0.7523 | Kinson New Road Northbourne STW | Kinson New Road Northbourne STW | 833 | 0.028846 | 103532.8518 | 5.0001 | 11.19 | 12.56 | 12.59 | 1008 | 1012 | 5.0001 | 17.5901 | 6.4001 | 1.4
15812 | Melksham Bowerhill Lane Bowerhill SPS | 100 | 7.9861 | 5.8905 | - | 5.8905 | 545.1529 | 0.1 | 0.7523 | Bowerhill Shails Lane STW | Bowerhill Shails Lane STW | 828 | 0.028846 | 57518.251 | 5.3222 | 45.06 | 53.63 | 53.63 | 546 | 546 | 5.3222 | 58.9522 | 13.8922 | 8.57
15371 | Cross Cross East SPS | 100 | 7.9398 | 5.8905 | 5.5 | 5.5 | 546.3248 | 0.1 | 0.70243 | Cheddar . STW | Axbridge Old Stw Site SPS | 824 | 0.025148 | 53705.3086 | 4.6644 | 6.73 | 20.16 | 20.16 | 546 | 546 | 4.6644 | 24.8244 | 18.0944 | 13.43
15173 | Almondsbury Hortham Lane SPS | 220 | 7.9167 | 28.51 | - | 28.51 | 891.8448 | 0.22 | 0.7523 | Almondsbury . STW | Almondsbury . STW | 821 | 0.028846 | 126540.1522 | 3.134 | 59.88 | 84.2 | 84.2 | 888 | 888 | 3.134 | 87.334 | 27.454 | 24.32
14349 | Salisbury Stratford Sub Castle SPS | 150 | 7.9167 | 13.2536 | - | 13.2536 | 619.0934 | 0.15 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 821 | 0.028846 | 86277.3765 | 3.5615 | 49.71 | 53.99 | 53.99 | 620 | 620 | 3.5615 | 57.5515 | 7.8415 | 4.28
14475 | Broughton Gifford The Green SPS | 150 | 7.8935 | 13.2536 | 12.2 | 12.2 | 2970.2376 | 0.15 | 0.69249 | Melksham . STW | Melksham . STW | 819 | 0.024442 | 79418.7594 | 14.5318 | 35.47 | 37.05 | 42.07 | 840 | 2970 | 14.5318 | 56.6018 | 21.1318 | 6.6
14340 | Fovant Church Lane SPS | 160 | 7.8241 | 15.0796 | - | 15.0796 | 756.2379 | 0.16 | 0.7523 | Fovant . STW | Fovant . STW | 812 | 0.028846 | 129416.0648 | 2.5822 | - | 86.7 | 93.59 | 2 | 752 | 2.5822 | 96.1722 | - | -
15033 | Mudeford Mudeford Church SPS | 150 | 7.8009 | 13.2536 | - | 13.2536 | 13.839 | 0.15 | 0.7523 | Christchurch Stoney Lane STW | Mudeford Mudeford Gardens SPS | 809 | 0.028846 | 86277.3765 | 0.079611 | 3.13 | 2.99 | 3.13 | 0 | 6 | 0.079611 | 3.2096 | 0.079611 | 0
15352 | East Brent Orchard Close SPS | 200 | 7.7315 | 23.5619 | - | 23.5619 | 652.6024 | 0.2 | 0.7523 | West Huntspill STW | East Brent Chestnut Farm SPS | 802 | 0.028846 | 115036.502 | 2.5911 | 5.97 | 6.38 | 6.38 | 652 | 652 | 2.5911 | 8.9711 | 3.0011 | 0.41
15153 | Patchway Brighton Road SPS | 125 | 7.6852 | 9.2039 | - | 9.2039 | 342.1925 | 0.125 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Kingsweston Lane STW | 797 | 0.028846 | 71897.8138 | 2.4947 | 77.73 | 81.08 | 81.13 | - | 342 | 2.4947 | 83.6247 | 5.8947 | 3.4
14293 | Queen Camel Englands Mead Green Lane SPS | 125 | 7.6389 | 9.2039 | 9.3 | 9.3 | 1313.3825 | 0.125 | 0.76015 | Sparkford Off Sparkford Hill Lane STW | Sparkford Off Sparkford Hill Lane STW | 792 | 0.029451 | 72648.6356 | 9.7716 | 29.91 | 34.49 | 35.75 | 1198 | 1314 | 9.7716 | 45.5216 | 15.6116 | 5.84
19035 | Kingsbury Episcopi . SPS | 130 | 7.6389 | 9.9549 | 14 | 14 | 2970.0438 | 0.13 | 1.058 | Martock Hurst Bow STW | Martock Hurst Bow STW | 792 | 0.057051 | 105157.2476 | 40.1647 | 9.67 | 13.67 | 15.14 | 254 | 2970 | 40.1647 | 55.3047 | 45.6347 | 5.47
15805 | Bridgwater Showground No1 SPS | 280 | 7.6157 | 46.1814 | - | 46.1814 | 1078.4622 | 0.28 | 0.7523 | Chilton Trinity . STW | Bridgwater Taunton Road SPS | 790 | 0.028846 | 161051.1028 | 2.7869 | - | 7.3 | 8.56 | 934 | 1014 | 2.7869 | 11.3469 | - | -
15301 | Odcombe No 1 SPS | 150 | 7.5463 | 13.2536 | - | 13.2536 | 1226.4119 | 0.15 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Sherborne Road (Pen Mill) STW | 783 | 0.028846 | 86277.3765 | 7.0552 | 77.11 | 69.69 | 84.41 | - | 1492 | 7.0552 | 91.4652 | 14.3552 | 7.3
15467 | Nailsbourne . SPS | 200 | 7.5 | 23.5619 | 16 | 16 | 589.3288 | 0.2 | 0.51086 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 778 | 0.013301 | 78116.8125 | 1.0998 | 42.03 | 54.99 | 56.38 | - | 590 | 1.0998 | 57.4798 | 15.4498 | 14.35
14260 | Lytchett Matravers Glebe Road SPS | 160 | 7.5 | 15.0796 | 7 | 7 | 252.6111 | 0.16 | 0.34922 | Blackheath . STW | Lytchett Matravers Bulbury Lane SPS | 778 | 0.0062158 | 42720.1318 | 0.30114 | 35.16 | 47.52 | 47.52 | - | 248 | 0.30114 | 47.8211 | 12.6611 | 12.36
14157 | Calne Rough Leaze SPS | 225 | 7.4768 | 29.8206 | 20 | 20 | 3258.8408 | 0.225 | 0.50455 | Calne . STW | Calne . STW | 776 | 0.012975 | 86796.4584 | 5.1046 | 90.13 | 104.67 | 105.12 | 3238 | 3248 | 5.1046 | 110.2246 | 20.0946 | 14.99
14508 | Shirehampton Cerney Lane SPS | 225 | 7.4768 | 29.8206 | - | 29.8206 | 235.5512 | 0.225 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 776 | 0.028846 | 129416.0648 | 0.80428 | 12.85 | 18.91 | 18.91 | 240 | 240 | 0.80428 | 19.7143 | 6.8643 | 6.06
14077 | Street Strode Road SPS | 150 | 7.4768 | 13.2536 | - | 13.2536 | 152.2122 | 0.15 | 0.7523 | Glastonbury The Beckery SSTW | Street Main SPS | 776 | 0.028846 | 86277.3765 | 0.87563 | 10.62 | 17.37 | 17.37 | 152 | 152 | 0.87563 | 18.2456 | 7.6256 | 6.75
15058 | Sturminster Marshall High Street SPS | 150 | 7.4537 | 13.2536 | - | 13.2536 | 347.4061 | 0.15 | 0.7523 | Tarrant Crawford . STW | Sturminster Marshall Newton Road SPS | 773 | 0.028846 | 86277.3765 | 1.9985 | 24.27 | 24.62 | 24.63 | 348 | 350 | 1.9985 | 26.6285 | 2.3585 | 0.36
15561 | Weymouth Ferrybridge Portland Road SPS | 300 | 7.4305 | 53.0144 | 20 | 20 | 555.6109 | 0.3 | 0.28381 | Weymouth . STW | Weymouth . STW | 771 | 0.0041054 | 65097.3438 | 0.19859 | 3.08 | 19.11 | 21.73 | - | 556 | 0.19859 | 21.9286 | 18.8486 | 18.65
14175 | Eastcourt Oatridge Farm SPS | 100 | 7.4074 | 5.8905 | - | 5.8905 | 1706.2368 | 0.1 | 0.7523 | Malmesbury . STW | Hankerton Hankerton Bridge SPS | 768 | 0.028846 | 57518.251 | 16.6575 | 90.23 | 93.24 | 95.33 | 720 | 1702 | 16.6575 | 111.9875 | 21.7575 | 5.1
15125 | Worton Mill Road SPS | 120 | 7.3842 | 8.4823 | 11 | 11 | 1249.541 | 0.12 | 0.97559 | Potterne . STW | Poulshot Townsend SPS | 766 | 0.048511 | 89508.8477 | 15.9923 | 50.76 | 53.66 | 55.27 | 1062 | 1250 | 15.9923 | 71.2623 | 20.5023 | 4.51
17047 | West Lulworth Barn SPS | 280 | 7.3611 | 46.1814 | - | 46.1814 | 8957.1643 | 0.28 | 0.7523 | Wool . STW | Wool . STW | 764 | 0.028846 | 161051.1028 | 23.1467 | - | 24.51 | 118.75 | 620 | 8944 | 23.1467 | 141.8967 | - | -
14383 | Combwich Brookside SPS | 200 | 7.2685 | 23.5619 | - | 23.5619 | 331.8384 | 0.2 | 0.7523 | Combwich Quay Road SPS | Combwich Quay Road SPS | 754 | 0.028846 | 115036.502 | 1.3175 | 6.59 | 8.1 | 8.1 | - | 334 | 1.3175 | 9.4175 | 2.8275 | 1.51
15402 | Middlezoy Nethermoor Road SPS | 225 | 7.2685 | 29.8206 | 11 | 11 | 5302.3034 | 0.225 | 0.2775 | Chilton Trinity . STW | Westonzoyland . SPS | 754 | 0.0039249 | 47738.0521 | 2.6205 | 5.97 | 5.05 | 13.49 | - | 5302 | 2.6205 | 16.1105 | 10.1405 | 7.52
13074 | Combwich Quay Road SPS | 125 | 7.2685 | 9.2039 | 4.9 | 4.9 | 520.5695 | 0.125 | 0.40051 | Combwich Quay Road SPS | - | 754 | 0.0081758 | 38277.2381 | 1.1141 | - | - | - | - | - | 1.1141 | - | - | -
17233 | Portishead Marina Lock Gate SPS | - | 7.2454 | - | - | - | 514.4149 | - | - | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 752 | - | - | - | 8.61 | 8.3 | 8.92 | - | 520 | - | - | - | 0.31
14213 | Crudwell The Ridgeway SPS | 180 | 7.1991 | 19.0852 | - | 19.0852 | 1979.2109 | 0.18 | 0.7523 | Malmesbury . STW | Hankerton Hankerton Bridge SPS | 747 | 0.028846 | 103532.8518 | 8.9976 | 95.68 | 93.25 | 96.6 | 36 | 1980 | 8.9976 | 105.5976 | 9.9176 | 0.92
15103 | Bromham Loop Hill SPS | 180 | 7.1991 | 19.0852 | - | 19.0852 | 900.4296 | 0.18 | 0.7523 | Rowde . STW | Rowde . STW | 747 | 0.028846 | 103532.8518 | 4.0934 | 67.25 | 102.28 | 103.22 | 684 | 888 | 4.0934 | 107.3134 | 40.0634 | 35.97
17046 | West Lulworth Lulstead SPS | 225 | 7.1759 | 29.8206 | - | 29.8206 | 310.4565 | 0.225 | 0.7523 | Wool . STW | West Lulworth Barn SPS | 744 | 0.028846 | 129416.0648 | 1.06 | 59.05 | 89.32 | 89.46 | 312 | 316 | 1.06 | 90.52 | 31.47 | 30.41
15718 | Bishops Hull Shutemead SPS | 100 | 7.1759 | 5.8905 | - | 5.8905 | 178.4302 | 0.1 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Mountway Bishops Hull SPS | 744 | 0.028846 | 57518.251 | 1.742 | 26.48 | 39.06 | 39.06 | 178 | 178 | 1.742 | 40.802 | 14.322 | 12.58
13337 | West Lulworth Hambury Farm SPS | 225 | 7.1528 | 29.8206 | 15.9 | 15.9 | 657.7457 | 0.225 | 0.40112 | Wool . STW | West Lulworth Lulstead SPS | 742 | 0.0082005 | 69003.1844 | 0.66046 | 21.18 | 59.04 | 59.07 | 652 | 656 | 0.66046 | 59.7305 | 38.5505 | 37.89
17553 | Christian Malford The Green Street SPS | 150 | 7.1065 | 13.2536 | - | 13.2536 | 1001.1557 | 0.15 | 0.7523 | Sutton Benger . STW | Sutton Benger . STW | 737 | 0.028846 | 86277.3765 | 5.7594 | 53.56 | 50.82 | 54.26 | 128 | 992 | 5.7594 | 60.0194 | 6.4594 | 0.7
15362 | Bridgwater Silver Springs Folletts Farm SPS | 100 | 7.0602 | 5.8905 | - | 5.8905 | 1042.7244 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Bower Manor 3a SPS | 732 | 0.028846 | 57518.251 | 10.1798 | 5.76 | 5.72 | 6.51 | 904 | 1042 | 10.1798 | 16.6898 | 10.9298 | 0.75
14643 | Lyneham Preston Lane Building 488 (Ps 11 And 12) SPS | 120 | 7.037 | 8.4823 | - | 8.4823 | 147.6561 | 0.12 | 0.7523 | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham B Site (Main Stw) Raf Lyneham STW | 730 | 0.028846 | 69021.9012 | 1.1353 | 116.28 | 120.52 | 120.52 | 144 | 144 | 1.1353 | 121.6553 | 5.3753 | 4.24
18718 | Chapmanslade Divers Bridge SPS | 150 | 6.8981 | 13.2536 | 5.2 | 5.2 | 3990.3972 | 0.15 | 0.29516 | Frome Welshmill Lane STW | Frome Welshmill Lane STW | 716 | 0.0044404 | 33850.6188 | 3.7449 | 89.14 | 70.44 | 89.55 | - | 3992 | 3.7449 | 93.2949 | 4.1549 | 0.41
14322 | Dinton Bratch Lane SPS | 150 | 6.8518 | 13.2536 | - | 13.2536 | 2505.8124 | 0.15 | 0.7523 | Fovant . STW | Fovant . STW | 711 | 0.028846 | 86277.3765 | 14.4152 | 71.53 | 86.64 | 87.26 | - | 2500 | 14.4152 | 101.6752 | 30.1452 | 15.73
14368 | Mere Edgebridge SPS | 150 | 6.8055 | 13.2536 | 11 | 11 | 103.6783 | 0.15 | 0.62438 | Mere Rook Street STW | Mere Rook Street STW | 706 | 0.01987 | 71607.0781 | 0.41441 | 95.41 | 97.48 | 97.48 | - | 104 | 0.41441 | 97.8944 | 2.4844 | 2.07
14084 | Glastonbury Actis SPS | 150 | 6.8055 | 13.2536 | 21.9 | 21.9 | 722.8911 | 0.15 | 1.2431 | Glastonbury The Beckery SSTW | Glastonbury Porchestall SPS | 706 | 0.078759 | 142563.1828 | 11.1527 | 8.78 | 27.45 | 27.78 | 706 | 724 | 11.1527 | 38.9327 | 30.1527 | 19
15162 | Alveston Alveston Down SPS | 150 | 6.7824 | 13.2536 | - | 13.2536 | 535.6264 | 0.15 | 0.7523 | Thornbury . STW | Thornbury . STW | 704 | 0.028846 | 86277.3765 | 3.0813 | 93.34 | 96.32 | 97.07 | - | 536 | 3.0813 | 100.1513 | 6.8113 | 3.73
14288 | Marston Magna Church Lane SPS | 100 | 6.7361 | 5.8905 | 4 | 4 | 2506.4017 | 0.1 | 0.51086 | Chilton Cantelo Hornsey Bridge STW | Chilton Cantelo Hornsey Bridge STW | 699 | 0.013301 | 39058.4063 | 11.5102 | 27.67 | 22.42 | 28.25 | 400 | 2500 | 11.5102 | 39.7602 | 12.0902 | 0.58
15507 | Bridport West Bay Sluices SPS | 100 | 6.6898 | 5.8905 | 9.3 | 9.3 | 52.4104 | 0.1 | 1.1877 | Bridport Wych Farm STW | Bridport West Bay SPS | 694 | 0.071902 | 90810.7946 | 1.254 | - | 2.69 | 2.96 | 16 | 30 | 1.254 | 4.214 | - | -
14428 | Corston Newton St Loe SPS | 100 | 6.6667 | 5.8905 | 23.5 | 23.5 | 261.4818 | 0.1 | 3.0013 | Saltford Mead Lane STW | Saltford Mead Lane STW | 692 | 0.45911 | 229468.1368 | 39.1568 | 19.09 | 14.48 | 20.62 | 50 | 262 | 39.1568 | 59.7768 | 40.6868 | 1.53
17120 | Blandford Wyvern Way SPS | 100 | 6.6435 | 5.8905 | - | 5.8905 | 61.8166 | 0.1 | 0.7523 | Tarrant Crawford . STW | Blandford Langton Road (Blandford No 1) SPS | 689 | 0.028846 | 57518.251 | 0.6035 | 80.27 | 80.05 | 80.31 | 2 | 60 | 0.6035 | 80.9135 | 0.6435 | 0.04
14455 | North Bradley The Rank SPS | 150 | 6.6435 | 13.2536 | - | 13.2536 | 479.7352 | 0.15 | 0.7523 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 689 | 0.028846 | 86277.3765 | 2.7598 | 42.77 | 47.38 | 47.38 | 480 | 480 | 2.7598 | 50.1398 | 7.3698 | 4.61
15593 | Tickenham East SPS | 150 | 6.5509 | 13.2536 | - | 13.2536 | 679.4734 | 0.15 | 0.7523 | Kingston Seymour Back Lane STW | Kenn Kenn Pier SPS | 680 | 0.028846 | 86277.3765 | 3.9088 | 10.99 | 29.89 | 29.89 | 678 | 678 | 3.9088 | 33.7988 | 22.8088 | 18.9
15207 | Shaftesbury Long Cross SPS | 125 | 6.5278 | 9.2039 | 15 | 15 | 1827.5208 | 0.125 | 1.2261 | Shaftesbury Gears Mill STW | Shaftesbury Gears Mill STW | 677 | 0.076616 | 117175.2188 | 34.7665 | 117.14 | 139.67 | 139.67 | - | 1826 | 34.7665 | 174.4365 | 57.2965 | 22.53
15277 | Poole Wood Lane SPS | 150 | 6.5046 | 13.2536 | 14.5 | 14.5 | 355.9844 | 0.15 | 0.82305 | Poole Cabot Lane STW | Poole Magna Road SPS | 675 | 0.034526 | 94391.1485 | 2.442 | 15.03 | 25.38 | 25.38 | 354 | 354 | 2.442 | 27.822 | 12.792 | 10.35
13153 | Holton Heath Holton Heath Sewage Pumping Station SPS | 225 | 6.4815 | 29.8206 | 20 | 20 | 2590.8877 | 0.225 | 0.50455 | Wareham Keysworth Drive STW | - | 672 | 0.012975 | 86796.4584 | 4.0583 | 3.48 | 4.06 | 5.47 | 1904 | 2590 | 4.0583 | 9.5283 | 6.0483 | 1.99
14460 | North Bradley Yarnbrook SPS | 180 | 6.4583 | 19.0852 | - | 19.0852 | 915.4546 | 0.18 | 0.7523 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 670 | 0.028846 | 103532.8518 | 4.1617 | 41.15 | 50.43 | 50.77 | 912 | 916 | 4.1617 | 54.9317 | 13.7817 | 9.62
14042 | Cranborne Alderholt Rd Higher Holwell SPS | 160 | 6.4352 | 15.0796 | - | 15.0796 | 423.4912 | 0.16 | 0.7523 | Cranborne Higher Holwell STW | Cranborne Higher Holwell STW | 668 | 0.028846 | 92029.2016 | 2.2411 | - | 53.05 | 57.27 | - | 216 | 2.2411 | 59.5111 | - | -
14055 | Marden High Street SPS | 120 | 6.412 | 8.4823 | 8 | 8 | 553.4552 | 0.12 | 0.70952 | Marden . STW | Marden . STW | 665 | 0.025659 | 65097.3438 | 3.7953 | 104.81 | 105.06 | 108.17 | 310 | 558 | 3.7953 | 111.9653 | 7.1553 | 3.36
14178 | Great Somerford Frog Lane SPS | 225 | 6.3889 | 29.8206 | - | 29.8206 | 566.4066 | 0.225 | 0.7523 | Great Somerford . STW | Great Somerford . STW | 663 | 0.028846 | 129416.0648 | 1.934 | 60.23 | 61.35 | 62.25 | 552 | 560 | 1.934 | 64.184 | 3.954 | 2.02
15197 | Blandford Brewery No 2 SPS | - | 6.3889 | - | - | - | 0 | - | - | Tarrant Crawford . STW | Spetisbury No 3 SPS | 663 | - | - | - | 32.04 | 39.89 | 40.04 | - | 550 | - | - | - | 8
15205 | Blandford St Mary Bournemouth Road SPS | 100 | 6.3657 | 5.8905 | 12 | 12 | 127.5586 | 0.1 | 1.5326 | Tarrant Crawford . STW | Blandford Brewery No 2 SPS | 660 | 0.11971 | 117175.2188 | 5.0454 | 32.9 | 32.04 | 33.57 | 146 | 204 | 5.0454 | 38.6154 | 5.7154 | 0.67
15303 | Huish Episcopi Peony Valley SPS | 150 | 6.3657 | 13.2536 | - | 13.2536 | 591.4012 | 0.15 | 0.7523 | Langport Portfield Lane STW | Langport Westover SPS | 660 | 0.028846 | 86277.3765 | 3.4022 | 17.77 | 16.73 | 22.68 | 196 | 592 | 3.4022 | 26.0822 | 8.3122 | 4.91
14351 | Tisbury Union Road SPS | 100 | 6.3426 | 5.8905 | - | 5.8905 | 99.7777 | 0.1 | 0.7523 | Tisbury Higher Chicksgrove STW | Tisbury Higher Chicksgrove STW | 658 | 0.028846 | 57518.251 | 0.9741 | 91.8 | 93.56 | 93.56 | 98 | 98 | 0.9741 | 94.5341 | 2.7341 | 1.76
15278 | Long Sutton Bennetts Orchard SPS | 180 | 6.2731 | 19.0852 | 7.8 | 7.8 | 1070.9082 | 0.18 | 0.30746 | Langport Portfield Lane STW | Huish Episcopi Pibsbury SPS | 651 | 0.0048181 | 42313.2734 | 0.85832 | 12.8 | 14.65 | 16.15 | - | 1044 | 0.85832 | 17.0083 | 4.2083 | 3.35
15388 | Othery Rye Lane/ Summerhedge Road SPS | 225 | 6.2731 | 29.8206 | 13.5 | 13.5 | 1980.2352 | 0.225 | 0.34057 | Chilton Trinity . STW | Westonzoyland . SPS | 651 | 0.0059117 | 58587.6094 | 1.4501 | 5.9 | 8.44 | 12.93 | - | 1980 | 1.4501 | 14.3801 | 8.4801 | 7.03
15659 | Bridgwater Wills Road SPS | 100 | 6.25 | 5.8905 | - | 5.8905 | 115.3451 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Taunton Road SPS | 648 | 0.028846 | 57518.251 | 1.1261 | 5.92 | 7.26 | 7.26 | 114 | 114 | 1.1261 | 8.3861 | 2.4661 | 1.34
15167 | Cromhall Jubilee Lane SPS | 100 | 6.2268 | 5.8905 | 12 | 12 | 946.6194 | 0.1 | 1.5326 | Cromhall . STW | Cromhall . STW | 646 | 0.11971 | 117175.2188 | 37.4419 | 53.67 | 56.75 | 57.04 | 926 | 946 | 37.4419 | 94.4819 | 40.8119 | 3.37
14057 | Great Cheverell Cheverell Green SPS | 150 | 6.2037 | 13.2536 | 6 | 6 | 1720.5198 | 0.15 | 0.34057 | Lavington Woodbridge STW | Lavington Woodbridge STW | 644 | 0.0059117 | 39058.4063 | 2.1251 | 62.26 | 64.98 | 66.81 | 644 | 1720 | 2.1251 | 68.9351 | 6.6751 | 4.55
14555 | Isle Abbotts Two Bridges SPS | 100 | 6.2037 | 6 | - | 17.0235 | 1953.7497 | 0.17 | 0.7523 | Fivehead . STW | Fivehead . STW | 644 | 0.028846 | 97781.0267 | 9.5607 | 16.14 | 19.88 | 20.73 | 1908 | 1922 | 9.5607 | 30.2907 | 14.1507 | 4.59
15461 | Stoke St Gregory Woodhill SPS | 150 | 6.2037 | 13.2536 | 16 | 16 | 1578.3323 | 0.15 | 0.90819 | Stoke St Gregory . STW | Stoke St Gregory . STW | 644 | 0.042039 | 104155.75 | 13.1328 | 6.91 | 30.09 | 30.16 | 1568 | 1578 | 13.1328 | 43.2928 | 36.3828 | 23.25
15421 | Stone Old Mill SPS | 120 | 6.1805 | 8.4823 | - | 8.4823 | 709.2788 | 0.12 | 0.7523 | Michaelwood . STW | Michaelwood . STW | 641 | 0.028846 | 69021.9012 | 5.4536 | 13.44 | 27.1 | 27.1 | - | 710 | 5.4536 | 32.5536 | 19.1136 | 13.66
15183 | Bagstone . SPS | 120 | 6.088 | 8.4823 | - | 8.4823 | 904.2908 | 0.12 | 0.7523 | Cromhall . STW | Tytherington Stidcott SPS | 632 | 0.028846 | 69021.9012 | 6.9531 | 51.7 | 51.56 | 51.82 | 346 | 904 | 6.9531 | 58.7731 | 7.0731 | 0.12
15369 | Burnham-On-Sea Pillsmouth Marine Drive SPS | 600 | 6.088 | 212.0575 | - | 212.0575 | 72.2285 | 0.6 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 632 | 0.028846 | 345109.5061 | 0.07162 | 5.7 | 5.79 | 5.85 | 62 | 72 | 0.07162 | 5.9216 | 0.22162 | 0.15
15252 | Poole Egmont Road SPS | 100 | 6.088 | 5.8905 | 10.6 | 10.6 | 333.9261 | 0.1 | 1.3538 | Poole Cabot Lane STW | Poole Turlin Main Blandford Road Turlin Moor SPS | 632 | 0.093409 | 103504.7766 | 10.3395 | 1.97 | 2.91 | 3.01 | 312 | 334 | 10.3395 | 13.3495 | 11.3795 | 1.04
15077 | Wimborne The Boatyard SPS | 100 | 6.0648 | 5.8905 | - | 5.8905 | 156.523 | 0.1 | 0.7523 | Wimborne Brook Road STW | Wimborne Brook Road STW | 629 | 0.028846 | 57518.251 | 1.5281 | 17.58 | 19.83 | 19.91 | 154 | 156 | 1.5281 | 21.4381 | 3.8581 | 2.33
15660 | Woodborough Ps1 . SPS | 100 | 5.9722 | 5.8905 | - | 5.8905 | 915.6073 | 0.1 | 0.7523 | Pewsey Salisbury Road STW | Hilcott Pumping Station No 3 SPS | 620 | 0.028846 | 57518.251 | 8.9388 | 111.62 | 116.84 | 120.3 | 646 | 910 | 8.9388 | 129.2388 | 17.6188 | 8.68
19824 | Longham Green Lane SPS | 180 | 5.9491 | 19.0852 | - | 19.0852 | 130.7517 | 0.18 | 0.7523 | Kinson New Road Northbourne STW | Longham Bridge House SPS | 617 | 0.028846 | 103532.8518 | 0.5944 | 12.26 | 12.94 | 13.01 | - | 130 | 0.5944 | 13.6044 | 1.3444 | 0.75
15304 | West Chinnock Garage SPS | 150 | 5.9259 | 13.2536 | 8.8 | 8.8 | 1011.4508 | 0.15 | 0.4995 | South Petherton North Street STW | Norton Sub Hamdon . SPS | 615 | 0.012717 | 57285.6625 | 2.6188 | - | 38.3 | 62.06 | - | 992 | 2.6188 | 64.6788 | - | -
15327 | Ilminster Lord Nelson SPS | 150 | 5.9028 | 13.2536 | 20 | 20 | 431.9296 | 0.15 | 1.1352 | Ilminster Ashwell STW | Ilminster Ashwell STW | 612 | 0.065686 | 130194.6875 | 5.5729 | 30.23 | 35.21 | 35.21 | - | 432 | 5.5729 | 40.7829 | 10.5529 | 4.98
13283 | Spaxton . SPS | 160 | 5.8796 | 15.0796 | 11.5 | 11.5 | 867.5304 | 0.16 | 0.57371 | Cannington . STW | Cannington . STW | 610 | 0.016776 | 70183.0737 | 2.7048 | 48.28 | 70.45 | 70.8 | 812 | 868 | 2.7048 | 73.5048 | 25.2248 | 22.52
13389 | Bossington . SPS | 150 | 5.8565 | 13.2536 | 13 | 13 | 1435.4955 | 0.15 | 0.7379 | Porlock Sparkhayes Lane STW | Porlock Sparkhayes Lane STW | 608 | 0.027752 | 84626.5469 | 7.9517 | 10.08 | 20.01 | 20.01 | 1424 | 1424 | 7.9517 | 27.9617 | 17.8817 | 9.93
17235 | Portishead Marjoram Way SPS | 150 | 5.8565 | 13.2536 | - | 13.2536 | 309.0936 | 0.15 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portbury Wharf The Drove Portbury STW | 608 | 0.028846 | 86277.3765 | 1.7781 | 8.91 | 10.15 | 10.37 | 282 | 310 | 1.7781 | 12.1481 | 3.2381 | 1.46
17771 | Bowerhill Melksham Oak SPS | 150 | 5.8333 | 13.2536 | - | 13.2536 | 639.6541 | 0.15 | 0.7523 | Bowerhill Shails Lane STW | Bowerhill Shails Lane STW | 605 | 0.028846 | 86277.3765 | 3.6797 | 45.32 | 53.63 | 53.83 | 630 | 636 | 3.6797 | 57.5097 | 12.1897 | 8.51
14110 | Stoke St Michael Stoke Hill SPS | 100 | 5.8102 | 5.8905 | 11.3 | 11.3 | 454.7677 | 0.1 | 1.4432 | Edford . STW | Edford . STW | 603 | 0.10615 | 110339.9977 | 15.9748 | 183.51 | 202.66 | 202.66 | - | 452 | 15.9748 | 218.6348 | 35.1248 | 19.15
15111 | All Cannings . SPS | 100 | 5.8102 | 5.8905 | 8.5 | 8.5 | 2213.8354 | 0.1 | 1.0856 | All Cannings Lower Mill Farm STW | All Cannings Lower Mill Farm STW | 603 | 0.060064 | 82999.1133 | 44.3742 | 120.1 | 117.99 | 120.25 | - | 2222 | 44.3742 | 164.6242 | 44.5242 | 0.15
14283 | Barton St David . SPS | 170 | 5.8102 | 17.0235 | 5.5 | 5.5 | 1249.682 | 0.17 | 0.24305 | Butleigh . STW | Butleigh . STW | 603 | 0.003011 | 31591.358 | 0.68799 | 14.47 | 14.19 | 18.58 | 884 | 1250 | 0.68799 | 19.268 | 4.798 | 4.11
17472 | Street Houndwood SPS | 110 | 5.8102 | 7.1275 | - | 7.1275 | 105.9791 | 0.11 | 0.7523 | Glastonbury The Beckery SSTW | Street Main SPS | 603 | 0.028846 | 63270.0761 | 0.91305 | 12.06 | 11.79 | 12.06 | 0 | 106 | 0.91305 | 12.973 | 0.91305 | 0
19828 | Portishead Port Marine SPS | 150 | 5.8102 | 13.2536 | - | 13.2536 | 205.1102 | 0.15 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 603 | 0.028846 | 86277.3765 | 1.1799 | 10.23 | 11.15 | 12.04 | 152 | 206 | 1.1799 | 13.2199 | 2.9899 | 1.81
14346 | Hindon The Dene SPS | 100 | 5.787 | 5.8905 | 13 | 13 | 135.3341 | 0.1 | 1.6603 | Hindon . STW | Hindon . STW | 600 | 0.1405 | 126939.8203 | 6.2701 | 116.16 | 130.58 | 130.58 | - | 136 | 6.2701 | 136.8501 | 20.6901 | 14.42
15695 | Wincanton Lawrence Hill SPS | 150 | 5.787 | 13.2536 | - | 13.2536 | 239.878 | 0.15 | 0.7523 | Wincanton . STW | Wincanton . STW | 600 | 0.028846 | 86277.3765 | 1.3799 | 73.34 | 72.97 | 73.35 | 4 | 240 | 1.3799 | 74.7299 | 1.3899 | 0.01
19057 | Kington Magna Five Bridges SPS | 225 | 5.7639 | 29.8206 | - | 29.8206 | 3723.5985 | 0.225 | 0.7523 | Marnhull Common STW | Marnhull Common STW | 598 | 0.028846 | 129416.0648 | 12.7141 | 55.08 | 63.75 | 63.75 | 3724 | 3724 | 12.7141 | 76.4641 | 21.3841 | 8.67
15575 | Portbury Hundred SPS | 150 | 5.7639 | 13.2536 | - | 13.2536 | 1025.1632 | 0.15 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portbury Drove SPS | 598 | 0.028846 | 86277.3765 | 5.8975 | 7.56 | 7.85 | 15.14 | 638 | 1026 | 5.8975 | 21.0375 | 13.4775 | 7.58
17724 | Devizes Quakers Walk SPS | 200 | 5.7407 | 23.5619 | - | 23.5619 | 753.4122 | 0.2 | 0.7523 | Devizes Webbs Lane STW | Devizes Webbs Lane STW | 596 | 0.028846 | 115036.502 | 2.9913 | 133.85 | 133.08 | 134.34 | 122 | 754 | 2.9913 | 137.3313 | 3.4813 | 0.49
15654 | Ilminster Westport SPS | 110 | 5.7407 | 7.1275 | - | 7.1275 | 1594.9447 | 0.11 | 0.7523 | Ilminster Ashwell STW | Barrington West End View SPS | 596 | 0.028846 | 63270.0761 | 13.741 | - | 18.83 | 18.83 | 1582 | 1582 | 13.741 | 32.571 | - | -
14186 | Royal Wootton Bassett Goldborough SPS | 150 | 5.7176 | 13.2536 | - | 13.2536 | 1983.766 | 0.15 | 0.7523 | Royal Wootton Bassett . STW | Royal Wootton Bassett . STW | 593 | 0.028846 | 86277.3765 | 11.412 | 96.07 | 91.35 | 97.89 | - | 1984 | 11.412 | 109.302 | 13.232 | 1.82
14487 | Melksham Berryfields SPS | 315 | 5.7176 | 58.4483 | - | 58.4483 | 1292.3141 | 0.315 | 0.7523 | Bowerhill Shails Lane STW | Bowerhill Shails Lane STW | 593 | 0.028846 | 181182.4907 | 2.8763 | 34.43 | 38.54 | 38.64 | 1064 | 1072 | 2.8763 | 41.5163 | 7.0863 | 4.21
15230 | Poole Kennart Road SPS | 100 | 5.7176 | 5.8905 | 12 | 12 | 231.6555 | 0.1 | 1.5326 | Poole Cabot Lane STW | Poole Cabot Lane STW | 593 | 0.11971 | 117175.2188 | 9.1627 | 2.31 | 2.32 | 2.36 | 230 | 232 | 9.1627 | 11.5227 | 9.2127 | 0.05
14200 | Lea Lea North SPS | 100 | 5.6944 | 5.8905 | 11.2 | 11.2 | 972.8949 | 0.1 | 1.4304 | Malmesbury . STW | Malmesbury Tanners Bridge SPS | 591 | 0.10428 | 109363.5375 | 33.581 | 70.49 | 70.29 | 72.53 | 182 | 972 | 33.581 | 106.111 | 35.621 | 2.04
15115 | Chirton Small Street SPS | 120 | 5.6713 | 8.4823 | 8 | 8 | 936.4698 | 0.12 | 0.70952 | Marden . STW | Marden High Street SPS | 588 | 0.025659 | 65097.3438 | 6.4218 | 110.1 | 105.69 | 111.76 | 188 | 942 | 6.4218 | 118.1818 | 8.0818 | 1.66
15253 | Poole Fairview Road SPS | 100 | 5.6713 | 5.8905 | 13.3 | 13.3 | 111.5737 | 0.1 | 1.6986 | Poole Cabot Lane STW | Poole Cabot Lane STW | 588 | 0.14706 | 129869.2008 | 5.4077 | 42.49 | 42.9 | 42.9 | - | 112 | 5.4077 | 48.3077 | 5.8177 | 0.41
15532 | Timsbury Lippiatt Lane SPS | 150 | 5.625 | 13.2536 | - | 13.2536 | 902.6818 | 0.15 | 0.7523 | Cam Valley Dunkerton STW | Carlingcott Stoneage Lane SPS | 584 | 0.028846 | 86277.3765 | 5.1929 | 139.9 | 153.69 | 154.55 | 864 | 902 | 5.1929 | 159.7429 | 19.8429 | 14.65
14415 | Litton Cheney Chicksbridge SPS | 90 | 5.6018 | 4.7713 | 5.3 | 5.3 | 999.8182 | 0.09 | 0.83566 | Puncknowle Next To Gully Knap Farm STW | Puncknowle Next To Gully Knap Farm STW | 581 | 0.035593 | 57502.6537 | 13.7744 | - | 57.08 | 57.08 | 990 | 990 | 13.7744 | 70.8544 | - | -
17613 | Malmesbury Cowbridge New SPS | 120 | 5.5787 | 8.4823 | - | 8.4823 | 923.36 | 0.12 | 0.7523 | Malmesbury . STW | Malmesbury . STW | 579 | 0.028846 | 69021.9012 | 7.0997 | 67.39 | 73.25 | 79.41 | 318 | 924 | 7.0997 | 86.5097 | 19.1197 | 12.02
14256 | Affpuddle . SPS | 120 | 5.5787 | 8.4823 | 6 | 6 | 527.242 | 0.12 | 0.53214 | Blackheath . STW | Briantspuddle . SPS | 579 | 0.014433 | 48823.0078 | 2.0638 | 39.36 | 53.71 | 54.04 | 506 | 532 | 2.0638 | 56.1038 | 16.7438 | 14.68
19821 | Pitminster Weir SPS | 125 | 5.5555 | 9.2039 | - | 9.2039 | 799.8091 | 0.125 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 576 | 0.028846 | 71897.8138 | 5.8309 | 69.56 | 80.51 | 80.51 | 790 | 790 | 5.8309 | 86.3409 | 16.7809 | 10.95
14149 | Chippenham Field View SPS | 100 | 5.5324 | 5.8905 | - | 5.8905 | 94.07 | 0.1 | 0.7523 | Chippenham Blackwell Hams STW | Chippenham Blackwell Hams STW | 574 | 0.028846 | 57518.251 | 0.91838 | 46.34 | 47.19 | 47.19 | 94 | 94 | 0.91838 | 48.1084 | 1.7684 | 0.85
15165 | Easter Compton Pilning Road SPS | 200 | 5.5324 | 23.5619 | - | 23.5619 | 1813.264 | 0.2 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Kingsweston Lane STW | 574 | 0.028846 | 115036.502 | 7.1993 | 9.4 | 6.67 | 10.93 | 310 | 1814 | 7.1993 | 18.1293 | 8.7293 | 1.53
15639 | Compton Dundon Moor Close SPS | 100 | 5.463 | 5.8905 | - | 5.8905 | 1526.6276 | 0.1 | 0.7523 | Somerton Barpool Lane STW | Somerton Barpool Lane STW | 567 | 0.028846 | 57518.251 | 14.904 | 9.48 | 9.28 | 9.65 | 22 | 1526 | 14.904 | 24.554 | 15.074 | 0.17
14396 | Over Compton . SPS | 125 | 5.4398 | 9.2039 | - | 9.2039 | 956.4461 | 0.125 | 0.7523 | Trent Mill Lane STW | Trent Mill Lane STW | 564 | 0.028846 | 71897.8138 | 6.9728 | - | 39.25 | 40.16 | - | 798 | 6.9728 | 47.1328 | - | -
15548 | Keynsham Keynsham Low Level SPS | 100 | 5.3472 | 5.8905 | 10 | 10 | 32.7557 | 0.1 | 1.2771 | Keynsham . STW | Keynsham Keynsham High Level SPS | 555 | 0.083134 | 97646.0157 | 0.90416 | 12.24 | 13.23 | 13.23 | 32 | 32 | 0.90416 | 14.1342 | 1.8942 | 0.99
14287 | Hinton St George . SPS | 100 | 5.3241 | 5.8905 | 7 | 7 | 438.0217 | 0.1 | 0.894 | Longbridge Fosse Way STW | Longbridge Fosse Way STW | 552 | 0.040736 | 68352.211 | 5.996 | 79.66 | 85.25 | 90.03 | - | 438 | 5.996 | 96.026 | 16.366 | 10.37
14507 | Shirehampton Lamplighters SPS | 250 | 5.3241 | 36.8155 | 37 | 37 | 142.4873 | 0.25 | 0.75607 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 552 | 0.029135 | 144516.1032 | 0.42949 | 8.27 | 12.83 | 13.39 | 120 | 142 | 0.42949 | 13.8195 | 5.5495 | 5.12
14554 | Chard Touches Lane SPS | 150 | 5.3241 | 13.2536 | - | 13.2536 | 415.6802 | 0.15 | 0.7523 | Chard Peasmarsh STW | Chard Peasmarsh STW | 552 | 0.028846 | 86277.3765 | 2.3913 | - | 81.6 | 81.6 | 402 | 402 | 2.3913 | 83.9913 | - | -
14216 | Stoborough Kings Arms SPS | 150 | 5.3009 | 13.2536 | 15.3 | 15.3 | 1642.9075 | 0.15 | 0.86845 | Wareham Keysworth Drive STW | Wareham South East SPS | 550 | 0.038441 | 99598.936 | 12.5214 | 1.08 | 2.27 | 2.96 | - | 1632 | 12.5214 | 15.4814 | 14.4014 | 1.88
15490 | Crossways Redbridge SPS | 100 | 5.2546 | 5.8905 | - | 5.8905 | 587.3643 | 0.1 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Warmwell Crossways Of B3390 SPS | 545 | 0.028846 | 57518.251 | 5.7343 | 58.16 | 59.84 | 60.24 | 488 | 588 | 5.7343 | 65.9743 | 7.8143 | 2.08
15186 | Iron Acton Latteridge Road SPS | 200 | 5.2546 | 23.5619 | - | 23.5619 | 1280.5373 | 0.2 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 545 | 0.028846 | 115036.502 | 5.0842 | 50.71 | 53.64 | 54.89 | 1212 | 1280 | 5.0842 | 59.9742 | 9.2642 | 4.18
14094 | Glastonbury Thorndun SPS | 150 | 5.2546 | 13.2536 | - | 13.2536 | 1082.6307 | 0.15 | 0.7523 | Glastonbury The Beckery SSTW | Glastonbury Porchestall SPS | 545 | 0.028846 | 86277.3765 | 6.2281 | 6.23 | 16.56 | 16.56 | - | 1080 | 6.2281 | 22.7881 | 16.5581 | 10.33
11663 | Melksham Caretakers Close SPS | - | 5.2315 | - | - | - | 67.3088 | - | - | Melksham . STW | Melksham Caretakers Close SPS | 543 | - | - | - | - | - | - | - | - | - | - | - | -
15641 | Salway Ash Old Stw SPS | 120 | 5.2083 | 8.4823 | - | 8.4823 | 1346.2064 | 0.12 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 540 | 0.028846 | 69021.9012 | 10.351 | 34.31 | 45.41 | 55.44 | 506 | 1346 | 10.351 | 65.791 | 31.481 | 21.13
15710 | Bridgwater Docks SPS | 100 | 5.1852 | 5.8905 | - | 5.8905 | 160.434 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater West Quay Drawbridge SPS | 538 | 0.028846 | 57518.251 | 1.5663 | 8.64 | 9.48 | 10.69 | 74 | 160 | 1.5663 | 12.2563 | 3.6163 | 2.05
17087 | Bridport Meadowlands SPS | 125 | 5.1389 | 9.2039 | - | 9.2039 | 115.1841 | 0.125 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 533 | 0.028846 | 71897.8138 | 0.83973 | 3.82 | 2.5 | 3.82 | 0 | 116 | 0.83973 | 4.6597 | 0.83973 | 0
15557 | Weymouth Overcombe SPS | 160 | 5.1389 | 15.0796 | - | 15.0796 | 532.4239 | 0.16 | 0.7523 | Weymouth . STW | Weymouth Lodmoor Weymouth Bay Avenue SPS | 533 | 0.028846 | 92029.2016 | 2.8175 | 1.46 | 4.03 | 4.03 | 532 | 532 | 2.8175 | 6.8475 | 5.3875 | 2.57
15493 | Frampton Muckleford SPS | 100 | 5.0926 | 5.8905 | - | 5.8905 | 859.0167 | 0.1 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Stratton Stratton Bridge SPS | 528 | 0.028846 | 57518.251 | 8.3863 | 71.93 | 76.62 | 77.31 | 848 | 860 | 8.3863 | 85.6963 | 13.7663 | 5.38
14562 | Glastonbury Wirral Park SPS | 100 | 5.0463 | 5.8905 | 3 | 3 | 355.9685 | 0.1 | 0.38314 | Glastonbury The Beckery SSTW | Glastonbury Porchestall SPS | 524 | 0.007482 | 29293.8047 | 0.93712 | 7.48 | 6.61 | 7.48 | 0 | 338 | 0.93712 | 8.4171 | 0.93712 | 0
15001 | Southbourne Wick Lane SPS | 150 | 5.0463 | 13.2536 | - | 13.2536 | 288.178 | 0.15 | 0.7523 | Holdenhurst Riverside Avenue STW | Southbourne Hengistbury Head SPS | 524 | 0.028846 | 86277.3765 | 1.6578 | 1.6 | 5.67 | 5.93 | - | 288 | 1.6578 | 7.5878 | 5.9878 | 4.33
15494 | Abbotsbury Church Street SPS | 100 | 5.0231 | 5.8905 | 9.3 | 9.3 | 412.764 | 0.1 | 1.1877 | Abbotsbury B3157 Portesham Road STW | Abbotsbury B3157 Portesham Road STW | 521 | 0.071902 | 90810.7946 | 9.8757 | 32.89 | 44.08 | 44.25 | - | 412 | 9.8757 | 54.1257 | 21.2357 | 11.36
15408 | Bridgwater Eastern Avenue SPS | 190 | 5.0231 | 21.2647 | - | 21.2647 | 8.2457 | 0.19 | 0.7523 | Chilton Trinity . STW | Bridgwater Colley Lane SPS | 521 | 0.028846 | 109284.6769 | 0.034967 | 5.92 | 5.88 | 5.92 | 0 | 8 | 0.034967 | 5.955 | 0.034967 | 0
14179 | Biddestone Manor Cottages SPS | 100 | 5 | 5.8905 | 7 | 7 | 1362.7986 | 0.1 | 0.894 | Thingley Coppershell Lane STW | Thingley Coppershell Lane STW | 519 | 0.040736 | 68352.211 | 18.655 | 106.19 | 115 | 116.15 | - | 1362 | 18.655 | 134.805 | 28.615 | 9.96
10414 | Weston-Super-Mare Wilson Gardens Private SPS | 90 | 5 | 4.7713 | - | 4.7713 | 9.2425 | 0.09 | 0.7523 | Wick St Lawrence . STW | St Georges Brimbleworth Farm SPS | 519 | 0.028846 | 51766.4259 | 0.10366 | 5.24 | 5.26 | 5.3 | 6 | 10 | 0.10366 | 5.4037 | 0.16366 | 0.06
15484 | Charmouth Lower Sea Lane SPS | 125 | 5 | 9.2039 | - | 9.2039 | 271.0894 | 0.125 | 0.7523 | Charmouth Headworks/Sea Outfall STW | Charmouth Headworks/Sea Outfall STW | 519 | 0.028846 | 71897.8138 | 1.9763 | 4.39 | 18.3 | 18.3 | 272 | 272 | 1.9763 | 20.2763 | 15.8863 | 13.91
19712 | Litton . SPS | 180 | 4.9537 | 19.0852 | - | 19.0852 | 3060.4552 | 0.18 | 0.7523 | Radstock Mill Lane STW | Radstock Mill Lane STW | 514 | 0.028846 | 103532.8518 | 13.913 | 104.54 | 144.59 | 165.88 | 1442 | 3050 | 13.913 | 179.793 | 75.253 | 61.34
15457 | Wellington Westford SPS | 100 | 4.9537 | 5.8905 | 13.8 | 13.8 | 180.389 | 0.1 | 1.7625 | Wellington Tone STW | Wellington Tone STW | 514 | 0.15832 | 134751.5016 | 9.4049 | 59.53 | 58.9 | 60.15 | 54 | 176 | 9.4049 | 69.5549 | 10.0249 | 0.62
17079 | Bridgwater Reedmoor Gardens SPS | 100 | 4.9537 | 5.8905 | - | 5.8905 | 331.9654 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Chilton Street Saltlands SPS | 514 | 0.028846 | 57518.251 | 3.2409 | 7.05 | 6.47 | 7.06 | 2 | 332 | 3.2409 | 10.3009 | 3.2509 | 0.01
14071 | Meare Oxenpill SPS | 75 | 4.9537 | 3.3134 | - | 3.3134 | 386.3315 | 0.075 | 0.7523 | Meare . STW | Meare . STW | 514 | 0.028846 | 43138.6883 | 5.5162 | 6.56 | 7.36 | 8.35 | 308 | 386 | 5.5162 | 13.8662 | 7.3062 | 1.79
14362 | Chilmark . SPS | 150 | 4.9305 | 13.2536 | 4.9 | 4.9 | 1902.7248 | 0.15 | 0.27813 | Tisbury Higher Chicksgrove STW | Tisbury Higher Chicksgrove STW | 512 | 0.0039428 | 31897.6984 | 1.5937 | 98.24 | 91.45 | 103.32 | 348 | 1902 | 1.5937 | 104.9137 | 6.6737 | 5.08
15124 | Enford Coombe SPS | 125 | 4.9305 | 9.2039 | - | 9.2039 | 397.3315 | 0.125 | 0.7523 | Netheravon . STW | Netheravon Camp Road SPS | 512 | 0.028846 | 71897.8138 | 2.8967 | 84.47 | 91.76 | 91.79 | 396 | 398 | 2.8967 | 94.6867 | 10.2167 | 7.32
14131 | Ringwood Moortown SPS | 150 | 4.9305 | 13.2536 | - | 13.2536 | 728.2143 | 0.15 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Hampshire Hatches Lane STW | 512 | 0.028846 | 86277.3765 | 4.1892 | 12.88 | 12.1 | 15.47 | 578 | 728 | 4.1892 | 19.6592 | 6.7792 | 2.59
19558 | Cheddar Draycott Road SPS | 125 | 4.9305 | 9.2039 | - | 9.2039 | 670.0452 | 0.125 | 0.7523 | Cheddar . STW | Cheddar Froglands SPS | 512 | 0.028846 | 71897.8138 | 4.8848 | 7.33 | 8.74 | 9.79 | 10 | 666 | 4.8848 | 14.6748 | 7.3448 | 2.46
15178 | Pilning Pilning Church The Green SPS | 150 | 4.9074 | 13.2536 | - | 13.2536 | 256.759 | 0.15 | 0.7523 | Redwick . STW | Pilning Redwick Road SPS | 509 | 0.028846 | 86277.3765 | 1.4771 | 6.19 | 7.03 | 7.5 | - | 250 | 1.4771 | 8.9771 | 2.7871 | 1.31
14116 | Gurney Slade . SPS | 100 | 4.8842 | 5.8905 | 7 | 7 | 2389.1043 | 0.1 | 0.894 | Oakhill . STW | Oakhill . STW | 507 | 0.040736 | 68352.211 | 32.7038 | 171.68 | 151.2 | 174.14 | 82 | 2390 | 32.7038 | 206.8438 | 35.1638 | 2.46
15131 | Collingbourne Kingston . SPS | 100 | 4.8842 | 5.8905 | - | 5.8905 | 1614.0576 | 0.1 | 0.7523 | Collingbourne Ducis . STW | Collingbourne Ducis . SPS | 507 | 0.028846 | 57518.251 | 15.7576 | 133.88 | 138.06 | 140.92 | 1394 | 1614 | 15.7576 | 156.6776 | 22.7976 | 7.04
15468 | Bradford On Tone Hockholler A38 SPS | 100 | 4.8842 | 5.8905 | 6 | 6 | 509.0625 | 0.1 | 0.76628 | Bradford On Tone . STW | Bradford On Tone . STW | 507 | 0.029928 | 58587.6094 | 5.1522 | 39.04 | 54.8 | 55.44 | 504 | 552 | 5.1522 | 60.5922 | 21.5522 | 16.4
14153 | Broadtown Cotmarsh Farm SPS | 100 | 4.8148 | 5.8905 | - | 5.8905 | 272.4709 | 0.1 | 0.7523 | Royal Wootton Bassett . STW | Royal Wootton Bassett Goldborough SPS | 500 | 0.028846 | 57518.251 | 2.6601 | 100.12 | 99.71 | 100.27 | - | 268 | 2.6601 | 102.9301 | 2.8101 | 0.15
17249 | Tolpuddle East Farm SPS | 180 | 4.8148 | 19.0852 | - | 19.0852 | 1790.7001 | 0.18 | 0.7523 | Blackheath . STW | Affpuddle . SPS | 500 | 0.028846 | 103532.8518 | 8.1406 | - | 39.47 | 53.51 | 492 | 1790 | 8.1406 | 61.6506 | - | -
13375 | Lyneham Preston Lane SPS | - | 4.8148 | - | - | - | 222.4884 | - | - | Lyneham Preston Lane SPS | - | 500 | - | - | - | - | - | - | - | - | - | - | - | -
15574 | Sandford Batch . SPS | 150 | 4.7917 | 13.2536 | 9.8 | 9.8 | 406.8188 | 0.15 | 0.55627 | Winscombe . STW | Winscombe . STW | 497 | 0.015771 | 63795.3969 | 1.2984 | 29.51 | 38.33 | 38.47 | - | 406 | 1.2984 | 39.7684 | 10.2584 | 8.96
15635 | Poole Cowslip Road Pine Springs SPS | 170 | 4.7917 | 17.0235 | - | 17.0235 | 321.3198 | 0.17 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 497 | 0.028846 | 97781.0267 | 1.5724 | 23.62 | 39.64 | 39.65 | 314 | 316 | 1.5724 | 41.2224 | 17.6024 | 16.03
15028 | Christchurch Clive Road SPS | 100 | 4.7917 | 5.8905 | - | 5.8905 | 83.0086 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Somerford Bridge SPS | 497 | 0.028846 | 57518.251 | 0.81039 | 20.22 | 21.52 | 23.16 | 20 | 84 | 0.81039 | 23.9704 | 3.7504 | 2.94
15266 | Poole Merley Lane Merley SPS | 100 | 4.7685 | 5.8905 | - | 5.8905 | 659.2398 | 0.1 | 0.7523 | Wimborne Brook Road STW | Canford Magna Canford Main SPS | 495 | 0.028846 | 57518.251 | 6.436 | 26.64 | 39.71 | 39.79 | 502 | 660 | 6.436 | 46.226 | 19.586 | 13.15
17034 | Lympsham Innsbruck SPS | 110 | 4.7454 | 7.1275 | - | 7.1275 | 2050.3486 | 0.11 | 0.7523 | West Huntspill STW | Brent Knoll Forge House Brent Street SPS | 492 | 0.028846 | 63270.0761 | 17.6645 | 5.41 | 5.74 | 5.94 | 492 | 2056 | 17.6645 | 23.6045 | 18.1945 | 0.53
15293 | Stoford Newton Road Garage SPS | 75 | 4.7222 | 3.3134 | - | 3.3134 | 102.9335 | 0.075 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Stoford Hillside Main SPS | 490 | 0.028846 | 43138.6883 | 1.4697 | 37.44 | 37.59 | 37.59 | 102 | 102 | 1.4697 | 39.0597 | 1.6197 | 0.15
14101 | Westbury-Sub-Mendip Easton SPS | 100 | 4.7222 | 5.8905 | - | 5.8905 | 620.7274 | 0.1 | 0.7523 | Westbury-Sub-Mendip . STW | Westbury-Sub-Mendip . STW | 490 | 0.028846 | 57518.251 | 6.06 | 13.98 | 25.75 | 25.75 | 620 | 620 | 6.06 | 31.81 | 17.83 | 11.77
14104 | Frome Spring Gardens SPS | 350 | 4.7222 | 72.1585 | - | 72.1585 | 637.2699 | 0.35 | 0.7523 | Frome Welshmill Lane STW | Frome Leonards Mill SPS | 490 | 0.028846 | 201313.8786 | 1.2415 | - | 62.51 | 65.89 | 12 | 308 | 1.2415 | 67.1315 | - | -
14358 | South Newton Bell Inn SPS | 150 | 4.6991 | 13.2536 | - | 13.2536 | 846.3744 | 0.15 | 0.7523 | Wishford Wilton Road STW | Wishford Wilton Road STW | 488 | 0.028846 | 86277.3765 | 4.8689 | 57.29 | 60.1 | 60.63 | 834 | 840 | 4.8689 | 65.4989 | 8.2089 | 3.34
14271 | Wareham Drax Avenue SPS | 125 | 4.6991 | 9.2039 | - | 9.2039 | 60.6162 | 0.125 | 0.7523 | Wareham Keysworth Drive STW | Wareham Sandford Lane SPS | 488 | 0.028846 | 71897.8138 | 0.44191 | 4.84 | 5.86 | 5.86 | 60 | 60 | 0.44191 | 6.3019 | 1.4619 | 1.02
14364 | Figheldean Avon Banks SPS | 125 | 4.6759 | 9.2039 | - | 9.2039 | 1581.2766 | 0.125 | 0.7523 | Ratfyn . STW | Durrington Nags Head SPS | 485 | 0.028846 | 71897.8138 | 11.528 | 78.61 | 80.43 | 81.37 | 104 | 1582 | 11.528 | 92.898 | 14.288 | 2.76
15443 | Taunton New Barn Queensway SPS | 150 | 4.6528 | 13.2536 | 21 | 21 | 184.889 | 0.15 | 1.192 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 483 | 0.072419 | 136704.4219 | 2.6261 | 29.49 | 30.88 | 30.88 | 184 | 184 | 2.6261 | 33.5061 | 4.0161 | 1.39
15735 | Ringwood Waterloo Way (Station Yard) SPS | 150 | 4.6528 | 13.2536 | - | 13.2536 | 455.5017 | 0.15 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Bickerley SPS | 483 | 0.028846 | 86277.3765 | 2.6204 | 17.03 | 14.77 | 17.76 | 138 | 456 | 2.6204 | 20.3804 | 3.3504 | 0.73
14219 | Upton Sandy Lane SPS | 100 | 4.6296 | 5.8905 | 6.4 | 6.4 | 316.7814 | 0.1 | 0.81737 | Lytchett Minster Lytchett Bay STW | Upton Moorlands Way SPS | 480 | 0.034052 | 62493.45 | 3.6379 | 2.45 | 6.36 | 6.99 | 276 | 310 | 3.6379 | 10.6279 | 8.1779 | 4.54
15462 | Bishops Lydeard Greenway SPS | 100 | 4.5833 | 5.8905 | - | 5.8905 | 615.99 | 0.1 | 0.7523 | Sandhill Park . STW | Sandhill Park . STW | 476 | 0.028846 | 57518.251 | 6.0137 | 53.57 | 59.16 | 59.89 | 580 | 616 | 6.0137 | 65.9037 | 12.3337 | 6.32
14217 | Upton Hibbs Close SPS | 100 | 4.5602 | 5.8905 | - | 5.8905 | 208.2054 | 0.1 | 0.7523 | Lytchett Minster Lytchett Bay STW | Upton Moorlands Way SPS | 473 | 0.028846 | 57518.251 | 2.0327 | 17.81 | 23.35 | 23.52 | 204 | 208 | 2.0327 | 25.5527 | 7.7427 | 5.71
14083 | West Pennard Havyatt SPS | 125 | 4.5602 | 9.2039 | 8.1 | 8.1 | 3179.5419 | 0.125 | 0.66207 | Butleigh . STW | Baltonsborough Baltonsborough Main SPS | 473 | 0.022341 | 63274.6181 | 18.0585 | 16.49 | 19.86 | 21.51 | - | 3180 | 18.0585 | 39.5685 | 23.0785 | 5.02
15356 | Rooksbridge Mendip Road (Factory Road) Edingworth SPS | 150 | 4.537 | 13.2536 | - | 13.2536 | 1307.206 | 0.15 | 0.7523 | West Huntspill STW | East Brent Orchard Close SPS | 471 | 0.028846 | 86277.3765 | 7.52 | 5.95 | 5.83 | 8.1 | 196 | 1308 | 7.52 | 15.62 | 9.67 | 2.15
15469 | Leigh Frampton Farm SPS | 125 | 4.537 | 9.2039 | 14 | 14 | 868.9497 | 0.125 | 1.1443 | Thornford Bridge Halt STW | Beer Hackett . SPS | 471 | 0.066741 | 109363.5375 | 14.4305 | - | 70 | 70.15 | - | 830 | 14.4305 | 84.5805 | - | -
14398 | Owermoigne Crossways Road SPS | 150 | 4.5139 | 13.2536 | - | 13.2536 | 1466.0462 | 0.15 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Warmwell Crossways Of B3390 SPS | 468 | 0.028846 | 86277.3765 | 8.4337 | 34.38 | 53.2 | 53.21 | 1468 | 1470 | 8.4337 | 61.6437 | 27.2637 | 18.83
14634 | Wellington Farthings Pitts SPS | 100 | 4.4907 | 5.8905 | - | 5.8905 | 411.7447 | 0.1 | 0.7523 | Wellington Tone STW | Wellington Tone STW | 466 | 0.028846 | 57518.251 | 4.0197 | 83.67 | 89.39 | 89.39 | - | 412 | 4.0197 | 93.4097 | 9.7397 | 5.72
19612 | Milton Abbas Milton Road SPS | 100 | 4.4676 | 5.8905 | - | 5.8905 | 11.1397 | 0.1 | 0.7523 | Milborne St Andrew . STW | Milborne St Andrew Manor Farm SPS | 464 | 0.028846 | 57518.251 | 0.10875 | 98.84 | 98.61 | 98.84 | 0 | 12 | 0.10875 | 98.9488 | 0.10875 | 0
14139 | Christian Malford Swalletts Gate SPS | 100 | 4.4676 | 5.8905 | 10 | 10 | 623.946 | 0.1 | 1.2771 | Sutton Benger . STW | Sutton Benger . STW | 464 | 0.083134 | 97646.0157 | 17.2228 | 58.3 | 59.47 | 59.83 | 584 | 616 | 17.2228 | 77.0528 | 18.7528 | 1.53
14058 | Horton Horton Farm SPS | 110 | 4.4444 | 7.1275 | 5.6 | 5.6 | 1197.0138 | 0.11 | 0.59107 | All Cannings Lower Mill Farm STW | All Cannings Lower Mill Farm STW | 461 | 0.017807 | 49710.6989 | 6.4407 | 122.68 | 118.03 | 123.32 | 148 | 1196 | 6.4407 | 129.7607 | 7.0807 | 0.64
14523 | Low Ham Moretons Lane SPS | 150 | 4.4444 | 13.2536 | - | 13.2536 | 3508.031 | 0.15 | 0.7523 | Langport Portfield Lane STW | Langport Portfield Lane STW | 461 | 0.028846 | 86277.3765 | 20.1807 | 21.26 | 16.5 | 64.18 | 1718 | 3506 | 20.1807 | 84.3607 | 63.1007 | 42.92
15229 | Poole Whitecliff Recreation Ground SPS | 100 | 4.4444 | 5.8905 | - | 5.8905 | 259.6076 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Shore Road SPS | 461 | 0.028846 | 57518.251 | 2.5345 | 1.79 | 3.65 | 3.65 | 260 | 260 | 2.5345 | 6.1845 | 4.3945 | 1.86
14126 | Shroton . SPS | 100 | 4.3981 | 5.8905 | 9.6 | 9.6 | 783.2618 | 0.1 | 1.2261 | Shroton . STW | Shroton . STW | 456 | 0.076616 | 93740.175 | 19.9494 | 53.77 | 50.56 | 62.49 | - | 784 | 19.9494 | 82.4394 | 28.6694 | 8.72
14392 | West Buckland . SPS | 100 | 4.3981 | 5.8905 | 10 | 10 | 795.9519 | 0.1 | 1.2771 | Bradford On Tone . STW | Bradford On Tone . STW | 456 | 0.083134 | 97646.0157 | 21.9707 | 47.66 | 50.96 | 51.51 | 706 | 794 | 21.9707 | 73.4807 | 25.8207 | 3.85
14550 | Lacock Nethercote Hill SPS | 150 | 4.3981 | 13.2536 | 13.5 | 13.5 | 416.4134 | 0.15 | 0.76628 | Lacock . STW | Lacock . STW | 456 | 0.029928 | 87881.4141 | 2.4834 | 40.09 | 43.93 | 44.6 | 384 | 408 | 2.4834 | 47.0834 | 6.9934 | 4.51
13265 | Shapwick Somerset SPS | 100 | 4.375 | 5.8905 | 7 | 7 | 2714.7607 | 0.1 | 0.894 | West Huntspill STW | Edington Broadmead Lane (Som) SPS | 454 | 0.040736 | 68352.211 | 37.1617 | 20.95 | 20.2 | 30.74 | 2186 | 2714 | 37.1617 | 67.9017 | 46.9517 | 9.79
15194 | Marnhull ¦ Musbury SPS | 100 | 4.3287 | 5.8905 | - | 5.8905 | 552.2793 | 0.1 | 0.7523 | Marnhull Common STW | Marnhull Common STW | 449 | 0.028846 | 57518.251 | 5.3917 | 70.85 | 87.33 | 87.98 | 506 | 552 | 5.3917 | 93.3717 | 22.5217 | 17.13
14654 | Westbury Washington Road SPS | 170 | 4.3287 | 17.0235 | - | 17.0235 | 862.9331 | 0.17 | 0.7523 | Westbury STW | Westbury STW | 449 | 0.028846 | 97781.0267 | 4.2228 | 50.72 | 64.08 | 64.08 | 862 | 862 | 4.2228 | 68.3028 | 17.5828 | 13.36
14531 | Midford Tucking Mill SPS | 125 | 4.3287 | 9.2039 | 6 | 6 | 1027.3865 | 0.125 | 0.49042 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 449 | 0.012259 | 46870.0875 | 3.2539 | 34.78 | 61.78 | 61.83 | 1024 | 1028 | 3.2539 | 65.0839 | 30.3039 | 27.05
15319 | Chard Edwards SPS | 150 | 4.3055 | 13.2536 | - | 13.2536 | 978.9872 | 0.15 | 0.7523 | Chard Peasmarsh STW | Chard Peasmarsh STW | 447 | 0.028846 | 86277.3765 | 5.6318 | 85.63 | 91.11 | 92.92 | - | 978 | 5.6318 | 98.5518 | 12.9218 | 7.29
15474 | Crossways Combe Way SPS | 100 | 4.2593 | 5.8905 | - | 5.8905 | 31.7921 | 0.1 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Warmwell Crossways Of B3390 SPS | 442 | 0.028846 | 57518.251 | 0.31038 | 60.16 | 60.64 | 60.76 | 28 | 32 | 0.31038 | 61.0704 | 0.91038 | 0.6
14291 | West Camel . SPS | 75 | 4.2593 | 3.3134 | 3.5 | 3.5 | 1746.5686 | 0.075 | 0.79466 | Chilton Cantelo Hornsey Bridge STW | Chilton Cantelo Hornsey Bridge STW | 442 | 0.032186 | 45568.1406 | 27.759 | 25.15 | 22.44 | 31.42 | 758 | 1748 | 27.759 | 59.179 | 34.029 | 6.27
15150 | Oldbury The Naite SPS | 100 | 4.2593 | 5.8905 | - | 5.8905 | 1532.6037 | 0.1 | 0.7523 | Thornbury . STW | Thornbury . STW | 442 | 0.028846 | 57518.251 | 14.9624 | 6.12 | 6.44 | 6.62 | 596 | 634 | 14.9624 | 21.5824 | 15.4624 | 0.5
15505 | Symondsbury West Road Foundry SPS | 300 | 4.2361 | 53.0144 | 6 | 6 | 3566.6599 | 0.3 | 0.085143 | Bridport Wych Farm STW | Bridport West Bay SPS | 440 | 0.00036948 | 19529.2031 | 0.13238 | 9.33 | 13.81 | 31.33 | 662 | 3566 | 0.13238 | 31.4624 | 22.1324 | 22
11937 | Wimborne Waters Edge SPS | - | 4.2361 | - | - | - | 337.0361 | - | - | Wimborne Brook Road STW | Wimborne Brook Road STW | 440 | - | - | - | - | - | - | - | - | - | - | - | -
14341 | Alderbury Junction Road SPS | 125 | 4.1898 | 9.2039 | - | 9.2039 | 567.2142 | 0.125 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Alderbury Home Farm SPS | 435 | 0.028846 | 71897.8138 | 4.1352 | 66.71 | 81.95 | 81.95 | 568 | 568 | 4.1352 | 86.0852 | 19.3752 | 15.24
15052 | Verwood Ebblake SPS | 80 | 4.1898 | 3.7699 | 5 | 5 | 840.8724 | 0.08 | 0.99777 | Palmersford . STW | Verwood Potterne Way SPS | 435 | 0.050741 | 61028.7598 | 19.1666 | 24 | 26.92 | 27.84 | - | 840 | 19.1666 | 47.0066 | 23.0066 | 3.84
14152 | Broads Green . SPS | 125 | 4.1667 | 9.2039 | 7.6 | 7.6 | 1503.4823 | 0.125 | 0.6212 | Calne . STW | Calne Rough Leaze SPS | 432 | 0.019668 | 59368.7775 | 7.5411 | 83.47 | 96.78 | 96.78 | - | 1504 | 7.5411 | 104.3211 | 20.8511 | 13.31
14354 | Barford St Martin . SPS | 100 | 4.1667 | 5.8905 | 5 | 5 | 581.2403 | 0.1 | 0.63857 | Barford St Martin Burcombe STW | Barford St Martin Burcombe STW | 432 | 0.020783 | 48823.0078 | 4.1202 | 61.22 | 67.57 | 69.73 | 548 | 582 | 4.1202 | 73.8502 | 12.6302 | 8.51
14281 | Lytchett Minster Bakers Arms SPS | 160 | 4.1667 | 15.0796 | - | 15.0796 | 1524.4974 | 0.16 | 0.7523 | Lytchett Minster Lytchett Bay STW | Lytchett Minster Lytchett Bay STW | 432 | 0.028846 | 92029.2016 | 8.0675 | 1.8 | 1.66 | 3.93 | 800 | 1524 | 8.0675 | 11.9975 | 10.1975 | 2.13
19816 | Banwell Elborough Village SPS | 125 | 4.1435 | 9.2039 | - | 9.2039 | 296.291 | 0.125 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Uphill . SPS | 430 | 0.028846 | 71897.8138 | 2.1601 | 12.42 | 9.57 | 12.42 | 0 | 296 | 2.1601 | 14.5801 | 2.1601 | 0
14193 | Sherston Sandpits Lane SPS | 75 | 4.1204 | 3.3134 | - | 3.3134 | 184.4789 | 0.075 | 0.7523 | Sherston . STW | Sherston . STW | 428 | 0.028846 | 43138.6883 | 2.6341 | 114.66 | 115.64 | 116.54 | - | 184 | 2.6341 | 119.1741 | 4.5141 | 1.88
14411 | Sydling St Nicholas . SPS | 150 | 4.1204 | 13.2536 | 17 | 17 | 512.3921 | 0.15 | 0.96495 | Sydling St Nicholas Near Huish Farm STW | Sydling St Nicholas Near Huish Farm STW | 428 | 0.047458 | 110665.4844 | 4.8024 | 104.4 | 105.76 | 105.82 | 250 | 254 | 4.8024 | 110.6224 | 6.2224 | 1.42
14065 | Kingswood Parkwall Road SPS | 100 | 4.1204 | 5.8905 | - | 5.8905 | 167.0593 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 428 | 0.028846 | 57518.251 | 1.631 | 46.51 | 52.04 | 52.1 | 150 | 168 | 1.631 | 53.731 | 7.221 | 5.59
14339 | Downton Moot Close/ Moot Gardens SPS | 100 | 4.1204 | 5.8905 | - | 5.8905 | 657.5202 | 0.1 | 0.7523 | Downton Moot Lane STW | Downton Moot Lane STW | 428 | 0.028846 | 57518.251 | 6.4192 | 37.58 | 39.73 | 39.78 | 656 | 658 | 6.4192 | 46.1992 | 8.6192 | 2.2
14380 | North Newton Church Road SPS | 180 | 4.0972 | 19.0852 | 13.2 | 13.2 | 2004.2832 | 0.18 | 0.52032 | North Petherton . STW | North Petherton . STW | 425 | 0.013799 | 71607.0781 | 4.4385 | 9.81 | 22.37 | 27.24 | 1348 | 1888 | 4.4385 | 31.6785 | 21.8685 | 17.43
14255 | Stoborough Ridge SPS | 100 | 4.0741 | 5.8905 | 5 | 5 | 727.9648 | 0.1 | 0.63857 | Wareham Keysworth Drive STW | Wareham South East SPS | 423 | 0.020783 | 48823.0078 | 5.1603 | 2.82 | 3.59 | 10.63 | 486 | 726 | 5.1603 | 15.7903 | 12.9703 | 7.81
15355 | West Huntspill Main Road SPS | 150 | 4.0509 | 13.2536 | - | 13.2536 | 271.1519 | 0.15 | 0.7523 | West Huntspill STW | West Huntspill Crossways Withy Road SPS | 420 | 0.028846 | 86277.3765 | 1.5599 | 5.48 | 5.54 | 5.71 | 14 | 272 | 1.5599 | 7.2699 | 1.7899 | 0.23
19663 | Blackford Blackford Moor Lane SPS | 125 | 4.0509 | 9.2039 | - | 9.2039 | 2442.0741 | 0.125 | 0.7523 | West Huntspill STW | Mark . SPS | 420 | 0.028846 | 71897.8138 | 17.8035 | 5.42 | 5.32 | 6.01 | 2288 | 2438 | 17.8035 | 23.8135 | 18.3935 | 0.59
15166 | Rangeworthy Berrows Mead SPS | 150 | 4.0278 | 13.2536 | 8 | 8 | 701.6061 | 0.15 | 0.45409 | Cromhall . STW | Bagstone . SPS | 418 | 0.01051 | 52077.875 | 1.51 | 69.27 | 62.07 | 69.39 | 2 | 702 | 1.51 | 70.9 | 1.63 | 0.12
18710 | Bristol Royal Edward Dock St Andrews Road SPS | 350 | 4.0278 | 72.1585 | - | 72.1585 | 3474.6393 | 0.35 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Kingsweston Lane STW | 418 | 0.028846 | 201313.8786 | 6.7694 | 8.97 | 8.06 | 9.59 | 220 | 2588 | 6.7694 | 16.3594 | 7.3894 | 0.62
15098 | Devizes Mayenne Place SPS | 100 | 3.9815 | 5.8905 | - | 5.8905 | 342.7307 | 0.1 | 0.7523 | Devizes Webbs Lane STW | Devizes Webbs Lane STW | 413 | 0.028846 | 57518.251 | 3.346 | 112.19 | 117.77 | 118.76 | 220 | 342 | 3.346 | 122.106 | 9.916 | 6.57
11895 | Wells Wand Road SPS | 125 | 3.9815 | 9.2039 | - | 9.2039 | 313.7005 | 0.125 | 0.7523 | Wells . STW | Wells . STW | 413 | 0.028846 | 71897.8138 | 2.287 | - | - | - | - | - | 2.287 | - | - | -
14197 | Malmesbury Corston SPS | 110 | 3.9583 | 7.1275 | - | 7.1275 | 3987.378 | 0.11 | 0.7523 | Malmesbury . STW | Malmesbury . STW | 411 | 0.028846 | 63270.0761 | 34.3527 | 70.68 | 73.25 | 85.39 | 2984 | 3988 | 34.3527 | 119.7427 | 49.0627 | 14.71
14075 | Glastonbury North Load Bridge SPS | 100 | 3.9583 | 5.8905 | 3 | 3 | 566.5446 | 0.1 | 0.38314 | Glastonbury The Beckery SSTW | Glastonbury Porchestall SPS | 411 | 0.007482 | 29293.8047 | 1.4915 | 6.04 | 15.01 | 15.01 | - | 566 | 1.4915 | 16.5015 | 10.4615 | 8.97
14113 | Trudoxhill . SPS | 125 | 3.912 | 9.2039 | 6 | 6 | 1806.461 | 0.125 | 0.49042 | Nunney . STW | Nunney . STW | 406 | 0.012259 | 46870.0875 | 5.7214 | 89.43 | 144.66 | 144.7 | 1800 | 1802 | 5.7214 | 150.4214 | 60.9914 | 55.27
15122 | Enford Long Street SPS | 120 | 3.912 | 8.4823 | - | 8.4823 | 1105.844 | 0.12 | 0.7523 | Netheravon . STW | Enford Coombe SPS | 406 | 0.028846 | 69021.9012 | 8.5028 | 85.94 | 99.36 | 99.64 | 1104 | 1106 | 8.5028 | 108.1428 | 22.2028 | 13.7
15328 | Crewkerne Wadham Park SPS | 120 | 3.912 | 8.4823 | - | 8.4823 | 271.7873 | 0.12 | 0.7523 | Merriott B3165 STW | Merriott B3165 STW | 406 | 0.028846 | 69021.9012 | 2.0898 | 77.92 | 87.9 | 87.96 | 266 | 272 | 2.0898 | 90.0498 | 12.1298 | 10.04
14087 | West Lydford . SPS | 100 | 3.912 | 5.8905 | - | 5.8905 | 424.5279 | 0.1 | 0.7523 | Lydford Track Off High Street STW | Lydford Track Off High Street STW | 406 | 0.028846 | 57518.251 | 4.1445 | 19.03 | 28.45 | 29.23 | 384 | 412 | 4.1445 | 33.3745 | 14.3445 | 10.2
15392 | Chedzoy Ward Lane SPS | 125 | 3.912 | 9.2039 | - | 9.2039 | 610.8821 | 0.125 | 0.7523 | Chilton Trinity . STW | Bridgwater Bradney Bridge SPS | 406 | 0.028846 | 71897.8138 | 4.4535 | 6.18 | 4.47 | 7.23 | 172 | 610 | 4.4535 | 11.6835 | 5.5035 | 1.05
14268 | Wareham North Bridge SPS | 200 | 3.912 | 23.5619 | - | 23.5619 | 315.8415 | 0.2 | 0.7523 | Wareham Keysworth Drive STW | Wareham Keysworth Drive STW | 406 | 0.028846 | 115036.502 | 1.254 | 2.2 | 2.14 | 3.39 | 124 | 312 | 1.254 | 4.644 | 2.444 | 1.19
15093 | Seend Barge Inn SPS | 125 | 3.8889 | 9.2039 | - | 9.2039 | 1266.6865 | 0.125 | 0.7523 | Seend . STW | Seend . STW | 404 | 0.028846 | 71897.8138 | 9.2345 | 48.27 | 94.1 | 97.11 | 966 | 1266 | 9.2345 | 106.3445 | 58.0745 | 48.84
15218 | Burley Mill Lawn SPS | 160 | 3.8889 | 15.0796 | - | 15.0796 | 1556.1194 | 0.16 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Burley Esdaile Lane SPS | 404 | 0.028846 | 92029.2016 | 8.2348 | 41.67 | 53.89 | 53.89 | 1556 | 1556 | 8.2348 | 62.1248 | 20.4548 | 12.22
14244 | Swanage Durlston Road SPS | 125 | 3.8889 | 9.2039 | 11 | 11 | 274.9154 | 0.125 | 0.89911 | Swanage Marine Parade STW | Swanage Marine Parade STW | 404 | 0.041202 | 85928.4938 | 2.8421 | 39.83 | 57.88 | 58.21 | 254 | 274 | 2.8421 | 61.0521 | 21.2221 | 18.38
14359 | Newton Toney Village Hall Car Park SPS | 100 | 3.8657 | 5.8905 | - | 5.8905 | 2156.6758 | 0.1 | 0.7523 | Hurdcott . STW | Idmiston . SPS | 401 | 0.028846 | 57518.251 | 21.055 | 80.64 | 83.07 | 88.33 | 1746 | 2156 | 21.055 | 109.385 | 28.745 | 7.69
14262 | Bere Regis Sitterton SPS | 100 | 3.8657 | 5.8905 | - | 5.8905 | 353.6336 | 0.1 | 0.7523 | Blackheath . STW | Bere Regis Court Farm Southbrook SPS | 401 | 0.028846 | 57518.251 | 3.4524 | 35.97 | 46.59 | 46.59 | 348 | 348 | 3.4524 | 50.0424 | 14.0724 | 10.62
15066 | Wimborne Brook Road No 2 SPS | 100 | 3.8657 | 5.8905 | - | 5.8905 | 191.0733 | 0.1 | 0.7523 | Wimborne Brook Road STW | Wimborne Brook Road STW | 401 | 0.028846 | 57518.251 | 1.8654 | 17.7 | 17.35 | 17.89 | 16 | 192 | 1.8654 | 19.7554 | 2.0554 | 0.19
15521 | Radstock Victoria Square SPS | 120 | 3.8426 | 8.4823 | - | 8.4823 | 41.8214 | 0.12 | 0.7523 | Radstock Mill Lane STW | Radstock Mill Lane STW | 399 | 0.028846 | 69021.9012 | 0.32157 | 68.97 | 68.53 | 69.05 | 6 | 44 | 0.32157 | 69.3716 | 0.40157 | 0.08
15549 | Saltford Chelwood Road SPS | 100 | 3.8426 | 5.8905 | - | 5.8905 | 419.4943 | 0.1 | 0.7523 | Keynsham . STW | Keynsham . STW | 399 | 0.028846 | 57518.251 | 4.0954 | 31.42 | 37.44 | 37.51 | 296 | 414 | 4.0954 | 41.6054 | 10.1854 | 6.09
14263 | Corfe Castle Red Lane SPS | 150 | 3.8426 | 13.2536 | 18.3 | 18.3 | 166.2396 | 0.15 | 1.0387 | Corfe Castle Wytch Farm Road STW | Corfe Castle Studland Road SPS | 399 | 0.054994 | 119128.1391 | 1.8009 | 21.73 | 31.04 | 31.04 | 166 | 166 | 1.8009 | 32.8409 | 11.1109 | 9.31
17995 | Frampton Cotterell The Meads SPS | 100 | 3.8194 | 5.8905 | - | 5.8905 | 244.3276 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 396 | 0.028846 | 57518.251 | 2.3853 | 54.65 | 59.42 | 59.42 | 244 | 244 | 2.3853 | 61.8053 | 7.1553 | 4.77
14520 | Heywood Dursley Road SPS | 100 | 3.8194 | 5.8905 | - | 5.8905 | 1214.9987 | 0.1 | 0.7523 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 396 | 0.028846 | 57518.251 | 11.8617 | 45.7 | 50.97 | 51.06 | 1130 | 1214 | 11.8617 | 62.9217 | 17.2217 | 5.36
15299 | Kingsdon . SPS | 120 | 3.8194 | 8.4823 | 4.4 | 4.4 | 2134.2107 | 0.12 | 0.39024 | Somerton Barpool Lane STW | Charlton Mackerell Rookery Farm SPS | 396 | 0.0077617 | 35803.5391 | 4.5823 | 24.95 | 15.49 | 26.56 | 1940 | 2134 | 4.5823 | 31.1423 | 6.1923 | 1.61
15130 | Pewsey Wharf SPS | 120 | 3.7731 | 8.4823 | - | 8.4823 | 118.6074 | 0.12 | 0.7523 | Pewsey Salisbury Road STW | Pewsey Jubilee SPS | 392 | 0.028846 | 69021.9012 | 0.91197 | 131.7 | 130.56 | 131.95 | - | 116 | 0.91197 | 132.862 | 1.162 | 0.25
15184 | Acton Turville School Luckington Road SPS | 110 | 3.75 | 7.1275 | - | 7.1275 | 1564.1848 | 0.11 | 0.7523 | Great Badminton . STW | Great Badminton . STW | 389 | 0.028846 | 63270.0761 | 13.476 | 125.38 | 125.4 | 129.25 | 290 | 1566 | 13.476 | 142.726 | 17.346 | 3.87
14327 | Laverstock Ross Warmafoam SPS | 125 | 3.7268 | 9.2039 | - | 9.2039 | 278.2672 | 0.125 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 387 | 0.028846 | 71897.8138 | 2.0287 | 49.96 | 51.12 | 52.58 | 216 | 278 | 2.0287 | 54.6087 | 4.6487 | 2.62
15065 | Sturminster Marshall Station Road SPS | 160 | 3.7268 | 15.0796 | - | 15.0796 | 775.3507 | 0.16 | 0.7523 | Tarrant Crawford . STW | Sturminster Marshall Newton Road SPS | 387 | 0.028846 | 92029.2016 | 4.1031 | 24.43 | 24.73 | 25.9 | 256 | 782 | 4.1031 | 30.0031 | 5.5731 | 1.47
15382 | East Huntspill Hackness Road SPS | 100 | 3.7268 | 5.8905 | - | 5.8905 | 107.9413 | 0.1 | 0.7523 | West Huntspill STW | East Huntspill Withy Road SPS | 387 | 0.028846 | 57518.251 | 1.0538 | 5.05 | 5.14 | 5.37 | - | 108 | 1.0538 | 6.4238 | 1.3738 | 0.32
19537 | Pill Ham Green Hospital No.1 Station SPS | 100 | 3.7037 | 5.8905 | - | 5.8905 | 395.4745 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Pill Avon Road SPS | 384 | 0.028846 | 57518.251 | 3.8609 | 26.25 | 31.08 | 31.08 | 396 | 396 | 3.8609 | 34.9409 | 8.6909 | 4.83
14324 | Wylye Chequers Cottages SPS | 75 | 3.6805 | 3.3134 | - | 3.3134 | 1507.6426 | 0.075 | 0.7523 | Wishford Wilton Road STW | Hanging Langford . SPS | 382 | 0.028846 | 43138.6883 | 21.5267 | 72.32 | 73.89 | 74.32 | 1502 | 1508 | 21.5267 | 95.8467 | 23.5267 | 2
14247 | Lytchett Matravers Flowers Drove SPS | 150 | 3.6805 | 13.2536 | - | 13.2536 | 387.7411 | 0.15 | 0.7523 | Blackheath . STW | Lytchett Matravers Bulbury Lane SPS | 382 | 0.028846 | 86277.3765 | 2.2306 | 69.27 | 82.59 | 82.59 | - | 388 | 2.2306 | 84.8206 | 15.5506 | 13.32
15265 | Poole Canford School SPS | 150 | 3.6805 | 13.2536 | - | 13.2536 | 352.3108 | 0.15 | 0.7523 | Wimborne Brook Road STW | Canford Magna Canford Main SPS | 382 | 0.028846 | 86277.3765 | 2.0267 | 16.92 | 25.89 | 25.89 | 352 | 352 | 2.0267 | 27.9167 | 10.9967 | 8.97
14173 | Castle Combe . SPS | 150 | 3.6343 | 13.2536 | - | 13.2536 | 342.6286 | 0.15 | 0.7523 | Long Dean . STW | Long Dean . STW | 377 | 0.028846 | 86277.3765 | 1.971 | 76.57 | 86.7 | 88.47 | 220 | 342 | 1.971 | 90.441 | 13.871 | 11.9
15201 | Durweston Water Lane SPS | 100 | 3.6343 | 5.8905 | 7 | 7 | 680.7153 | 0.1 | 0.894 | Stourpaine . STW | Stourpaine . SPS | 377 | 0.040736 | 68352.211 | 9.3181 | 36.78 | 39.43 | 39.63 | 654 | 680 | 9.3181 | 48.9481 | 12.1681 | 2.85
15311 | Yeovil Mudford SPS | 150 | 3.6343 | 13.2536 | 9.3 | 9.3 | 1948.259 | 0.15 | 0.52788 | Yeovil Without Off Stone Lane STW | Yeovil Without Off Stone Lane STW | 377 | 0.014203 | 60540.5297 | 5.6161 | 20.97 | 69.24 | 69.36 | 1936 | 1940 | 5.6161 | 74.9761 | 54.0061 | 48.39
14382 | Bawdrip . SPS | 150 | 3.6343 | 13.2536 | - | 13.2536 | 406.8161 | 0.15 | 0.7523 | Chilton Trinity . STW | Bridgwater Bradney Bridge SPS | 377 | 0.028846 | 86277.3765 | 2.3403 | 5.9 | 6.23 | 8.07 | - | 406 | 2.3403 | 10.4103 | 4.5103 | 2.17
14488 | Monkton Farleigh Church Farm SPS | 170 | 3.6111 | 17.0235 | - | 17.0235 | 1211.4789 | 0.17 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 375 | 0.028846 | 97781.0267 | 5.9284 | 137.93 | 192.04 | 199.45 | - | 1210 | 5.9284 | 205.3784 | 67.4484 | 61.52
15431 | Stone Courtmead Estate SPS | 100 | 3.6111 | 5.8905 | - | 5.8905 | 353.3247 | 0.1 | 0.7523 | Michaelwood . STW | Stone Old Mill SPS | 375 | 0.028846 | 57518.251 | 3.4494 | 25 | 26.3 | 26.3 | 354 | 354 | 3.4494 | 29.7494 | 4.7494 | 1.3
19773 | Weymouth Douglas Road SPS | 100 | 3.6111 | 5.8905 | - | 5.8905 | 20.9283 | 0.1 | 0.7523 | Weymouth . STW | Wyke Regis Hillcrest Road SPS | 375 | 0.028846 | 57518.251 | 0.20432 | 5.13 | 5.49 | 5.49 | 20 | 20 | 0.20432 | 5.6943 | 0.56432 | 0.36
19058 | Bristol Robertson Drive Bristol SPS | 100 | 3.588 | 5.8905 | - | 5.8905 | 366.6698 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Riverside St Annes SPS | 372 | 0.028846 | 57518.251 | 3.5797 | 13.01 | 19.36 | 19.39 | 364 | 366 | 3.5797 | 22.9697 | 9.9597 | 6.38
14164 | Foxham West End SPS | 100 | 3.588 | 5.8905 | - | 5.8905 | 1509.8495 | 0.1 | 0.7523 | Sutton Benger . STW | Christian Malford The Green Street SPS | 372 | 0.028846 | 57518.251 | 14.7402 | - | 53.19 | 53.88 | 962 | 1504 | 14.7402 | 68.6202 | - | -
15439 | Henlade . SPS | 100 | 3.5648 | 5.8905 | 4.8 | 4.8 | 597.0308 | 0.1 | 0.61303 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 370 | 0.019154 | 46870.0875 | 3.9085 | 15.12 | 24.42 | 25.27 | 514 | 598 | 3.9085 | 29.1785 | 14.0585 | 10.15
12705 | Amesbury Kingsgate Southern Link Road SPS | 150 | 3.5648 | 13.2536 | - | 13.2536 | 367.26 | 0.15 | 0.7523 | 13008amesbury Off Church Street STW | Amesbury Flower Lane SPS | 370 | 0.028846 | 86277.3765 | 2.1127 | - | - | - | - | - | 2.1127 | - | - | -
15686 | Compton Dundon Ham Lane SPS | 100 | 3.5417 | 5.8905 | - | 5.8905 | 543.4299 | 0.1 | 0.7523 | Somerton Barpool Lane STW | Compton Dundon Moor Close SPS | 368 | 0.028846 | 57518.251 | 5.3054 | 8.65 | 28.45 | 28.53 | 536 | 544 | 5.3054 | 33.8354 | 25.1854 | 19.88
14229 | Wareham West Mill Crescent SPS | 125 | 3.5417 | 9.2039 | 16.7 | 16.7 | 254.3214 | 0.125 | 1.365 | Wareham Keysworth Drive STW | Wareham Keysworth Drive STW | 368 | 0.094966 | 130455.0769 | 5.9787 | 2.71 | 8.56 | 8.64 | 252 | 254 | 5.9787 | 14.6187 | 11.9087 | 5.93
14108 | Mells . SPS | 100 | 3.5185 | 5.8905 | 11 | 11 | 311.2942 | 0.1 | 1.4049 | Mells . STW | Mells . STW | 365 | 0.10059 | 107410.6172 | 10.3695 | 91.24 | 96.97 | 98.87 | 152 | 310 | 10.3695 | 109.2395 | 17.9995 | 7.63
14598 | Lower Weare . SPS | 80 | 3.5185 | 3.7699 | - | 3.7699 | 2000.7941 | 0.08 | 0.7523 | Cheddar . STW | Cross Cross East SPS | 365 | 0.028846 | 46014.6008 | 26.2227 | 6.44 | 8.41 | 8.5 | - | 2000 | 26.2227 | 34.7227 | 28.2827 | 2.06
15566 | Clevedon Teignmouth Road SPS | 75 | 3.5185 | 3.3134 | - | 3.3134 | 7.0712 | 0.075 | 0.7523 | Kingston Seymour Back Lane STW | Clevedon Clevedon Main SPS | 365 | 0.028846 | 43138.6883 | 0.10097 | 5.99 | 5.87 | 6.03 | 4 | 8 | 0.10097 | 6.131 | 0.14097 | 0.04
15188 | Yate North Road SPS | 160 | 3.4722 | 15.0796 | 20 | 20 | 425.0255 | 0.16 | 0.99777 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 360 | 0.050741 | 122057.5196 | 3.9135 | 68.74 | 69.9 | 70.78 | - | 426 | 3.9135 | 74.6935 | 5.9535 | 2.04
14159 | Dauntsey St James SPS | 100 | 3.4722 | 5.8905 | - | 5.8905 | 399.7829 | 0.1 | 0.7523 | Sutton Benger . STW | Christian Malford Swalletts Gate SPS | 360 | 0.028846 | 57518.251 | 3.903 | 58.88 | 59.86 | 60.03 | 392 | 398 | 3.903 | 63.933 | 5.053 | 1.15
15567 | Brockley Chelvey Green SPS | 125 | 3.4722 | 9.2039 | - | 9.2039 | 262.4525 | 0.125 | 0.7523 | Kingston Seymour Back Lane STW | Kenn Kenn Pier SPS | 360 | 0.028846 | 71897.8138 | 1.9134 | 7.66 | 10.37 | 10.41 | 260 | 262 | 1.9134 | 12.3234 | 4.6634 | 2.75
14580 | Bristol Ullswater Close SPS | 150 | 3.4259 | 13.2536 | 12 | 12 | 305.7869 | 0.15 | 0.68114 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 356 | 0.023647 | 78116.8125 | 1.4485 | 41.12 | 44.52 | 45.3 | 282 | 306 | 1.4485 | 46.7485 | 5.6285 | 4.18
15656 | Ilminster Wharf Lane SPS | 100 | 3.4259 | 5.8905 | - | 5.8905 | 51.8502 | 0.1 | 0.7523 | Ilminster Ashwell STW | Ilminster Ashwell STW | 356 | 0.028846 | 57518.251 | 0.5062 | 35.26 | 35.18 | 35.48 | 16 | 52 | 0.5062 | 35.9862 | 0.7262 | 0.22
14596 | Long Load Meadow View SPS | 100 | 3.4259 | 5.8905 | - | 5.8905 | 1571.3326 | 0.1 | 0.7523 | Martock Hurst Bow STW | Martock Hurst Bow STW | 356 | 0.028846 | 57518.251 | 15.3405 | 24.6 | 30.19 | 30.32 | 1552 | 1572 | 15.3405 | 45.6605 | 21.0605 | 5.72
14311 | Tilshead Camp Road SPS | 100 | 3.4028 | 5.8905 | 12 | 12 | 867.0814 | 0.1 | 1.5326 | Tilshead Camp Road STW | Tilshead Camp Road STW | 353 | 0.11971 | 117175.2188 | 34.296 | 97.85 | 108.64 | 116.3 | 470 | 868 | 34.296 | 150.596 | 52.746 | 18.45
19082 | Wimborne Furzehill SPS | 120 | 3.4028 | 8.4823 | - | 8.4823 | 406.2764 | 0.12 | 0.7523 | Wimborne Brook Road STW | Wimborne East Borough Road SPS | 353 | 0.028846 | 69021.9012 | 3.1239 | 29.29 | 36.7 | 37.76 | 338 | 400 | 3.1239 | 40.8839 | 11.5939 | 8.47
15239 | Poole Poole Park SPS | 150 | 3.4028 | 13.2536 | - | 13.2536 | 626.885 | 0.15 | 0.7523 | Poole Cabot Lane STW | Poole East Quay Perry Gardens SPS | 353 | 0.028846 | 86277.3765 | 3.6063 | 2.37 | 5.95 | 6.39 | 518 | 626 | 3.6063 | 9.9963 | 7.6263 | 4.02
17121 | Verwood Ebblake Close SPS | 100 | 3.3796 | 5.8905 | - | 5.8905 | 152.7593 | 0.1 | 0.7523 | Palmersford . STW | Verwood Potterne Way SPS | 351 | 0.028846 | 57518.251 | 1.4913 | 22.32 | 24.55 | 24.55 | 152 | 152 | 1.4913 | 26.0413 | 3.7213 | 2.23
14438 | Upton Scudamore . SPS | 125 | 3.3565 | 9.2039 | - | 9.2039 | 2317.4006 | 0.125 | 0.7523 | Dilton Marsh . STW | Dilton Marsh . STW | 348 | 0.028846 | 71897.8138 | 16.8946 | 119.52 | 115.92 | 131.13 | - | 2318 | 16.8946 | 148.0246 | 28.5046 | 11.61
15241 | Poole Harkwood Drive SPS | 100 | 3.3565 | 5.8905 | - | 5.8905 | 392.2657 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Turlin Main Blandford Road Turlin Moor SPS | 348 | 0.028846 | 57518.251 | 3.8296 | 2.33 | 9.49 | 9.49 | 392 | 392 | 3.8296 | 13.3196 | 10.9896 | 7.16
13189 | Lympsham Worthy Crescent SPS | 100 | 3.3333 | 5.8905 | - | 5.8905 | 607.2616 | 0.1 | 0.7523 | West Huntspill STW | Lympsham Innsbruck SPS | 346 | 0.028846 | 57518.251 | 5.9285 | 6.22 | 5.37 | 6.22 | 0 | 608 | 5.9285 | 12.1485 | 5.9285 | 0
15817 | Yate Scott Way SPS | 80 | 3.3102 | 3.7699 | - | 3.7699 | 339.5437 | 0.08 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 344 | 0.028846 | 46014.6008 | 4.4501 | 83.92 | 83.73 | 83.96 | 12 | 340 | 4.4501 | 88.4101 | 4.4901 | 0.04
15036 | Christchurch Abingdon Drive SPS | 100 | 3.3102 | 5.8905 | - | 5.8905 | 122.1887 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Somerford Bridge SPS | 344 | 0.028846 | 57518.251 | 1.1929 | 23.59 | 29.49 | 29.49 | 122 | 122 | 1.1929 | 30.6829 | 7.0929 | 5.9
14079 | Meare Turnbridge SPS | 125 | 3.3102 | 9.2039 | - | 9.2039 | 1087.137 | 0.125 | 0.7523 | Meare . STW | Meare . STW | 344 | 0.028846 | 71897.8138 | 7.9256 | 4.73 | 12.79 | 12.79 | 1088 | 1088 | 7.9256 | 20.7156 | 15.9856 | 8.06
14106 | Norton St Philip Tellisford Lane SPS | 100 | 3.287 | 5.8905 | - | 5.8905 | 216.7143 | 0.1 | 0.7523 | Norton St Philip . STW | Norton St Philip . STW | 341 | 0.028846 | 57518.251 | 2.1157 | 117.22 | 120.08 | 120.13 | 212 | 216 | 2.1157 | 122.2457 | 5.0257 | 2.91
14563 | Frome Courts Barton Marston Lane SPS | 100 | 3.2639 | 5.8905 | 8 | 8 | 242.9466 | 0.1 | 1.0217 | Frome Welshmill Lane STW | Frome Welshmill Lane STW | 339 | 0.053206 | 78116.8125 | 4.3225 | 111.59 | 110.58 | 111.59 | - | 242 | 4.3225 | 115.9125 | 4.3225 | 0
15257 | Poole Poole Bridge Poole Quay SPS | 150 | 3.2639 | 13.2536 | 15 | 15 | 210.1652 | 0.15 | 0.85143 | Poole Cabot Lane STW | Poole East Quay Perry Gardens SPS | 339 | 0.036948 | 97646.0157 | 1.5408 | 1.62 | 1.73 | 1.81 | - | 210 | 1.5408 | 3.3508 | 1.7308 | 0.19
14426 | Paulton Goosard Bridge SPS | 225 | 3.2639 | 29.8206 | 50 | 50 | 231.5321 | 0.225 | 1.2614 | Paulton . STW | Paulton . STW | 339 | 0.081094 | 216991.1459 | 2.1829 | - | - | - | - | - | 2.1829 | - | - | -
19406 | Frampton Cotterell Park Farm Beesmoor Road SPS | 100 | 3.2407 | 5.8905 | - | 5.8905 | 148.7963 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 336 | 0.028846 | 57518.251 | 1.4527 | 54.08 | 57.22 | 57.6 | 146 | 148 | 1.4527 | 59.0527 | 4.9727 | 3.52
19103 | Yeovil Marsh SPS | 120 | 3.2407 | 8.4823 | - | 8.4823 | 1605.9084 | 0.12 | 0.7523 | Yeovil Without Off Stone Lane STW | Yeovil Without Off Stone Lane STW | 336 | 0.028846 | 69021.9012 | 12.3478 | 33.66 | 49.29 | 51.93 | 1428 | 1608 | 12.3478 | 64.2778 | 30.6178 | 18.27
19104 | Chilton Trinity Squares Road SPS | 100 | 3.2407 | 5.8905 | - | 5.8905 | 969.8321 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Chilton Street Saltlands SPS | 336 | 0.028846 | 57518.251 | 9.4682 | 5.63 | 6.2 | 6.65 | - | 970 | 9.4682 | 16.1182 | 10.4882 | 1.02
15650 | Bridgwater Shelthorn Grove SPS | 100 | 3.2407 | 5.8905 | - | 5.8905 | 147.6504 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Wills Road SPS | 336 | 0.028846 | 57518.251 | 1.4415 | 5.07 | 5.39 | 5.43 | - | 148 | 1.4415 | 6.8715 | 1.8015 | 0.36
15163 | Cromhall Townwell SPS | 100 | 3.2176 | 5.8905 | - | 5.8905 | 200.8188 | 0.1 | 0.7523 | Cromhall . STW | Cromhall Jubilee Lane SPS | 334 | 0.028846 | 57518.251 | 1.9605 | 59.34 | 65.22 | 65.22 | - | 200 | 1.9605 | 67.1805 | 7.8405 | 5.88
14405 | West Stafford Dorchester Road SPS | 100 | 3.2176 | 5.8905 | 14.1 | 14.1 | 1184.0183 | 0.1 | 1.8008 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 334 | 0.16528 | 137680.8821 | 64.4135 | 46.28 | 52.35 | 52.35 | 1184 | 1184 | 64.4135 | 116.7635 | 70.4835 | 6.07
15466 | Oake . SPS | 100 | 3.2176 | 5.8905 | - | 5.8905 | 1384.9658 | 0.1 | 0.7523 | Milverton STW | Milverton STW | 334 | 0.028846 | 57518.251 | 13.521 | 45.11 | 57.13 | 58.51 | 1274 | 1384 | 13.521 | 72.031 | 26.921 | 13.4
15310 | Aller . SPS | 125 | 3.2176 | 9.2039 | - | 9.2039 | 3113.9356 | 0.125 | 0.7523 | Langport Portfield Lane STW | Langport Westover SPS | 334 | 0.028846 | 71897.8138 | 22.7016 | 7.14 | 26.7 | 27.02 | 3080 | 3114 | 22.7016 | 49.7216 | 42.5816 | 19.88
15353 | Burnham-On-Sea Quantock Close SPS | 100 | 3.2176 | 5.8905 | - | 5.8905 | 236.8479 | 0.1 | 0.7523 | West Huntspill STW | Burnham-On-Sea Ashcott Drive SPS | 334 | 0.028846 | 57518.251 | 2.3123 | 5.43 | 5.34 | 5.59 | 52 | 236 | 2.3123 | 7.9023 | 2.4723 | 0.16
10135 | Durrington Primrose Place SPS | 100 | 3.2176 | 5.8905 | - | 5.8905 | 366.1759 | 0.1 | 0.7523 | Ratfyn . STW | Durrington Nags Head SPS | 334 | 0.028846 | 57518.251 | 3.5749 | - | - | - | - | - | 3.5749 | - | - | -
14440 | Dilton Marsh Pen Knapp SPS | 90 | 3.1713 | 4.7713 | 10 | 10 | 64.9467 | 0.09 | 1.5767 | Westbury STW | Westbury STW | 329 | 0.12671 | 108495.5729 | 3.1209 | 71.91 | 71.58 | 71.95 | 2 | 64 | 3.1209 | 75.0709 | 3.1609 | 0.04
11898 | Bridgwater Willow Down Primary Academy SPS | 90 | 3.1481 | 4.7713 | - | 4.7713 | 345.7792 | 0.09 | 0.7523 | Chilton Trinity . STW | Bridgwater Bristol Road SPS | 327 | 0.028846 | 51766.4259 | 3.8781 | 6.07 | 5.8 | 6.8 | 338 | 346 | 3.8781 | 10.6781 | 4.6081 | 0.73
14295 | Yeovilton Weir SPS | 100 | 3.1018 | 5.8905 | 5 | 5 | 2581.1511 | 0.1 | 0.63857 | Chilton Cantelo Hornsey Bridge STW | Chilton Cantelo Hornsey Bridge STW | 322 | 0.020783 | 48823.0078 | 18.2969 | 16.76 | 22.5 | 22.5 | 2570 | 2570 | 18.2969 | 40.7969 | 24.0369 | 5.74
15345 | Mark Queensway SPS | 100 | 3.1018 | 5.8905 | - | 5.8905 | 143.3018 | 0.1 | 0.7523 | West Huntspill STW | Mark . SPS | 322 | 0.028846 | 57518.251 | 1.399 | 5.68 | 5.12 | 6.01 | 48 | 144 | 1.399 | 7.409 | 1.729 | 0.33
14403 | Toller Porcorum Lower Road SPS | 100 | 3.0787 | 5.8905 | - | 5.8905 | 213.0321 | 0.1 | 0.7523 | Toller Porcorum Toller Lane STW | Toller Porcorum Toller Lane STW | 320 | 0.028846 | 57518.251 | 2.0798 | 109.43 | 109.42 | 109.56 | 206 | 214 | 2.0798 | 111.6398 | 2.2098 | 0.13
14547 | West Harptree . SPS | 100 | 3.0787 | 5.8905 | - | 5.8905 | 1659.0204 | 0.1 | 0.7523 | Ubley Frog Lane STW | Ubley Frog Lane STW | 320 | 0.028846 | 57518.251 | 16.1966 | 79.93 | 105.16 | 105.46 | 1664 | 1668 | 16.1966 | 121.6566 | 41.7266 | 25.53
14100 | Glastonbury Tor View SPS | 150 | 3.0787 | 13.2536 | - | 13.2536 | 261.7946 | 0.15 | 0.7523 | Glastonbury The Beckery SSTW | Glastonbury Porchestall SPS | 320 | 0.028846 | 86277.3765 | 1.506 | 10.44 | 27.45 | 27.78 | - | 262 | 1.506 | 29.286 | 18.846 | 17.34
17213 | Weston-Super-Mare Moor Lane Area 22 SPS | 125 | 3.0787 | 9.2039 | - | 9.2039 | 276.752 | 0.125 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Uphill . SPS | 320 | 0.028846 | 71897.8138 | 2.0176 | - | 5.27 | 5.9 | - | 268 | 2.0176 | 7.9176 | - | -
15133 | Oare Sunnyhill Lane SPS | 100 | 3.0555 | 5.8905 | - | 5.8905 | 777.5246 | 0.1 | 0.7523 | Pewsey Salisbury Road STW | Pewsey Wharf SPS | 317 | 0.028846 | 57518.251 | 7.5908 | 143.16 | 136.95 | 143.98 | 306 | 774 | 7.5908 | 151.5708 | 8.4108 | 0.82
14028 | Bristol Broomhill Road SPS | 225 | 3.0555 | 29.8206 | - | 29.8206 | 242.9382 | 0.225 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Dalby Ave SPS | 317 | 0.028846 | 129416.0648 | 0.82951 | 53.25 | 61.59 | 61.59 | 242 | 242 | 0.82951 | 62.4195 | 9.1695 | 8.34
19458 | Failand Beggar Bush Lane (Redwood Lodge Hotel) SPS | 100 | 3.0324 | 5.8905 | - | 5.8905 | 406.8833 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 315 | 0.028846 | 57518.251 | 3.9723 | 140.9 | 145.42 | 145.53 | - | 406 | 3.9723 | 149.5023 | 8.6023 | 4.63
15100 | North Newnton . SPS | 120 | 3.0324 | 8.4823 | 10 | 10 | 1765.5129 | 0.12 | 0.8869 | Upavon . STW | Upavon Andover Road SPS | 315 | 0.040092 | 81371.6797 | 18.7404 | 99.34 | 94.64 | 99.4 | 2 | 1766 | 18.7404 | 118.1404 | 18.8004 | 0.06
15155 | Westerleigh Henfield SPS | 150 | 3.0324 | 13.2536 | - | 13.2536 | 822.0334 | 0.15 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 315 | 0.028846 | 86277.3765 | 4.7289 | 58.45 | 84.98 | 84.98 | 816 | 816 | 4.7289 | 89.7089 | 31.2589 | 26.53
17169 | Sturminster Newton Field Close SPS | 110 | 3.0324 | 7.1275 | - | 7.1275 | 92.8656 | 0.11 | 0.7523 | Sturminster Newton Opp Rixon Close STW | Sturminster Newton Opp Rixon Close STW | 315 | 0.028846 | 63270.0761 | 0.80007 | 54.49 | 54.6 | 54.63 | - | 92 | 0.80007 | 55.4301 | 0.94007 | 0.14
15471 | Dorchester Mill Street Durnover Court SPS | 100 | 3.0324 | 5.8905 | - | 5.8905 | 22.9997 | 0.1 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 315 | 0.028846 | 57518.251 | 0.22454 | 53.13 | 53.08 | 53.23 | 8 | 22 | 0.22454 | 53.4545 | 0.32454 | 0.1
15796 | Trowbridge Jasmine Way SPS | 100 | 3.0324 | 5.8905 | - | 5.8905 | 91.6852 | 0.1 | 0.7523 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 315 | 0.028846 | 57518.251 | 0.8951 | 38.04 | 35.63 | 38.04 | 0 | 92 | 0.8951 | 38.9351 | 0.8951 | 0
19731 | Harmans Cross Transfer Station SPS | 125 | 3.0093 | 9.2039 | 7.5 | 7.5 | 1436.0933 | 0.125 | 0.61303 | Swanage Marine Parade STW | Swanage Marine Parade STW | 312 | 0.019154 | 58587.6094 | 7.0195 | 32.5 | 40.45 | 41.46 | 894 | 1436 | 7.0195 | 48.4795 | 15.9795 | 8.96
15585 | Bleadon Bleadon Bridge SPS | 150 | 3.0093 | 13.2536 | - | 13.2536 | 180.6395 | 0.15 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Bleadon Purn SPS | 312 | 0.028846 | 86277.3765 | 1.0392 | 6.35 | 7.09 | 7.25 | 10 | 180 | 1.0392 | 8.2892 | 1.9392 | 0.9
15046 | Christchurch Russell Drive Riverslea Estate SPS | 100 | 3.0093 | 5.8905 | - | 5.8905 | 4.4995 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Purewell SPS | 312 | 0.028846 | 57518.251 | 0.043927 | 2.51 | 2.56 | 2.56 | 4 | 4 | 0.043927 | 2.6039 | 0.093927 | 0.05
17813 | Yate Elswick Park SPS | - | 3.0093 | - | - | - | 216.0802 | - | - | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 312 | - | - | - | - | - | - | - | - | - | - | - | -
15176 | Old Sodbury Cross Hands SPS | 75 | 2.9861 | 3.3134 | - | 3.3134 | 483.2892 | 0.075 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 310 | 0.028846 | 43138.6883 | 6.9006 | 165.64 | 183.96 | 184.98 | - | 484 | 6.9006 | 191.8806 | 26.2406 | 19.34
14112 | Wanstrow . SPS | 160 | 2.9861 | 15.0796 | 7 | 7 | 306.3215 | 0.16 | 0.34922 | Wanstrow . STW | Wanstrow . STW | 310 | 0.0062158 | 42720.1318 | 0.36517 | 134.2 | 138.8 | 139.71 | 238 | 298 | 0.36517 | 140.0752 | 5.8752 | 5.51
15099 | Devizes Waiblingen Way SPS | 100 | 2.9861 | 5.8905 | - | 5.8905 | 187.6609 | 0.1 | 0.7523 | Devizes Webbs Lane STW | Devizes Webbs Lane STW | 310 | 0.028846 | 57518.251 | 1.8321 | 126.38 | 130.71 | 130.71 | 188 | 188 | 1.8321 | 132.5421 | 6.1621 | 4.33
14355 | Amesbury Countess Road SPS | 125 | 2.9861 | 9.2039 | - | 9.2039 | 356.2169 | 0.125 | 0.7523 | 13008amesbury Off Church Street STW | Amesbury Flower Lane SPS | 310 | 0.028846 | 71897.8138 | 2.5969 | 71.15 | 77.01 | 77.51 | 344 | 356 | 2.5969 | 80.1069 | 8.9569 | 6.36
15191 | Blandford Blandford Heights SPS | 150 | 2.963 | 13.2536 | - | 13.2536 | 227.0391 | 0.15 | 0.7523 | Tarrant Crawford . STW | Blandford Langton Road (Blandford No 1) SPS | 308 | 0.028846 | 86277.3765 | 1.3061 | 70.19 | 76.86 | 76.89 | 150 | 228 | 1.3061 | 78.1961 | 8.0061 | 6.7
15050 | Wimborne Winston Churchill SPS | 100 | 2.963 | 5.8905 | - | 5.8905 | 133.2818 | 0.1 | 0.7523 | Wimborne Brook Road STW | Wimborne Brook Road No 1 SPS | 308 | 0.028846 | 57518.251 | 1.3012 | 17.54 | 19.19 | 19.19 | 134 | 134 | 1.3012 | 20.4912 | 2.9512 | 1.65
15629 | Hambridge . SPS | 100 | 2.963 | 5.8905 | - | 5.8905 | 1137.6277 | 0.1 | 0.7523 | Ilminster Ashwell STW | Ilminster Westport SPS | 308 | 0.028846 | 57518.251 | 11.1063 | 9.42 | 25.61 | 26.06 | 862 | 1116 | 11.1063 | 37.1663 | 27.7463 | 16.64
19957 | Portishead Charlecombe Park SPS | 110 | 2.963 | 7.1275 | - | 7.1275 | 399.7619 | 0.11 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Black Nore (Nautical School) SPS | 308 | 0.028846 | 63270.0761 | 3.4441 | - | 56.75 | 61.9 | 134 | 398 | 3.4441 | 65.3441 | - | -
15083 | St Leonards Forest Edge Drive SPS | 150 | 2.9398 | 13.2536 | 10 | 10 | 375.7314 | 0.15 | 0.56762 | Palmersford . STW | St Leonards Craigside Road SPS | 305 | 0.016421 | 65097.3438 | 1.2473 | 17.85 | 20.79 | 21.14 | 304 | 376 | 1.2473 | 22.3873 | 4.5373 | 3.29
14360 | Alderbury Grimstead Road SPS | 150 | 2.9167 | 13.2536 | - | 13.2536 | 411.7201 | 0.15 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Alderbury Home Farm SPS | 303 | 0.028846 | 86277.3765 | 2.3685 | 68.69 | 74.62 | 77 | - | 412 | 2.3685 | 79.3685 | 10.6785 | 8.31
15406 | Durleigh Queenswood Lane Broadlands SPS | 100 | 2.9167 | 5.8905 | - | 5.8905 | 248.2178 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater West Quay Drawbridge SPS | 303 | 0.028846 | 57518.251 | 2.4233 | 25.82 | 29.37 | 29.37 | 248 | 248 | 2.4233 | 31.7933 | 5.9733 | 3.55
15321 | Huish Episcopi Courtfield No 2 SPS | 150 | 2.9167 | 13.2536 | - | 13.2536 | 307.3914 | 0.15 | 0.7523 | Langport Portfield Lane STW | Langport Westover SPS | 303 | 0.028846 | 86277.3765 | 1.7683 | 9.49 | 15.41 | 15.92 | 272 | 308 | 1.7683 | 17.6883 | 8.1983 | 6.43
15348 | Burnham-On-Sea Brent Road SPS | 100 | 2.9167 | 5.8905 | - | 5.8905 | 189.9899 | 0.1 | 0.7523 | West Huntspill STW | Burnham-On-Sea Braithwaite Place Off Berrow Road SPS | 303 | 0.028846 | 57518.251 | 1.8548 | 5.32 | 5.29 | 5.63 | 60 | 190 | 1.8548 | 7.4848 | 2.1648 | 0.31
17102 | Taunton Severn Drive SPS | 100 | 2.8935 | 5.8905 | - | 5.8905 | 117.0372 | 0.1 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 300 | 0.028846 | 57518.251 | 1.1426 | 13.84 | 13.35 | 13.84 | 0 | 118 | 1.1426 | 14.9826 | 1.1426 | 0
15440 | North Curry Main SPS | 80 | 2.8935 | 3.7699 | 8.3 | 8.3 | 311.7963 | 0.08 | 1.6563 | Stoke St Gregory . STW | North Curry Stoke Road SPS | 300 | 0.13982 | 101307.7412 | 19.2937 | 12.21 | 25.36 | 25.76 | 310 | 316 | 19.2937 | 45.0537 | 32.8437 | 13.55
14595 | Long Load Church Lane SPS | 100 | 2.8935 | 5.8905 | - | 5.8905 | 467.3355 | 0.1 | 0.7523 | Martock Hurst Bow STW | Long Load Meadow View SPS | 300 | 0.028846 | 57518.251 | 4.5625 | 9.41 | 24.38 | 24.38 | 468 | 468 | 4.5625 | 28.9425 | 19.5325 | 14.97
14342 | Teffont Evias . SPS | 150 | 2.8704 | 13.2536 | - | 13.2536 | 3875.7566 | 0.15 | 0.7523 | Tisbury Higher Chicksgrove STW | Tisbury Higher Chicksgrove STW | 298 | 0.028846 | 86277.3765 | 22.2961 | - | 88.6 | 117.37 | 2664 | 3870 | 22.2961 | 139.6661 | - | -
14468 | Melksham Semington Road SPS | 125 | 2.8472 | 9.2039 | 7 | 7 | 307.0027 | 0.125 | 0.57216 | Bowerhill Shails Lane STW | Bowerhill Shails Lane STW | 296 | 0.016685 | 54681.7688 | 1.3119 | 36.74 | 38.54 | 38.69 | 300 | 308 | 1.3119 | 40.0019 | 3.2619 | 1.95
14226 | Church Knowle Glebe Farm SPS | 100 | 2.8472 | 5.8905 | 8 | 8 | 933.8333 | 0.1 | 1.0217 | Corfe Castle Wytch Farm Road STW | Corfe Castle Studland Road SPS | 296 | 0.053206 | 78116.8125 | 16.6146 | 32.64 | 13.72 | 40.76 | 630 | 934 | 16.6146 | 57.3746 | 24.7346 | 8.12
15086 | Verwood Aspen Drive SPS | 100 | 2.8472 | 5.8905 | - | 5.8905 | 129.2619 | 0.1 | 0.7523 | Palmersford . STW | Verwood Potterne Way SPS | 296 | 0.028846 | 57518.251 | 1.2619 | 28.94 | 29.09 | 29.09 | - | 130 | 1.2619 | 30.3519 | 1.4119 | 0.15
15062 | Sturminster Marshall Church Street SPS | 100 | 2.8472 | 5.8905 | - | 5.8905 | 306.2448 | 0.1 | 0.7523 | Tarrant Crawford . STW | Sturminster Marshall Newton Road SPS | 296 | 0.028846 | 57518.251 | 2.9898 | 23.53 | 24.62 | 24.69 | 284 | 306 | 2.9898 | 27.6798 | 4.1498 | 1.16
15210 | Hale . SPS | 180 | 2.8241 | 19.0852 | - | 19.0852 | 796.6581 | 0.18 | 0.7523 | Downton Moot Lane STW | Downton Moot Lane STW | 293 | 0.028846 | 103532.8518 | 3.6217 | 91.6 | 113.75 | 113.85 | 786 | 796 | 3.6217 | 117.4717 | 25.8717 | 22.25
14211 | Royal Wootton Bassett Westbury Park SPS | 100 | 2.8241 | 5.8905 | - | 5.8905 | 301.6073 | 0.1 | 0.7523 | Royal Wootton Bassett . STW | Royal Wootton Bassett . STW | 293 | 0.028846 | 57518.251 | 2.9445 | 91.11 | 95.92 | 95.92 | 298 | 298 | 2.9445 | 98.8645 | 7.7545 | 4.81
15322 | Pitney . SPS | 150 | 2.8241 | 13.2536 | 5.3 | 5.3 | 1199.6355 | 0.15 | 0.30084 | Langport Portfield Lane STW | Langport Westover SPS | 293 | 0.0046128 | 34501.5922 | 1.1677 | 17 | 27.17 | 51.18 | 720 | 1200 | 1.1677 | 52.3477 | 35.3477 | 34.18
14171 | Chippenham Hardenhuish SPS | 110 | 2.7778 | 7.1275 | - | 7.1275 | 427.4541 | 0.11 | 0.7523 | Chippenham Blackwell Hams STW | Chippenham Blackwell Hams STW | 288 | 0.028846 | 63270.0761 | 3.6827 | 88 | 100.4 | 100.4 | 428 | 428 | 3.6827 | 104.0827 | 16.0827 | 12.4
14304 | Allington Old Inn SPS | 75 | 2.7778 | 3.3134 | 6.8 | 6.8 | 365.5631 | 0.075 | 1.5439 | Hurdcott . STW | Idmiston . SPS | 288 | 0.12149 | 88532.3875 | 21.4481 | 74.28 | 82.84 | 83.22 | 352 | 366 | 21.4481 | 104.6681 | 30.3881 | 8.94
15285 | Horsington Horsington Main SPS | 100 | 2.7778 | 5.8905 | - | 5.8905 | 819.7141 | 0.1 | 0.7523 | Wincanton . STW | North Cheriton Grove Lane SPS | 288 | 0.028846 | 57518.251 | 8.0026 | 69.44 | 81.58 | 82.34 | 812 | 820 | 8.0026 | 90.3426 | 20.9026 | 12.9
14237 | Winfrith Newburgh Winfrith Church SPS | 120 | 2.7778 | 8.4823 | - | 8.4823 | 354.3096 | 0.12 | 0.7523 | Wool . STW | East Knighton Blacknoll SPS | 288 | 0.028846 | 69021.9012 | 2.7243 | 41.61 | 42.62 | 42.88 | 346 | 354 | 2.7243 | 45.6043 | 3.9943 | 1.27
15564 | Kingston Seymour North SPS | 100 | 2.7778 | 5.8905 | - | 5.8905 | 535.5442 | 0.1 | 0.7523 | Kingston Seymour Back Lane STW | Kingston Seymour Back Lane STW | 288 | 0.028846 | 57518.251 | 5.2284 | 5.81 | 5.85 | 6.09 | - | 536 | 5.2284 | 11.3184 | 5.5084 | 0.28
15444 | Goosenford . SPS | 100 | 2.7546 | 5.8905 | - | 5.8905 | 484.702 | 0.1 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Bathpool Hyde Lane SPS | 286 | 0.028846 | 57518.251 | 4.732 | 32.79 | 49.39 | 49.72 | 478 | 484 | 4.732 | 54.452 | 21.662 | 16.93
17922 | Taunton Great Western Way No. 1 SPS | 100 | 2.7546 | 5.8905 | - | 5.8905 | 94.8172 | 0.1 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Silk Mills SPS | 286 | 0.028846 | 57518.251 | 0.92567 | 23.72 | 26.15 | 26.16 | - | 94 | 0.92567 | 27.0857 | 3.3657 | 2.44
19978 | Rooksbridge Bristol Road SPS | 125 | 2.7546 | 9.2039 | 8.5 | 8.5 | 844.0061 | 0.125 | 0.69476 | West Huntspill STW | Rooksbridge Mendip Road (Factory Road) Edingworth SPS | 286 | 0.024602 | 66399.2906 | 5.2667 | 5.8 | 5.67 | 6.92 | - | 844 | 5.2667 | 12.1867 | 6.3867 | 1.12
12370 | Westbury The Mead SPS | 125 | 2.7546 | 9.2039 | - | 9.2039 | 383.604 | 0.125 | 0.7523 | Westbury STW | Westbury STW | 286 | 0.028846 | 71897.8138 | 2.7966 | - | - | - | - | - | 2.7966 | - | - | -
14361 | East Knoyle Warminster Road SPS | 100 | 2.7315 | 5.8905 | - | 5.8905 | 236.7616 | 0.1 | 0.7523 | East Knoyle Millbrook Lane STW | East Knoyle Millbrook Lane STW | 284 | 0.028846 | 57518.251 | 2.3114 | 139.11 | 143.31 | 146.67 | - | 232 | 2.3114 | 148.9814 | 9.8714 | 7.56
14238 | Sandford Heath Cottages SPS | 225 | 2.7083 | 29.8206 | - | 29.8206 | 776.3793 | 0.225 | 0.7523 | Wareham Keysworth Drive STW | Wareham Keysworth Drive STW | 281 | 0.028846 | 129416.0648 | 2.6509 | - | 9.45 | 11.83 | 348 | 720 | 2.6509 | 14.4809 | - | -
14243 | Morden Cock And Bottle SPS | 150 | 2.6852 | 13.2536 | 13.7 | 13.7 | 917.7183 | 0.15 | 0.77764 | Blackheath . STW | Blackheath . STW | 279 | 0.030821 | 89183.361 | 5.633 | 34.37 | 32.5 | 48.03 | 426 | 918 | 5.633 | 53.663 | 19.293 | 13.66
15262 | Poole Park Lake Road SPS | 100 | 2.6852 | 5.8905 | - | 5.8905 | 383.3236 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole East Quay Perry Gardens SPS | 279 | 0.028846 | 57518.251 | 3.7423 | 1.09 | 5.37 | 5.37 | 384 | 384 | 3.7423 | 9.1123 | 8.0223 | 4.28
14102 | Kilmersdon . SPS | 125 | 2.6389 | 9.2039 | 5 | 5 | 1610.4032 | 0.125 | 0.40868 | Kilmersdon . STW | Kilmersdon . STW | 274 | 0.0085129 | 39058.4063 | 3.5837 | 83.42 | 92.72 | 92.72 | 192 | 192 | 3.5837 | 96.3037 | 12.8837 | 9.3
14187 | Little Somerford Manor Farm SPS | 115 | 2.6389 | 7.7902 | - | 7.7902 | 217.9825 | 0.115 | 0.7523 | Great Somerford . STW | Great Somerford . STW | 274 | 0.028846 | 66145.9887 | 1.7719 | 66.43 | 66.7 | 67.71 | - | 216 | 1.7719 | 69.4819 | 3.0519 | 1.28
14320 | Stapleford Pelican Inn SPS | 125 | 2.6389 | 9.2039 | - | 9.2039 | 1729.2717 | 0.125 | 0.7523 | Wishford Wilton Road STW | Stoford . SPS | 274 | 0.028846 | 71897.8138 | 12.6069 | 61.45 | 62.81 | 63.72 | 1678 | 1730 | 12.6069 | 76.3269 | 14.8769 | 2.27
14021 | Bristol Broadmead SPS | 100 | 2.6389 | 5.8905 | - | 5.8905 | 5.1152 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 274 | 0.028846 | 57518.251 | 0.049939 | 8.65 | 8.66 | 8.66 | - | 6 | 0.049939 | 8.7099 | 0.059939 | 0.01
15365 | Axbridge Walnut Farm SPS | 100 | 2.6389 | 5.8905 | - | 5.8905 | 254.9864 | 0.1 | 0.7523 | Cheddar . STW | Axbridge Old Stw Site SPS | 274 | 0.028846 | 57518.251 | 2.4894 | 7.57 | 6.24 | 8.07 | 70 | 250 | 2.4894 | 10.5594 | 2.9894 | 0.5
15211 | Burley Forest Road SPS | 125 | 2.6157 | 9.2039 | - | 9.2039 | 1221.0443 | 0.125 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Burley Esdaile Lane SPS | 272 | 0.028846 | 71897.8138 | 8.9018 | 51.53 | 53.87 | 59.93 | 832 | 1222 | 8.9018 | 68.8318 | 17.3018 | 8.4
14024 | Bristol Atwood Drive SPS | 75 | 2.6157 | 3.3134 | - | 3.3134 | 190.5902 | 0.075 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 272 | 0.028846 | 43138.6883 | 2.7213 | 7.66 | 9.79 | 9.79 | 190 | 190 | 2.7213 | 12.5113 | 4.8513 | 2.13
14138 | Colerne Thickwood SPS | 130 | 2.5926 | 9.9549 | - | 9.9549 | 1912.6158 | 0.13 | 0.7523 | Colerne . STW | Colerne . STW | 269 | 0.028846 | 74773.7263 | 13.2492 | 140.6 | 151.01 | 151.86 | 1896 | 1912 | 13.2492 | 165.1092 | 24.5092 | 11.26
14333 | East Knoyle Shaftesbury Road SPS | 75 | 2.5926 | 3.3134 | - | 3.3134 | 719.3283 | 0.075 | 0.7523 | East Knoyle Millbrook Lane STW | East Knoyle Millbrook Lane STW | 269 | 0.028846 | 43138.6883 | 10.2709 | 124.12 | 132.47 | 133.65 | 658 | 714 | 10.2709 | 143.9209 | 19.8009 | 9.53
14141 | Hilmarton Snow Hill SPS | 80 | 2.5926 | 3.7699 | - | 3.7699 | 660.5176 | 0.08 | 0.7523 | Hilmarton . STW | Hilmarton . STW | 269 | 0.028846 | 46014.6008 | 8.6568 | 79.31 | 80.47 | 85.03 | - | 660 | 8.6568 | 93.6868 | 14.3768 | 5.72
19569 | Melksham Forest Road SPS | 100 | 2.5926 | 5.8905 | - | 5.8905 | 47.7348 | 0.1 | 0.7523 | Melksham . STW | Melksham . STW | 269 | 0.028846 | 57518.251 | 0.46602 | 39.06 | 39.13 | 39.26 | 44 | 48 | 0.46602 | 39.726 | 0.66602 | 0.2
14444 | Wingfield Church Lane SPS | 90 | 2.5694 | 4.7713 | 2.9 | 2.9 | 1330.2565 | 0.09 | 0.45725 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 267 | 0.010656 | 31463.7162 | 5.6622 | 49.63 | 38.75 | 50.17 | - | 1330 | 5.6622 | 55.8322 | 6.2022 | 0.54
15416 | Berrow Meade Farm Coast Road SPS | 180 | 2.5694 | 19.0852 | - | 19.0852 | 750.1739 | 0.18 | 0.7523 | West Huntspill STW | West Huntspill STW | 267 | 0.028846 | 103532.8518 | 3.4103 | 7.56 | 6.98 | 9.19 | 554 | 750 | 3.4103 | 12.6003 | 5.0403 | 1.63
19834 | Street Strawberry Hill SPS | 100 | 2.5694 | 5.8905 | - | 5.8905 | 354.6004 | 0.1 | 0.7523 | Glastonbury The Beckery SSTW | Street Main SPS | 267 | 0.028846 | 57518.251 | 3.4619 | 4.89 | 12.74 | 12.74 | 354 | 354 | 3.4619 | 16.2019 | 11.3119 | 7.85
15625 | Wincanton Elm Drive SPS | 100 | 2.5463 | 5.8905 | - | 5.8905 | 310.4407 | 0.1 | 0.7523 | Wincanton . STW | Wincanton . STW | 264 | 0.028846 | 57518.251 | 3.0307 | 71.62 | 74.61 | 74.61 | 310 | 310 | 3.0307 | 77.6407 | 6.0207 | 2.99
15627 | Ilton Frost Lane SPS | 120 | 2.5463 | 8.4823 | 5.6 | 5.6 | 482.2974 | 0.12 | 0.49667 | Ilton Ashford Farm (Near) STW | Ilton Ashford Farm (Near) STW | 264 | 0.012573 | 45568.1406 | 1.6512 | 22.99 | 30.41 | 30.41 | - | 466 | 1.6512 | 32.0612 | 9.0712 | 7.42
15726 | Portishead Lake Grounds SPS | 150 | 2.5463 | 13.2536 | 8 | 8 | 129.3162 | 0.15 | 0.45409 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 264 | 0.01051 | 52077.875 | 0.27832 | 7.57 | 20.79 | 20.79 | 130 | 130 | 0.27832 | 21.0683 | 13.4983 | 13.22
19794 | Ferndown Nimrod Way SPS | 200 | 2.5231 | 23.5619 | - | 23.5619 | 512.4783 | 0.2 | 0.7523 | Palmersford . STW | Ferndown Ameysford Road SPS | 262 | 0.028846 | 115036.502 | 2.0347 | 24.89 | 26.75 | 26.75 | 512 | 512 | 2.0347 | 28.7847 | 3.8947 | 1.86
15030 | Christchurch Argyle Road SPS | 125 | 2.5231 | 9.2039 | - | 9.2039 | 290.0573 | 0.125 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Queens Road SPS | 262 | 0.028846 | 71897.8138 | 2.1146 | 1.99 | 2.55 | 2.59 | 288 | 290 | 2.1146 | 4.7046 | 2.7146 | 0.6
17354 | Frome Commerce Park SPS | 250 | 2.5 | 36.8155 | - | 36.8155 | 2893.5619 | 0.25 | 0.7523 | Frome Welshmill Lane STW | Frome Welshmill Lane STW | 260 | 0.028846 | 143795.6275 | 8.6369 | 90.8 | 90.8 | 99.21 | 630 | 1260 | 8.6369 | 107.8469 | 17.0469 | 8.41
15214 | Thorney Hill Whitelands SPS | 150 | 2.5 | 13.2536 | - | 13.2536 | 318.781 | 0.15 | 0.7523 | Christchurch Stoney Lane STW | Bransgore Wiltshire Gardens SPS | 260 | 0.028846 | 86277.3765 | 1.8339 | 57.62 | 71.82 | 72.65 | - | 318 | 1.8339 | 74.4839 | 16.8639 | 15.03
19405 | Verwood Albion Way (The Sylvans Development) SPS | 100 | 2.5 | 5.8905 | - | 5.8905 | 57.9631 | 0.1 | 0.7523 | Palmersford . STW | Verwood Potterne Way SPS | 260 | 0.028846 | 57518.251 | 0.56588 | 35.67 | 37.23 | 37.23 | 58 | 58 | 0.56588 | 37.7959 | 2.1259 | 1.56
15661 | Wrington Garstons SPS | 100 | 2.5 | 5.8905 | - | 5.8905 | 216.7168 | 0.1 | 0.7523 | Wrington STW | Wrington STW | 260 | 0.028846 | 57518.251 | 2.1157 | 14.62 | 16.84 | 16.85 | 214 | 216 | 2.1157 | 18.9657 | 4.3457 | 2.23
19994 | Amesbury Married Quarters (Boscombe Down) SPS | 150 | 2.4768 | 13.2536 | - | 13.2536 | 544.0715 | 0.15 | 0.7523 | 13008amesbury Off Church Street STW | Amesbury Flower Lane SPS | 257 | 0.028846 | 86277.3765 | 3.1299 | 102.63 | 115.38 | 115.42 | 516 | 544 | 3.1299 | 118.5499 | 15.9199 | 12.79
15054 | Verwood Blackmoor Road SPS | 100 | 2.4768 | 5.8905 | - | 5.8905 | 507.1404 | 0.1 | 0.7523 | Palmersford . STW | Verwood Potterne Way SPS | 257 | 0.028846 | 57518.251 | 4.9511 | 23.01 | 24.55 | 25 | 208 | 508 | 4.9511 | 29.9511 | 6.9411 | 1.99
15302 | Yeovil St Johns Road SPS | 80 | 2.4537 | 3.7699 | - | 3.7699 | 74.2885 | 0.08 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Sherborne Road (Pen Mill) STW | 255 | 0.028846 | 46014.6008 | 0.97363 | 54.22 | 59.2 | 59.2 | 74 | 74 | 0.97363 | 60.1736 | 5.9536 | 4.98
14080 | Henton Ford Lane SPS | 100 | 2.4537 | 5.8905 | - | 5.8905 | 550.3095 | 0.1 | 0.7523 | Wookey . STW | Wookey . STW | 255 | 0.028846 | 57518.251 | 5.3725 | 16.49 | 17.36 | 18.81 | 160 | 550 | 5.3725 | 24.1825 | 7.6925 | 2.32
15426 | Newport South SPS | 115 | 2.4537 | 7.7902 | - | 7.7902 | 1911.9328 | 0.115 | 0.7523 | Michaelwood . STW | Michaelwood . STW | 255 | 0.028846 | 66145.9887 | 15.5413 | 13.32 | 26.94 | 26.95 | - | 1890 | 15.5413 | 42.4913 | 29.1713 | 13.63
15350 | Highbridge Olive Terrace SPS | 100 | 2.4537 | 5.8905 | - | 5.8905 | 152.2955 | 0.1 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 255 | 0.028846 | 57518.251 | 1.4868 | 5.53 | 5.52 | 5.76 | 14 | 152 | 1.4868 | 7.2468 | 1.7168 | 0.23
14303 | Berwick St John . SPS | 100 | 2.4306 | 5.8905 | - | 5.8905 | 2831.7231 | 0.1 | 0.7523 | Tisbury Higher Chicksgrove STW | Donhead St Andrew . SPS | 252 | 0.028846 | 57518.251 | 27.6453 | 139.89 | 141.56 | 157.37 | - | 2840 | 27.6453 | 185.0153 | 45.1253 | 17.48
15097 | Pewsey Wootton Rivers SPS | 120 | 2.4306 | 8.4823 | - | 8.4823 | 2176.4032 | 0.12 | 0.7523 | Pewsey Salisbury Road STW | Pewsey Swan SPS | 252 | 0.028846 | 69021.9012 | 16.7344 | 131.44 | 136.89 | 147.57 | 710 | 2174 | 16.7344 | 164.3044 | 32.8644 | 16.13
18716 | Buckhorn Weston Filley Brook Kington Magna Rd SPS | 100 | 2.4306 | 5.8905 | - | 5.8905 | 1005.0991 | 0.1 | 0.7523 | Marnhull Common STW | Kington Magna Five Bridges SPS | 252 | 0.028846 | 57518.251 | 9.8125 | 66.97 | 74.06 | 74.91 | 900 | 1006 | 9.8125 | 84.7225 | 17.7525 | 7.94
15094 | Worton Orchard SPS | 100 | 2.4306 | 5.8905 | - | 5.8905 | 121.3784 | 0.1 | 0.7523 | Potterne . STW | Worton Mill Road SPS | 252 | 0.028846 | 57518.251 | 1.185 | 57.21 | 57.68 | 57.73 | - | 122 | 1.185 | 58.915 | 1.705 | 0.52
14457 | Bulkington Wickleaze SPS | 200 | 2.4306 | 23.5619 | 3.3 | 3.3 | 1784.2725 | 0.2 | 0.10536 | Keevil . STW | Keevil . STW | 252 | 0.00056583 | 16111.5926 | 0.16551 | 46.29 | 48.97 | 49.3 | 1736 | 1780 | 0.16551 | 49.4655 | 3.1755 | 3.01
14432 | Compton Dando Turnbridge SPS | 120 | 2.4306 | 8.4823 | 3.1 | 3.1 | 663.3258 | 0.12 | 0.27494 | Compton Dando . STW | Compton Dando . STW | 252 | 0.0038528 | 25225.2207 | 0.72709 | 21.21 | 30.84 | 37.19 | 570 | 664 | 0.72709 | 37.9171 | 16.7071 | 15.98
15314 | Upton Nr Langport SPS | 180 | 2.4306 | 19.0852 | 5 | 5 | 3800.946 | 0.18 | 0.19709 | Langport Portfield Lane STW | Huish Episcopi Pibsbury SPS | 252 | 0.0019798 | 27123.8932 | 1.3052 | 13.07 | 15.08 | 15.25 | 252 | 3800 | 1.3052 | 16.5552 | 3.4852 | 2.18
19300 | Stawell Moor Lane SPS | 100 | 2.4306 | 5.8905 | - | 5.8905 | 3155.6438 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Bradney Bridge SPS | 252 | 0.028846 | 57518.251 | 30.8077 | 7.98 | 6.27 | 26.07 | 1332 | 3156 | 30.8077 | 56.8777 | 48.8977 | 18.09
15145 | Hallen Hallen Village SPS | 125 | 2.4306 | 9.2039 | - | 9.2039 | 950.6503 | 0.125 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Kingsweston Lane STW | 252 | 0.028846 | 71897.8138 | 6.9305 | 7.38 | 6.76 | 8.44 | 108 | 950 | 6.9305 | 15.3705 | 7.9905 | 1.06
15638 | Manningford No 4 Ps Pewsey SPS | 150 | 2.4074 | 13.2536 | - | 13.2536 | 2184.2504 | 0.15 | 0.7523 | Pewsey Salisbury Road STW | Pewsey Salisbury Road STW | 250 | 0.028846 | 86277.3765 | 12.5654 | 101.06 | 107.85 | 108.9 | 2124 | 2184 | 12.5654 | 121.4654 | 20.4054 | 7.84
14151 | Dauntsey The Green SPS | 80 | 2.4074 | 3.7699 | 5.6 | 5.6 | 484.7487 | 0.08 | 1.1175 | Sutton Benger . STW | Dauntsey St James SPS | 250 | 0.063649 | 68352.211 | 13.8063 | 59.09 | 58.94 | 64.43 | 372 | 478 | 13.8063 | 78.2363 | 19.1463 | 5.34
17163 | Trowbridge West Ashton Road SPS | 100 | 2.4074 | 5.8905 | - | 5.8905 | 199.5803 | 0.1 | 0.7523 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 250 | 0.028846 | 57518.251 | 1.9484 | 37.94 | 35.44 | 38.72 | 4 | 200 | 1.9484 | 40.6684 | 2.7284 | 0.78
19525 | Ilchester Blackthorne Close SPS | 100 | 2.4074 | 5.8905 | - | 5.8905 | 213.1121 | 0.1 | 0.7523 | Ilchester Pill Bridge Lane STW | Ilchester Ilchester Main SPS | 250 | 0.028846 | 57518.251 | 2.0806 | 20.9 | 23.1 | 23.1 | 208 | 208 | 2.0806 | 25.1806 | 4.2806 | 2.2
14129 | Ringwood Nags Head SPS | 100 | 2.4074 | 5.8905 | - | 5.8905 | 79.5067 | 0.1 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Hampshire Hatches Lane STW | 250 | 0.028846 | 57518.251 | 0.7762 | 13.7 | 12.16 | 13.97 | 72 | 80 | 0.7762 | 14.7462 | 1.0462 | 0.27
14073 | Street The Mead SPS | 150 | 2.4074 | 13.2536 | - | 13.2536 | 17.9192 | 0.15 | 0.7523 | Glastonbury The Beckery SSTW | Street Main SPS | 250 | 0.028846 | 86277.3765 | 0.10308 | 7.74 | 7.85 | 7.87 | 16 | 18 | 0.10308 | 7.9731 | 0.23308 | 0.13
15156 | Tormarton Marshfield Road SPS | 100 | 2.3843 | 5.8905 | - | 5.8905 | 2679.8024 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Old Sodbury Cross Hands SPS | 248 | 0.028846 | 57518.251 | 26.1622 | 159.79 | 173.59 | 181.21 | - | 2680 | 26.1622 | 207.3722 | 47.5822 | 21.42
14212 | Burton . SPS | 100 | 2.3843 | 5.8905 | - | 5.8905 | 85.7754 | 0.1 | 0.7523 | Burton . STW | Burton . STW | 248 | 0.028846 | 57518.251 | 0.8374 | 111.62 | 110.9 | 111.68 | 24 | 88 | 0.8374 | 112.5174 | 0.8974 | 0.06
15101 | Patney Patney Weir SPS | 120 | 2.3843 | 8.4823 | 2.9 | 2.9 | 722.1164 | 0.12 | 0.2572 | Marden . STW | Chirton Small Street SPS | 248 | 0.0033717 | 23597.7871 | 0.69696 | 105.79 | 115.5 | 117.01 | 604 | 722 | 0.69696 | 117.707 | 11.917 | 11.22
15725 | Wiveliscombe Ford Road (Lion D'Angers) SPS | 150 | 2.3843 | 13.2536 | - | 13.2536 | 107.1536 | 0.15 | 0.7523 | Wiveliscombe Hillsmoor STW | Wiveliscombe Hillsmoor STW | 248 | 0.028846 | 86277.3765 | 0.61642 | 101.12 | 103.7 | 103.7 | 104 | 104 | 0.61642 | 104.3164 | 3.1964 | 2.58
15216 | Sopley Ringwood Road SPS | 100 | 2.3843 | 5.8905 | - | 5.8905 | 871.214 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Burton Stony Lane SPS | 248 | 0.028846 | 57518.251 | 8.5054 | 6.65 | 8.59 | 10.5 | 342 | 872 | 8.5054 | 19.0054 | 12.3554 | 3.85
15370 | Westonzoyland Lakewall Road SPS | 100 | 2.3843 | 5.8905 | 9 | 9 | 361.2974 | 0.1 | 1.1494 | Chilton Trinity . STW | Westonzoyland . SPS | 248 | 0.067338 | 87881.4141 | 8.1039 | 4.76 | 7.05 | 7.05 | 362 | 362 | 8.1039 | 15.1539 | 10.3939 | 2.29
12299 | Salisbury Hampton Park Private SPS | 125 | 2.3843 | 9.2039 | - | 9.2039 | 214.2671 | 0.125 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 248 | 0.028846 | 71897.8138 | 1.5621 | - | - | - | - | - | 1.5621 | - | - | -
15545 | Farrington Gurney Hill View SPS | 75 | 2.3611 | 3.3134 | - | 3.3134 | 635.5545 | 0.075 | 0.7523 | Paulton . STW | Paulton . STW | 245 | 0.028846 | 43138.6883 | 9.0747 | 111.7 | 121.72 | 121.99 | 596 | 622 | 9.0747 | 131.0647 | 19.3647 | 10.29
14503 | Melksham Brunswick Park / Junction Lane SPS | 100 | 2.3611 | 5.8905 | - | 5.8905 | 6.8259 | 0.1 | 0.7523 | Melksham . STW | Melksham . STW | 245 | 0.028846 | 57518.251 | 0.066639 | 38.32 | 38.47 | 38.47 | 6 | 6 | 0.066639 | 38.5366 | 0.21664 | 0.15
15333 | Penselwood Penn Mill SPS | 100 | 2.338 | 5.8905 | 14 | 14 | 690.3348 | 0.1 | 1.788 | Bourton Silton STW | Bourton Silton STW | 243 | 0.16294 | 136704.4219 | 37.0309 | 109.43 | 105.86 | 125.14 | 264 | 690 | 37.0309 | 162.1709 | 52.7409 | 15.71
14232 | Church Knowle Animal Sanctuary SPS | 80 | 2.338 | 3.7699 | 7 | 7 | 353.502 | 0.08 | 1.3969 | Corfe Castle Wytch Farm Road STW | Church Knowle Glebe Farm SPS | 243 | 0.099452 | 85440.2637 | 15.6266 | 50.15 | 59.4 | 60.28 | - | 354 | 15.6266 | 75.9066 | 25.7566 | 10.13
14286 | Lopen . SPS | 125 | 2.3148 | 9.2039 | 11 | 11 | 1132.1406 | 0.125 | 0.89911 | Longbridge Fosse Way STW | Longbridge Fosse Way STW | 240 | 0.041202 | 85928.4938 | 11.704 | 29.9 | 35 | 35 | - | 1132 | 11.704 | 46.704 | 16.804 | 5.1
15048 | Verwood Acacia Avenue SPS | 75 | 2.3148 | 3.3134 | 8 | 8 | 61.039 | 0.075 | 1.8164 | Palmersford . STW | Verwood Potterne Way SPS | 240 | 0.16816 | 104155.75 | 4.9377 | 24.75 | 25.32 | 25.51 | 50 | 62 | 4.9377 | 30.4477 | 5.6977 | 0.76
15584 | Kingston Seymour Rustic Farm (Kingston Seymour Central) SPS | 75 | 2.3148 | 3.3134 | - | 3.3134 | 255.5617 | 0.075 | 0.7523 | Kingston Seymour Back Lane STW | Kingston Seymour North SPS | 240 | 0.028846 | 43138.6883 | 3.649 | 5.96 | 5.73 | 5.96 | 0 | 256 | 3.649 | 9.609 | 3.649 | 0
14228 | Bovington Rhine Road SPS | 170 | 2.2685 | 17.0235 | - | 17.0235 | 15.0805 | 0.17 | 0.7523 | Wool . STW | Bovington Terminal SPS | 236 | 0.028846 | 97781.0267 | 0.073797 | 34.63 | 34.74 | 34.74 | 16 | 16 | 0.073797 | 34.8138 | 0.1838 | 0.11
15965 | Bristol St Georges Avenue Crews Hole Road SPS | 100 | 2.2685 | 5.8905 | - | 5.8905 | 74.657 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Norton St Philip Tellisford Lane SPS | 236 | 0.028846 | 57518.251 | 0.72886 | 12.04 | 14.09 | 14.09 | 74 | 74 | 0.72886 | 14.8189 | 2.7789 | 2.05
14605 | Upton Pony Drive SPS | - | 2.2685 | - | - | - | 281.3931 | - | - | Lytchett Minster Lytchett Bay STW | Upton Moorlands Way SPS | 236 | - | - | - | 9.02 | 18.18 | 18.19 | 278 | 282 | - | - | - | 9.17
12710 | Chipping Sodbury Quarry Bank SPS | - | 2.2685 | - | - | - | 187.3847 | - | - | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 236 | - | - | - | - | - | - | - | - | - | - | - | -
14047 | Coate Spaniels Bridge SPS | 100 | 2.2454 | 5.8905 | 7.4 | 7.4 | 821.6089 | 0.1 | 0.94508 | All Cannings Lower Mill Farm STW | All Cannings Lower Mill Farm STW | 233 | 0.045524 | 72258.0516 | 12.5425 | 121.18 | 117.89 | 123.25 | 182 | 820 | 12.5425 | 135.7925 | 14.6125 | 2.07
14162 | Malmesbury Burton Hill SPS | 100 | 2.2454 | 5.8905 | 8 | 8 | 245.5773 | 0.1 | 1.0217 | Malmesbury . STW | Malmesbury St Johns Street SPS | 233 | 0.053206 | 78116.8125 | 4.3693 | 74.12 | 79.06 | 79.18 | - | 246 | 4.3693 | 83.5493 | 9.4293 | 5.06
15397 | Stawell Ford Lane SPS | 100 | 2.2222 | 5.8905 | 3 | 3 | 710.2203 | 0.1 | 0.38314 | Chilton Trinity . STW | Stawell Moor Lane SPS | 231 | 0.007482 | 29293.8047 | 1.8697 | 12.35 | 9.2 | 18.12 | 320 | 712 | 1.8697 | 19.9897 | 7.6397 | 5.77
14181 | Royal Wootton Bassett Hook Dianmer Close SPS | 100 | 2.1991 | 5.8905 | - | 5.8905 | 851.8984 | 0.1 | 0.7523 | Royal Wootton Bassett . STW | Royal Wootton Bassett . STW | 228 | 0.028846 | 57518.251 | 8.3168 | 131.58 | 136.17 | 136.3 | 844 | 848 | 8.3168 | 144.6168 | 13.0368 | 4.72
14442 | Westbury Hawkeridge Park SPS | 200 | 2.1991 | 23.5619 | - | 23.5619 | 547.5503 | 0.2 | 0.7523 | Westbury STW | Westbury STW | 228 | 0.028846 | 115036.502 | 2.174 | 63.79 | 62.27 | 67.12 | 436 | 548 | 2.174 | 69.294 | 5.504 | 3.33
14486 | Bradford-On-Avon Springfield SPS | 100 | 2.1991 | 5.8905 | - | 5.8905 | 203.5607 | 0.1 | 0.7523 | Bradford-On-Avon . STW | Bradford-On-Avon Barton Farm Terminal P Stn SPS | 228 | 0.028846 | 57518.251 | 1.9873 | 46.41 | 45.06 | 47.37 | 8 | 204 | 1.9873 | 49.3573 | 2.9473 | 0.96
15221 | Bransgore Neacroft No 3 SPS | 125 | 2.1991 | 9.2039 | - | 9.2039 | 586.5506 | 0.125 | 0.7523 | Christchurch Stoney Lane STW | Bransgore Wiltshire Gardens SPS | 228 | 0.028846 | 71897.8138 | 4.2761 | 18.81 | 18.35 | 22.56 | 394 | 586 | 4.2761 | 26.8361 | 8.0261 | 3.75
14169 | Grittleton Foscote SPS | 125 | 2.1759 | 9.2039 | - | 9.2039 | 564.0441 | 0.125 | 0.7523 | Grittleton Woodmans Lodge SPS | Grittleton Woodmans Lodge SPS | 226 | 0.028846 | 71897.8138 | 4.1121 | 109.1 | 110.13 | 110.13 | - | 504 | 4.1121 | 114.2421 | 5.1421 | 1.03
19510 | Kingsbury Episcopi Stembridge (New) SPS | 100 | 2.1759 | 5.8905 | - | 5.8905 | 560.8288 | 0.1 | 0.7523 | Martock Hurst Bow STW | Kingsbury Episcopi . SPS | 226 | 0.028846 | 57518.251 | 5.4752 | 15.21 | 25.17 | 25.29 | 494 | 560 | 5.4752 | 30.7652 | 15.5552 | 10.08
15390 | Burnham-On-Sea Westfield Drive SPS | 100 | 2.1759 | 5.8905 | - | 5.8905 | 210.2051 | 0.1 | 0.7523 | West Huntspill STW | Burnham-On-Sea Rectory Drive SPS | 226 | 0.028846 | 57518.251 | 2.0522 | 6.14 | 6.13 | 6.29 | 198 | 210 | 2.0522 | 8.3422 | 2.2022 | 0.15
14251 | Upton Tree Hamlets SPS | 100 | 2.1759 | 5.8905 | - | 5.8905 | 120.252 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Turlin Main Blandford Road Turlin Moor SPS | 226 | 0.028846 | 57518.251 | 1.174 | 1.71 | 1.79 | 2.3 | - | 120 | 1.174 | 3.474 | 1.764 | 0.59
13138 | Grittleton Woodmans Lodge SPS | 160 | 2.1759 | 15.0796 | - | 15.0796 | 5139.7985 | 0.16 | 0.7523 | Grittleton Woodmans Lodge SPS | - | 226 | 0.028846 | 92029.2016 | 27.1993 | - | - | - | - | - | 27.1993 | - | - | -
19819 | Blagdon Hill Howleigh Lane SPS | 80 | 2.1528 | 3.7699 | - | 3.7699 | 360.6325 | 0.08 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Pitminster Weir SPS | 224 | 0.028846 | 46014.6008 | 4.7265 | 101.23 | 104.62 | 105.46 | 342 | 358 | 4.7265 | 110.1865 | 8.9565 | 4.23
15473 | Stratton Mill Lane SPS | 100 | 2.1528 | 5.8905 | - | 5.8905 | 140.0297 | 0.1 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Stratton Stratton Bridge SPS | 224 | 0.028846 | 57518.251 | 1.3671 | 69.14 | 70.99 | 71.21 | 108 | 140 | 1.3671 | 72.5771 | 3.4371 | 2.07
15212 | Ringwood Fairlie Park SPS | 100 | 2.1528 | 5.8905 | - | 5.8905 | 53.9907 | 0.1 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Hightown Crow Lane SPS | 224 | 0.028846 | 57518.251 | 0.5271 | 22.39 | 22.08 | 22.41 | 4 | 54 | 0.5271 | 22.9371 | 0.5471 | 0.02
14422 | Shurton . SPS | 110 | 2.1528 | 7.1275 | - | 7.1275 | 1200.4368 | 0.11 | 0.7523 | Stogursey . STW | Stogursey . STW | 224 | 0.028846 | 63270.0761 | 10.3422 | 18.49 | 26.32 | 27.13 | - | 1196 | 10.3422 | 37.4722 | 18.9822 | 8.64
15376 | Cross Cross West Old Coach Road SPS | 75 | 2.1528 | 3.3134 | - | 3.3134 | 128.8808 | 0.075 | 0.7523 | Cheddar . STW | Cross Cross East SPS | 224 | 0.028846 | 43138.6883 | 1.8402 | 6.8 | 10.31 | 10.45 | 124 | 128 | 1.8402 | 12.2902 | 5.4902 | 3.65
15671 | Poole Creekmoor Pit SPS | 200 | 2.1528 | 23.5619 | - | 23.5619 | 274.9173 | 0.2 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 224 | 0.028846 | 115036.502 | 1.0915 | 4.05 | 9.98 | 10 | 230 | 232 | 1.0915 | 11.0915 | 7.0415 | 5.95
15678 | Shaftesbury Wincombe Park SPS | 100 | 2.1296 | 5.8905 | - | 5.8905 | 382.4842 | 0.1 | 0.7523 | Shaftesbury Gears Mill STW | Shaftesbury Gears Mill STW | 221 | 0.028846 | 57518.251 | 3.7341 | 231.9 | 234.01 | 235.01 | - | 382 | 3.7341 | 238.7441 | 6.8441 | 3.11
14511 | Colerne Pinewood SPS | 100 | 2.1296 | 5.8905 | - | 5.8905 | 446.2736 | 0.1 | 0.7523 | Colerne . STW | Colerne Southwood Doe Housing Estate SPS | 221 | 0.028846 | 57518.251 | 4.3568 | 152.59 | 159.76 | 161 | - | 446 | 4.3568 | 165.3568 | 12.7668 | 8.41
14565 | Calne Derry Hill SPS | 100 | 2.1296 | 5.8905 | - | 5.8905 | 108.0249 | 0.1 | 0.7523 | Calne . STW | Calne . STW | 221 | 0.028846 | 57518.251 | 1.0546 | 117.65 | 119.83 | 119.83 | 108 | 108 | 1.0546 | 120.8846 | 3.2346 | 2.18
14161 | Compton Bassett The Pond SPS | 125 | 2.1296 | 9.2039 | 6 | 6 | 1797.3816 | 0.125 | 0.49042 | Compton Bassett . STW | Compton Bassett . STW | 221 | 0.012259 | 46870.0875 | 5.6927 | 99.16 | 94.93 | 99.37 | 114 | 1798 | 5.6927 | 105.0627 | 5.9027 | 0.21
15482 | Swyre Gorselands Caravan Park SPS | 50 | 2.1296 | 1.4726 | - | 1.4726 | 367.4015 | 0.05 | 0.7523 | Puncknowle Next To Gully Knap Farm STW | Puncknowle Next To Gully Knap Farm STW | 221 | 0.028846 | 28759.1255 | 9.0347 | 51.42 | 85.33 | 85.33 | - | 368 | 9.0347 | 94.3647 | 42.9447 | 33.91
15767 | Salisbury Hudson Road SPS | 100 | 2.1296 | 5.8905 | - | 5.8905 | 123.0752 | 0.1 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 221 | 0.028846 | 57518.251 | 1.2015 | 48.82 | 52.89 | 52.89 | 124 | 124 | 1.2015 | 54.0915 | 5.2715 | 4.07
14564 | Chippenham Monkton Park SPS | 120 | 2.1065 | 8.4823 | - | 8.4823 | 218.981 | 0.12 | 0.7523 | Chippenham Blackwell Hams STW | Chippenham Blackwell Hams STW | 219 | 0.028846 | 69021.9012 | 1.6837 | 45.84 | 48.47 | 48.5 | 212 | 214 | 1.6837 | 50.1837 | 4.3437 | 2.66
15811 | Melksham Awdry Avenue New SPS | 80 | 2.1065 | 3.7699 | - | 3.7699 | 43.4506 | 0.08 | 0.7523 | Melksham . STW | Melksham . STW | 219 | 0.028846 | 46014.6008 | 0.56947 | 37.68 | 37.9 | 38.91 | 24 | 44 | 0.56947 | 39.4795 | 1.7995 | 1.23
17585 | Pymore Thread Mill Lane SPS | 150 | 2.1065 | 13.2536 | - | 13.2536 | 74.3805 | 0.15 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 219 | 0.028846 | 86277.3765 | 0.42789 | 14.6 | 14.94 | 15.03 | 14 | 74 | 0.42789 | 15.4579 | 0.85789 | 0.43
12718 | Weston-Super-Mare Diamond Batch 2 SPS | - | 2.0833 | - | - | - | 518.7854 | - | - | Wick St Lawrence . STW | Weston-Super-Mare Diamond Batch SPS | 216 | - | - | - | - | - | - | - | - | - | - | - | -
14056 | West Lavington Duck Street SPS | 100 | 2.0602 | 5.8905 | - | 5.8905 | 219.9429 | 0.1 | 0.7523 | Lavington Woodbridge STW | Lavington Woodbridge STW | 214 | 0.028846 | 57518.251 | 2.1472 | 76.08 | 77.36 | 77.68 | 176 | 214 | 2.1472 | 79.8272 | 3.7472 | 1.6
14148 | Malmesbury Holloway Hill SPS | 120 | 2.0602 | 8.4823 | - | 8.4823 | 111.2551 | 0.12 | 0.7523 | Malmesbury . STW | Malmesbury St Johns Street SPS | 214 | 0.028846 | 69021.9012 | 0.85544 | 70.36 | 69.66 | 70.36 | - | 112 | 0.85544 | 71.2154 | 0.85544 | 0
15804 | Taunton Killams Lane SPS | 150 | 2.0602 | 13.2536 | - | 13.2536 | 310.6617 | 0.15 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 214 | 0.028846 | 86277.3765 | 1.7871 | 27.89 | 29.39 | 29.39 | 310 | 310 | 1.7871 | 31.1771 | 3.2871 | 1.5
15486 | West Bexington . SPS | 50 | 2.0602 | 1.4726 | 1.5 | 1.5 | 1899.4709 | 0.05 | 0.76628 | Puncknowle Next To Gully Knap Farm STW | Swyre Gorselands Caravan Park SPS | 214 | 0.029928 | 29293.8047 | 48.4214 | 9.21 | 85.33 | 85.33 | - | 1900 | 48.4214 | 133.7514 | 124.5414 | 76.12
17216 | Nether Stowey Stogursey Ln SPS | 100 | 2.037 | 5.8905 | - | 5.8905 | 276.4471 | 0.1 | 0.7523 | Nether Stowey . STW | Nether Stowey . STW | 212 | 0.028846 | 57518.251 | 2.6989 | 78.07 | 82.44 | 83.35 | - | 276 | 2.6989 | 86.0489 | 7.9789 | 5.28
14257 | Stoborough Tuckers Mill Close SPS | 100 | 2.037 | 5.8905 | - | 5.8905 | 326.8539 | 0.1 | 0.7523 | Wareham Keysworth Drive STW | Wareham Keysworth Drive STW | 212 | 0.028846 | 57518.251 | 3.191 | 5.9 | 9.88 | 9.88 | 326 | 326 | 3.191 | 13.071 | 7.171 | 3.98
12630 | Bransgore Heatherstone Grange SPS | - | 2.037 | - | - | - | 574.1981 | - | - | Christchurch Stoney Lane STW | Bransgore Wiltshire Gardens SPS | 212 | - | - | - | - | - | - | - | - | - | - | - | -
14040 | Leighterton . SPS | 95 | 2.0139 | 5.3162 | - | 5.3162 | 3134.6355 | 0.095 | 0.7523 | Didmarton . STW | Didmarton . STW | 209 | 0.028846 | 54642.3385 | 32.7386 | 168.16 | 118.66 | 168.16 | 0 | 3134 | 32.7386 | 200.8986 | 32.7386 | 0
17490 | Longham Ham Lane SPS | 125 | 2.0139 | 9.2039 | - | 9.2039 | 138.0573 | 0.125 | 0.7523 | Kinson New Road Northbourne STW | Longham Green Lane SPS | 209 | 0.028846 | 71897.8138 | 1.0065 | 13.73 | 14.42 | 14.48 | 38 | 138 | 1.0065 | 15.4865 | 1.7565 | 0.75
15568 | Tickenham West SPS | 100 | 2.0139 | 5.8905 | - | 5.8905 | 1314.7214 | 0.1 | 0.7523 | Kingston Seymour Back Lane STW | Tickenham East SPS | 209 | 0.028846 | 57518.251 | 12.8353 | 13.1 | 18.04 | 22.57 | 1160 | 1304 | 12.8353 | 35.4053 | 22.3053 | 9.47
15806 | Bridgwater Showground No2 SPS | 150 | 2.0139 | 13.2536 | - | 13.2536 | 15.281 | 0.15 | 0.7523 | Chilton Trinity . STW | Bridgwater Showground No1 SPS | 209 | 0.028846 | 86277.3765 | 0.087907 | 6.16 | 6.24 | 6.24 | 4 | 4 | 0.087907 | 6.3279 | 0.16791 | 0.08
15613 | Weston-Super-Mare Hutton Park Caravan Site SPS | 100 | 2.0139 | 5.8905 | - | 5.8905 | 35.9917 | 0.1 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Uphill . SPS | 209 | 0.028846 | 57518.251 | 0.35138 | 5.67 | 9.73 | 9.73 | 36 | 36 | 0.35138 | 10.0814 | 4.4114 | 4.06
14089 | Westhay . SPS | 80 | 2.0139 | 3.7699 | - | 3.7699 | 1169.0403 | 0.08 | 0.7523 | Meare . STW | Meare Oxenpill SPS | 209 | 0.028846 | 46014.6008 | 15.3216 | 4.68 | 5.86 | 6.08 | 1140 | 1170 | 15.3216 | 21.4016 | 16.7216 | 1.4
11886 | Wells Thompson Road SPS | 125 | 2.0139 | 9.2039 | - | 9.2039 | 529.093 | 0.125 | 0.7523 | Wells . STW | Wells . STW | 209 | 0.028846 | 71897.8138 | 3.8573 | - | - | - | - | - | 3.8573 | - | - | -
14049 | Pewsey Wilcot Lodge SPS | 100 | 1.9907 | 5.8905 | 4 | 4 | 2191.5589 | 0.1 | 0.51086 | Pewsey Salisbury Road STW | Pewsey Salisbury Road STW | 207 | 0.013301 | 39058.4063 | 10.0644 | 124.57 | 107.53 | 126.17 | 114 | 2192 | 10.0644 | 136.2344 | 11.6644 | 1.6
15283 | Wincanton Bayford SPS | 75 | 1.9907 | 3.3134 | 5 | 5 | 146.8261 | 0.075 | 1.1352 | Wincanton . STW | Wincanton . STW | 207 | 0.065686 | 65097.3438 | 4.6989 | 95.62 | 110.5 | 110.5 | 146 | 146 | 4.6989 | 115.1989 | 19.5789 | 14.88
17439 | Gaunts Common Horseshoes SPS | 90 | 1.9907 | 4.7713 | - | 4.7713 | 572.5086 | 0.09 | 0.7523 | Gaunts Common . STW | Gaunts Common . STW | 207 | 0.028846 | 51766.4259 | 6.421 | 56.52 | 64.19 | 64.19 | - | 572 | 6.421 | 70.611 | 14.091 | 7.67
15499 | West Knighton Knighton Lane SPS | 100 | 1.9907 | 5.8905 | - | 5.8905 | 538.1569 | 0.1 | 0.7523 | Broadmayne West Knighton Road STW | Broadmayne West Knighton Road STW | 207 | 0.028846 | 57518.251 | 5.2539 | 46.46 | 67.84 | 68.12 | 532 | 538 | 5.2539 | 73.3739 | 26.9139 | 21.66
15441 | Cheddon Fitzpaine Cheddon Farm SPS | 100 | 1.9907 | 5.8905 | - | 5.8905 | 335.1473 | 0.1 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Goosenford . SPS | 207 | 0.028846 | 57518.251 | 3.2719 | 25.81 | 40.08 | 40.08 | 328 | 328 | 3.2719 | 43.3519 | 17.5419 | 14.27
15340 | Bridgwater Bower Manor 7 Wilkins Road SPS | 100 | 1.9907 | 5.8905 | - | 5.8905 | 178.121 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Silver Springs Folletts Farm SPS | 207 | 0.028846 | 57518.251 | 1.7389 | 5.91 | 5.88 | 6.17 | 12 | 178 | 1.7389 | 7.9089 | 1.9989 | 0.26
19408 | Alton Barnes . SPS | 100 | 1.9676 | 5.8905 | - | 5.8905 | 595.8978 | 0.1 | 0.7523 | Pewsey Salisbury Road STW | Woodborough Ps1 . SPS | 204 | 0.028846 | 57518.251 | 5.8176 | 128.64 | 130.58 | 133.2 | 210 | 596 | 5.8176 | 139.0176 | 10.3776 | 4.56
15733 | Ringwood Headlands SPS | 150 | 1.9676 | 13.2536 | - | 13.2536 | 746.3456 | 0.15 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Bickerley SPS | 204 | 0.028846 | 86277.3765 | 4.2935 | 21.39 | 21.11 | 21.61 | 700 | 746 | 4.2935 | 25.9035 | 4.5135 | 0.22
14512 | Glastonbury Palmers Road SPS | 100 | 1.9676 | 5.8905 | - | 5.8905 | 87.5569 | 0.1 | 0.7523 | Glastonbury The Beckery SSTW | Glastonbury Porchestall SPS | 204 | 0.028846 | 57518.251 | 0.85479 | 7.76 | 8.25 | 8.37 | 84 | 88 | 0.85479 | 9.2248 | 1.4648 | 0.61
15609 | Clapton In Gordano . SPS | 150 | 1.9676 | 13.2536 | - | 13.2536 | 797.5343 | 0.15 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 204 | 0.028846 | 86277.3765 | 4.588 | 6.45 | 6.46 | 6.63 | 652 | 798 | 4.588 | 11.218 | 4.768 | 0.18
15021 | Christchurch Millhams Street SPS | 100 | 1.9676 | 5.8905 | - | 5.8905 | 47.2693 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Quomps No 2 SPS | 204 | 0.028846 | 57518.251 | 0.46148 | 2.31 | 2.82 | 2.97 | 36 | 48 | 0.46148 | 3.4315 | 1.1215 | 0.66
15045 | Christchurch Bridge Street SPS | 125 | 1.9676 | 9.2039 | - | 9.2039 | 231.5629 | 0.125 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Quomps No 2 SPS | 204 | 0.028846 | 71897.8138 | 1.6882 | 1.48 | 2.23 | 3.02 | - | 232 | 1.6882 | 4.7082 | 3.2282 | 1.54
15081 | Stoney Down Crumpet Farm Road SPS | 125 | 1.9444 | 9.2039 | - | 9.2039 | 1738.7987 | 0.125 | 0.7523 | Blackheath . STW | Lytchett Matravers Bulbury Lane SPS | 202 | 0.028846 | 71897.8138 | 12.6764 | 45.96 | 82.59 | 82.59 | - | 1738 | 12.6764 | 95.2664 | 49.3064 | 36.63
17167 | Shaftesbury Wincombe Lane SPS | 100 | 1.9213 | 5.8905 | - | 5.8905 | 11.882 | 0.1 | 0.7523 | Shaftesbury Gears Mill STW | Shaftesbury Gears Mill STW | 200 | 0.028846 | 57518.251 | 0.116 | 220.98 | 221.23 | 221.23 | - | 12 | 0.116 | 221.346 | 0.366 | 0.25
14039 | Shipton Moyne . SPS | 75 | 1.9213 | 3.3134 | - | 3.3134 | 3904.893 | 0.075 | 0.7523 | Tetbury . STW | Tetbury . STW | 200 | 0.028846 | 43138.6883 | 55.7556 | 99.67 | 96.36 | 109.35 | - | 3904 | 55.7556 | 165.1056 | 65.4356 | 9.68
14107 | Witham Friary . SPS | 75 | 1.9213 | 3.3134 | 5 | 5 | 2638.7315 | 0.075 | 1.1352 | Nunney . STW | Trudoxhill . SPS | 200 | 0.065686 | 65097.3438 | 84.4475 | 90.45 | 89.46 | 117.38 | 1712 | 2640 | 84.4475 | 201.8275 | 111.3775 | 26.93
15501 | Frampton Southover SPS | 80 | 1.9213 | 3.7699 | - | 3.7699 | 245.6235 | 0.08 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Frampton Muckleford SPS | 200 | 0.028846 | 46014.6008 | 3.2192 | 78.65 | 82.06 | 82.06 | 246 | 246 | 3.2192 | 85.2792 | 6.6292 | 3.41
14120 | Street Middle Brooks Road SPS | 100 | 1.9213 | 5.8905 | 6 | 6 | 183.8184 | 0.1 | 0.76628 | Glastonbury The Beckery SSTW | Street Main SPS | 200 | 0.029928 | 58587.6094 | 1.8604 | 40.53 | 42.53 | 42.6 | 176 | 180 | 1.8604 | 44.4604 | 3.9304 | 2.07
15450 | Norton Fitzwarren Langford Lane SPS | 50 | 1.9213 | 1.4726 | 1.7 | 1.7 | 1435.0684 | 0.05 | 0.86845 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Silk Mills SPS | 200 | 0.038441 | 33199.6453 | 46.7326 | 26.59 | 36.55 | 40.59 | 714 | 1436 | 46.7326 | 87.3226 | 60.7326 | 14
15728 | Taunton Killams Park SPS | 80 | 1.9213 | 3.7699 | - | 3.7699 | 121.6124 | 0.08 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 200 | 0.028846 | 46014.6008 | 1.5939 | 25.08 | 30.72 | 30.74 | 116 | 122 | 1.5939 | 32.3339 | 7.2539 | 5.66
14521 | East Lambrook . SPS | 80 | 1.9213 | 3.7699 | - | 3.7699 | 1730.8739 | 0.08 | 0.7523 | South Petherton North Street STW | South Petherton North Street STW | 200 | 0.028846 | 46014.6008 | 22.6851 | 17.07 | 28.03 | 34.16 | 838 | 1730 | 22.6851 | 56.8451 | 39.7751 | 17.09
15151 | Aust M48 Services SPS | 150 | 1.9213 | 13.2536 | - | 13.2536 | 590.4907 | 0.15 | 0.7523 | Aust . STW | Aust . STW | 200 | 0.028846 | 86277.3765 | 3.3969 | 15.99 | 38.67 | 38.67 | 590 | 590 | 3.3969 | 42.0669 | 26.0769 | 22.68
17476 | Orcheston . SPS | 110 | 1.8981 | 7.1275 | - | 7.1275 | 607.1246 | 0.11 | 0.7523 | Shrewton . STW | Shrewton Homanton SPS | 197 | 0.028846 | 63270.0761 | 5.2306 | 85.06 | 106.94 | 107.08 | 538 | 608 | 5.2306 | 112.3106 | 27.2506 | 22.02
15092 | Burbage Stibbs Green SPS | 120 | 1.875 | 8.4823 | - | 8.4823 | 227.9703 | 0.12 | 0.7523 | Pewsey Salisbury Road STW | Pewsey Swan SPS | 195 | 0.028846 | 69021.9012 | 1.7529 | 168.87 | 171.83 | 171.96 | - | 228 | 1.7529 | 173.7129 | 4.8429 | 3.09
14158 | Hullavington Raf Station SPS | 100 | 1.875 | 5.8905 | 4.8 | 4.8 | 414.6858 | 0.1 | 0.61303 | Sutton Benger . STW | Lower Stanton St Quintin . SPS | 195 | 0.019154 | 46870.0875 | 2.7147 | 86.71 | 94.7 | 94.7 | 418 | 418 | 2.7147 | 97.4147 | 10.7047 | 7.99
17372 | Holt Bussons Corner SPS | 110 | 1.875 | 7.1275 | - | 7.1275 | 575.9846 | 0.11 | 0.7523 | Holt Pond Head STW | Holt Pond Head STW | 195 | 0.028846 | 63270.0761 | 4.9623 | 35.38 | 33.98 | 42.37 | - | 576 | 4.9623 | 47.3323 | 11.9523 | 6.99
15434 | Newport North SPS | 100 | 1.875 | 5.8905 | - | 5.8905 | 551.0602 | 0.1 | 0.7523 | Michaelwood . STW | Newport South SPS | 195 | 0.028846 | 57518.251 | 5.3798 | 14.86 | 20.98 | 21.07 | - | 550 | 5.3798 | 26.4498 | 11.5898 | 6.21
15354 | Burnham-On-Sea St Peters Road SPS | 100 | 1.875 | 5.8905 | - | 5.8905 | 77.8002 | 0.1 | 0.7523 | West Huntspill STW | Burnham-On-Sea Ashcott Drive SPS | 195 | 0.028846 | 57518.251 | 0.75954 | 5.36 | 5.23 | 5.5 | 4 | 78 | 0.75954 | 6.2595 | 0.89954 | 0.14
19787 | Stour Row . SPS | 125 | 1.8518 | 9.2039 | 6 | 6 | 3635.9154 | 0.125 | 0.49042 | Marnhull Common STW | Marnhull Sodom Lane SPS | 192 | 0.012259 | 46870.0875 | 11.5157 | 65.64 | 58.54 | 65.85 | 186 | 3636 | 11.5157 | 77.3657 | 11.7257 | 0.21
15227 | Ringwood Poplar Way SPS | 100 | 1.8518 | 5.8905 | - | 5.8905 | 185.023 | 0.1 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Hightown Crow Lane SPS | 192 | 0.028846 | 57518.251 | 1.8063 | 20.82 | 20.99 | 20.99 | - | 186 | 1.8063 | 22.7963 | 1.9763 | 0.17
15425 | Sharpness Docks Road East SPS | 170 | 1.8518 | 17.0235 | - | 17.0235 | 613.0992 | 0.17 | 0.7523 | Sharpness . STW | Sharpness Docks West SPS | 192 | 0.028846 | 97781.0267 | 3.0002 | 18.68 | 13.46 | 20.58 | - | 614 | 3.0002 | 23.5802 | 4.9002 | 1.9
14599 | Cheddar Wedmore Road SPS | 100 | 1.8518 | 5.8905 | - | 5.8905 | 417.2298 | 0.1 | 0.7523 | Cheddar . STW | Cheddar . STW | 192 | 0.028846 | 57518.251 | 4.0733 | 8.03 | 13.44 | 13.54 | 404 | 418 | 4.0733 | 17.6133 | 9.5833 | 5.51
15160 | Pilning Fire Station SPS | 150 | 1.8518 | 13.2536 | - | 13.2536 | 439.2738 | 0.15 | 0.7523 | Redwick . STW | Pilning Pilning Church The Green SPS | 192 | 0.028846 | 86277.3765 | 2.527 | 6.9 | 9.67 | 10.59 | 356 | 440 | 2.527 | 13.117 | 6.217 | 3.69
14410 | Burton Bradstock Burton Southover SPS | 100 | 1.8518 | 5.8905 | 12 | 12 | 111.6041 | 0.1 | 1.5326 | Bridport Wych Farm STW | Burton Bradstock Burton Freshwater SPS | 192 | 0.11971 | 117175.2188 | 4.4143 | 6.59 | 6.61 | 6.63 | 110 | 112 | 4.4143 | 11.0443 | 4.4543 | 0.04
13284 | St Georges No 1 SPS | 125 | 1.8518 | 9.2039 | - | 9.2039 | 173.5092 | 0.125 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 192 | 0.028846 | 71897.8138 | 1.2649 | 5.41 | 5.96 | 6.29 | 66 | 174 | 1.2649 | 7.5549 | 2.1449 | 0.88
14053 | Erlestoke Erlestoke Park SPS | 100 | 1.8287 | 5.8905 | - | 5.8905 | 370.3586 | 0.1 | 0.7523 | Erlestoke Erlestoke Park STW | Erlestoke Erlestoke Park STW | 190 | 0.028846 | 57518.251 | 3.6157 | 79.46 | 80.69 | 80.69 | 368 | 368 | 3.6157 | 84.3057 | 4.8457 | 1.23
19460 | Wells Jocelyn Drive SPS | 150 | 1.8287 | 13.2536 | - | 13.2536 | 257.0067 | 0.15 | 0.7523 | Wells . STW | Wells . STW | 190 | 0.028846 | 86277.3765 | 1.4785 | 25.3 | 28.5 | 28.5 | 258 | 258 | 1.4785 | 29.9785 | 4.6785 | 3.2
15384 | Bridgwater Bristol Road No 1 Bcl SPS | - | 1.8287 | - | - | - | 44.1231 | - | - | Chilton Trinity . STW | Bridgwater Bristol Road SPS | 190 | - | - | - | 6.3 | 6.23 | 6.64 | 26 | 44 | - | - | - | 0.34
12697 | Lansdown Chelscombe Close SPS | - | 1.8287 | - | - | - | 478.9427 | - | - | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 190 | - | - | - | - | - | - | - | - | - | - | - | -
15114 | Oare High Street SPS | 100 | 1.8056 | 5.8905 | - | 5.8905 | 617.2145 | 0.1 | 0.7523 | Pewsey Salisbury Road STW | Oare Sunnyhill Lane SPS | 188 | 0.028846 | 57518.251 | 6.0257 | 149.7 | 148.21 | 151.32 | 118 | 618 | 6.0257 | 157.3457 | 7.6457 | 1.62
15067 | West Parley Christchurch Road SPS | 100 | 1.8056 | 5.8905 | - | 5.8905 | 562.0745 | 0.1 | 0.7523 | Kinson New Road Northbourne STW | West Parley Church Lane SPS | 188 | 0.028846 | 57518.251 | 5.4874 | 26.18 | 31.16 | 31.41 | - | 562 | 5.4874 | 36.8974 | 10.7174 | 5.23
14647 | Barrington Gibbs Lane SPS | - | 1.8056 | - | - | - | 456.658 | - | - | Ilminster Ashwell STW | Barrington West End View SPS | 188 | - | - | - | 18.88 | 22.69 | 22.81 | 430 | 456 | - | - | - | 3.93
15298 | Limington Main SPS | 80 | 1.8056 | 3.7699 | 4 | 4 | 796.257 | 0.08 | 0.79821 | Chilton Cantelo Hornsey Bridge STW | Yeovilton Weir SPS | 188 | 0.032474 | 48823.0078 | 11.7181 | 18.28 | 16.76 | 18.28 | 0 | 804 | 11.7181 | 29.9981 | 11.7181 | 0
15432 | Wanswell Farm Lane SPS | 120 | 1.8056 | 8.4823 | - | 8.4823 | 479.0196 | 0.12 | 0.7523 | Sharpness . STW | Sharpness Old Minster Road SPS | 188 | 0.028846 | 69021.9012 | 3.6832 | 15.42 | 24.75 | 26.38 | - | 476 | 3.6832 | 30.0632 | 14.6432 | 10.96
14085 | Coxley Coxley Ripple SPS | 90 | 1.8056 | 4.7713 | 6 | 6 | 389.2509 | 0.09 | 0.94603 | Wells . STW | Coxley Mill Lane SPS | 188 | 0.045615 | 65097.3438 | 6.8395 | 10.79 | 16.44 | 16.47 | 380 | 382 | 6.8395 | 23.3095 | 12.5195 | 5.68
17208 | Amesbury Maple Way SPS | 125 | 1.7824 | 9.2039 | - | 9.2039 | 184.9777 | 0.125 | 0.7523 | Ratfyn . STW | Amesbury Ratfyn Lane SPS | 185 | 0.028846 | 71897.8138 | 1.3485 | 98.5 | 103.12 | 103.12 | 184 | 184 | 1.3485 | 104.4685 | 5.9685 | 4.62
14505 | Langley Burrell Peckingell Lane SPS | 100 | 1.7824 | 5.8905 | - | 5.8905 | 1021.3959 | 0.1 | 0.7523 | Chippenham Blackwell Hams STW | Chippenham Blackwell Hams STW | 185 | 0.028846 | 57518.251 | 9.9716 | 59.26 | 72.89 | 72.89 | 1022 | 1022 | 9.9716 | 82.8616 | 23.6016 | 13.63
14210 | Pewsham London Road Also S0191 SPS | 150 | 1.7824 | 13.2536 | - | 13.2536 | 1048.4562 | 0.15 | 0.7523 | Chippenham Blackwell Hams STW | Chippenham Blackwell Hams STW | 185 | 0.028846 | 86277.3765 | 6.0315 | 55.18 | 65.86 | 66.19 | 1022 | 1048 | 6.0315 | 72.2215 | 17.0415 | 11.01
19935 | Bradford-On-Avon Greenland Mills SPS | 100 | 1.7824 | 5.8905 | - | 5.8905 | 291.0278 | 0.1 | 0.7523 | Bradford-On-Avon . STW | Bradford-On-Avon Barton Farm Terminal P Stn SPS | 185 | 0.028846 | 57518.251 | 2.8412 | 31.21 | 32.11 | 32.11 | 292 | 292 | 2.8412 | 34.9512 | 3.7412 | 0.9
15059 | West Moors Three Legged Cross SPS | 100 | 1.7824 | 5.8905 | - | 5.8905 | 217.79 | 0.1 | 0.7523 | Palmersford . STW | West Moors The Forest SPS | 185 | 0.028846 | 57518.251 | 2.1262 | 25.52 | 26.57 | 26.63 | - | 218 | 2.1262 | 28.7562 | 3.2362 | 1.11
15284 | Huish Episcopi Wagg Drove SPS | 150 | 1.7824 | 13.2536 | 3 | 3 | 775.6618 | 0.15 | 0.17029 | Langport Portfield Lane STW | Langport Portfield Lane STW | 185 | 0.0014779 | 19529.2031 | 0.25613 | 10.27 | 7.91 | 10.43 | 32 | 776 | 0.25613 | 10.6861 | 0.41613 | 0.16
15714 | Poole Wentworth Drive SPS | 100 | 1.7593 | 5.8905 | - | 5.8905 | 465.4302 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 183 | 0.028846 | 57518.251 | 4.5439 | 40.97 | 45.72 | 45.72 | - | 466 | 4.5439 | 50.2639 | 9.2939 | 4.75
11876 | Falfield Eastwood Park S105a SPS | 125 | 1.7593 | 9.2039 | - | 9.2039 | 1313.655 | 0.125 | 0.7523 | Leyhill Prison STW | Leyhill Prison STW | 183 | 0.028846 | 71897.8138 | 9.5769 | 28.06 | 34.43 | 35.02 | - | 1306 | 9.5769 | 44.5969 | 16.5369 | 6.96
15500 | Bradpole Fishweir Foul SPS | 100 | 1.7593 | 5.8905 | 7 | 7 | 108.6989 | 0.1 | 0.894 | Bridport Wych Farm STW | Bridport West Bay SPS | 183 | 0.040736 | 68352.211 | 1.488 | 13.97 | 18.92 | 18.92 | 108 | 108 | 1.488 | 20.408 | 6.438 | 4.95
14399 | Osmington Mills . SPS | 100 | 1.7593 | 5.89 | - |  | 512.6891 | 0.15 | 0.7523 | Osmington Mills . STW | Osmington Mills . STW | 183 | 0.028846 | 86277.3765 | 2.9494 | 11.41 | 45.57 | 45.57 | 512 | 512 | 2.9494 | 48.5194 | 37.1094 | 34.16
13373 | Porlock Porlock Weir SPS | 100 | 1.7593 | 5.8905 | 7 | 7 | 2437.8995 | 0.1 | 0.894 | Porlock Sparkhayes Lane STW | Porlock Sparkhayes Lane STW | 183 | 0.040736 | 68352.211 | 33.3718 | 7.12 | 15.42 | 18.08 | - | 2434 | 33.3718 | 51.4518 | 44.3318 | 10.96
14044 | Stanton St Bernard Church Farm SPS | 100 | 1.7361 | 5.8905 | - | 5.8905 | 296.4286 | 0.1 | 0.7523 | Stanton St Bernard . STW | Stanton St Bernard . STW | 180 | 0.028846 | 57518.251 | 2.894 | 129.67 | 126.58 | 129.67 | 0 | 290 | 2.894 | 132.564 | 2.894 | 0
15424 | Berkeley Mobley SPS | 120 | 1.7361 | 8.4823 | - | 8.4823 | 864.4639 | 0.12 | 0.7523 | Sharpness . STW | Berkeley Park View Road SPS | 180 | 0.028846 | 69021.9012 | 6.6469 | 9.57 | 9.11 | 11.17 | - | 858 | 6.6469 | 17.8169 | 8.2469 | 1.6
15189 | Aust Village SPS | 100 | 1.7361 | 5.8905 | 3.1 | 3.1 | 370.2976 | 0.1 | 0.39591 | Aust . STW | Aust Village SPS | 180 | 0.0079892 | 30270.2649 | 1.0385 | 8.43 | 15.99 | 16.15 | - | 368 | 1.0385 | 17.1885 | 8.7585 | 7.72
19932 | Highbridge Station Walk SPS | 100 | 1.7361 | 5.8905 | - | 5.8905 | 111.5639 | 0.1 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 180 | 0.028846 | 57518.251 | 1.0892 | 4.78 | 6.17 | 6.26 | - | 112 | 1.0892 | 7.3492 | 2.5692 | 1.48
15644 | Sutton Waldron . SPS | 100 | 1.713 | 5.8905 | 6 | 6 | 749.6418 | 0.1 | 0.76628 | Iwerne Minster . STW | Iwerne Minster . STW | 178 | 0.029928 | 58587.6094 | 7.5871 | 73.78 | 76.77 | 76.79 | 750 | 754 | 7.5871 | 84.3771 | 10.5971 | 3.01
15344 | Highbridge Commerce Way SPS | 150 | 1.713 | 13.2536 | - | 13.2536 | 200.7403 | 0.15 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 178 | 0.028846 | 86277.3765 | 1.1548 | 6.19 | 6.28 | 6.62 | 146 | 200 | 1.1548 | 7.7748 | 1.5848 | 0.43
15258 | Poole Willis Way SPS | 180 | 1.713 | 19.0852 | - | 19.0852 | 380.2954 | 0.18 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 178 | 0.028846 | 103532.8518 | 1.7288 | 2.59 | 5.38 | 5.88 | 316 | 376 | 1.7288 | 7.6088 | 5.0188 | 3.29
15104 | Devizes Avon Road SPS | 100 | 1.6898 | 5.8905 | - | 5.8905 | 237.9264 | 0.1 | 0.7523 | Devizes Webbs Lane STW | Devizes Webbs Lane STW | 176 | 0.028846 | 57518.251 | 2.3228 | 112.58 | 117.77 | 117.79 | 234 | 238 | 2.3228 | 120.1128 | 7.5328 | 5.21
14336 | Berwick St James . SPS | 75 | 1.6898 | 3.3134 | - | 3.3134 | 188.4759 | 0.075 | 0.7523 | Berwick St James . STW | Berwick St James . STW | 176 | 0.028846 | 43138.6883 | 2.6911 | 66.35 | 67.28 | 67.28 | 188 | 188 | 2.6911 | 69.9711 | 3.6211 | 0.93
17027 | South Cadbury . SPS | 110 | 1.6898 | 7.1275 | 6 | 6 | 1208.9901 | 0.11 | 0.63329 | North Cadbury Ridgeway Lane STW | North Cadbury Ridgeway Lane STW | 176 | 0.020441 | 53261.4631 | 7.4411 | 65.28 | 67.69 | 67.95 | 1178 | 1210 | 7.4411 | 75.3911 | 10.1111 | 2.67
15076 | Wimborne Cuthbury Close SPS | 100 | 1.6898 | 5.8905 | - | 5.8905 | 105.0934 | 0.1 | 0.7523 | Wimborne Brook Road STW | Wimborne Poole Road SPS | 176 | 0.028846 | 57518.251 | 1.026 | 20.25 | 20.02 | 20.28 | 6 | 106 | 1.026 | 21.306 | 1.056 | 0.03
15281 | Holton . SPS | 100 | 1.6667 | 5.8905 | - | 5.8905 | 852.3676 | 0.1 | 0.7523 | Wincanton . STW | North Cheriton Grove Lane SPS | 173 | 0.028846 | 57518.251 | 8.3214 | 101.9 | 103.91 | 107.31 | - | 852 | 8.3214 | 115.6314 | 13.7314 | 5.41
15702 | Rushall Pewsey Road SPS | 120 | 1.6667 | 8.4823 | - | 8.4823 | 749.2113 | 0.12 | 0.7523 | Upavon . STW | North Newnton . SPS | 173 | 0.028846 | 69021.9012 | 5.7607 | 94.31 | 99.72 | 100.75 | 658 | 748 | 5.7607 | 106.5107 | 12.2007 | 6.44
17571 | Blandford Gurkha Road SPS | 100 | 1.6667 | 5.8905 | - | 5.8905 | 177.6676 | 0.1 | 0.7523 | Tarrant Crawford . STW | Blandford Wyvern Way SPS | 173 | 0.028846 | 57518.251 | 1.7345 | 81.32 | 84.27 | 84.27 | 178 | 178 | 1.7345 | 86.0045 | 4.6845 | 2.95
19817 | Sandford Orcas . SPS | 100 | 1.6667 | 5.8905 | 6 | 6 | 265.1845 | 0.1 | 0.76628 | Sandford Orcas . STW | Sandford Orcas . STW | 173 | 0.029928 | 58587.6094 | 2.6839 | 51.39 | 57.83 | 58.11 | 246 | 258 | 2.6839 | 60.7939 | 9.4039 | 6.72
15428 | Sharpness Sanigar Lane SPS | 120 | 1.6667 | 8.4823 | - | 8.4823 | 313.6302 | 0.12 | 0.7523 | Sharpness . STW | Sharpness Old Minster Road SPS | 173 | 0.028846 | 69021.9012 | 2.4115 | 9.5 | 17.94 | 17.94 | 312 | 312 | 2.4115 | 20.3515 | 10.8515 | 8.44
14254 | Wareham Bestwall SPS | 100 | 1.6667 | 5.8905 | - | 5.8905 | 60.3006 | 0.1 | 0.7523 | Wareham Keysworth Drive STW | Wareham South East SPS | 173 | 0.028846 | 57518.251 | 0.5887 | 1.44 | 2.35 | 2.5 | 26 | 60 | 0.5887 | 3.0887 | 1.6487 | 1.06
15530 | High Littleton . SPS | 120 | 1.6435 | 8.4823 | - | 8.4823 | 91.1456 | 0.12 | 0.7523 | Paulton . STW | Paulton . STW | 171 | 0.028846 | 69021.9012 | 0.70082 | 126.7 | 132.95 | 132.95 | 92 | 92 | 0.70082 | 133.6508 | 6.9508 | 6.25
15900 | Clutton Batch Farm SPS | 80 | 1.6435 | 3.7699 | - | 3.7699 | 201.7849 | 0.08 | 0.7523 | Paulton . STW | Paulton . STW | 171 | 0.028846 | 46014.6008 | 2.6446 | 117.63 | 125.07 | 125.29 | 180 | 202 | 2.6446 | 127.9346 | 10.3046 | 7.66
15821 | Frome Garsdale SPS | 125 | 1.6435 | 9.2039 | - | 9.2039 | 125.1115 | 0.125 | 0.7523 | Frome Welshmill Lane STW | Frome Welshmill Lane STW | 171 | 0.028846 | 71897.8138 | 0.9121 | 66.46 | 69.82 | 69.82 | 122 | 122 | 0.9121 | 70.7321 | 4.2721 | 3.36
19948 | Warmley Poplar Farm Estate SPS | 225 | 1.6435 | 29.8206 | - | 29.8206 | 149.2875 | 0.225 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 171 | 0.028846 | 129416.0648 | 0.50974 | 40.87 | 47.48 | 47.48 | 150 | 150 | 0.50974 | 47.9897 | 7.1197 | 6.61
19272 | Alhampton Main SPS | 125 | 1.6435 | 9.2039 | - | 9.2039 | 256.7031 | 0.125 | 0.7523 | Ditcheat . STW | Ditcheat . STW | 171 | 0.028846 | 71897.8138 | 1.8714 | 40.04 | 45.32 | 45.6 | 246 | 256 | 1.8714 | 47.4714 | 7.4314 | 5.56
14462 | Broughton Gifford Curtis Orchard SPS | 100 | 1.6435 | 5.8905 | 3 | 3 | 110.7199 | 0.1 | 0.38314 | Melksham . STW | Broughton Gifford The Green SPS | 171 | 0.007482 | 29293.8047 | 0.29148 | 38.56 | 39.17 | 39.8 | 80 | 110 | 0.29148 | 40.0915 | 1.5315 | 1.24
15161 | Pilning Chessel Avenue SPS | 100 | 1.6435 | 5.8905 | - | 5.8905 | 271.826 | 0.1 | 0.7523 | Redwick . STW | Pilning Pill Head SPS | 171 | 0.028846 | 57518.251 | 2.6538 | 6.89 | 6.54 | 9.98 | 18 | 272 | 2.6538 | 12.6338 | 5.7438 | 3.09
15373 | Chedzoy Manor Drive SPS | 100 | 1.6435 | 5.8905 | - | 5.8905 | 172.7043 | 0.1 | 0.7523 | Chilton Trinity . STW | Chedzoy Ward Lane SPS | 171 | 0.028846 | 57518.251 | 1.6861 | 6.36 | 7.49 | 7.51 | 170 | 172 | 1.6861 | 9.1961 | 2.8361 | 1.15
15003 | Boscombe No 2 SPS | 75 | 1.6435 | 3.3134 | - | 3.3134 | 48.7771 | 0.075 | 0.7523 | Holdenhurst Riverside Avenue STW | Boscombe No 1 SPS | 171 | 0.028846 | 43138.6883 | 0.69646 | 5.5 | 5.58 | 6.46 | 26 | 48 | 0.69646 | 7.1565 | 1.6565 | 0.96
14245 | Upton Shore Lane SPS | 75 | 1.6435 | 3.3134 | - | 3.3134 | 131.8272 | 0.075 | 0.7523 | Lytchett Minster Lytchett Bay STW | Upton Moorlands Way SPS | 171 | 0.028846 | 43138.6883 | 1.8823 | 3.53 | 6.35 | 6.43 | 124 | 132 | 1.8823 | 8.3123 | 4.7823 | 2.9
12660 | Bridgwater Nolana Court SPS | 125 | 1.6435 | 9.2039 | - | 9.2039 | 216.036 | 0.125 | 0.7523 | Chilton Trinity . STW | Bridgwater Stockmoor Village SPS | 171 | 0.028846 | 71897.8138 | 1.575 | - | - | - | - | - | 1.575 | - | - | -
19179 | North Petherton Baymead Lane SPS | 100 | 1.6204 | 5.8905 | - | 5.8905 | 236.2518 | 0.1 | 0.7523 | North Petherton . STW | North Petherton . STW | 168 | 0.028846 | 57518.251 | 2.3065 | 30.3 | 37.4 | 37.4 | 236 | 236 | 2.3065 | 39.7065 | 9.4065 | 7.1
15605 | Nailsea Brockley Court SPS | 100 | 1.6204 | 5.8905 | - | 5.8905 | 735.6944 | 0.1 | 0.7523 | Kingston Seymour Back Lane STW | Brockley Chelvey Green SPS | 168 | 0.028846 | 57518.251 | 7.1824 | 20.48 | 33.72 | 33.86 | - | 736 | 7.1824 | 41.0424 | 20.5624 | 13.38
14420 | Minehead Quay West SPS | 150 | 1.6204 | 13.2536 | 14 | 14 | 224.4203 | 0.15 | 0.79466 | Minehead Headworks STW | Minehead Mart Road SPS | 168 | 0.032186 | 91136.2813 | 1.4372 | 8.05 | 7.37 | 8.09 | 4 | 224 | 1.4372 | 9.5272 | 1.4772 | 0.04
19286 | Lower Weare Sparrow Hill Way SPS | 100 | 1.6204 | 5.8905 | - | 5.8905 | 428.0098 | 0.1 | 0.7523 | Cheddar . STW | Lower Weare . SPS | 168 | 0.028846 | 57518.251 | 4.1785 | 6.53 | 6.86 | 7.01 | 426 | 428 | 4.1785 | 11.1885 | 4.6585 | 0.48
19296 | Clevedon Kenn Road SPS | 160 | 1.6204 | 15.0796 | - | 15.0796 | 731.7783 | 0.16 | 0.7523 | Kingston Seymour Back Lane STW | Clevedon Clevedon Main SPS | 168 | 0.028846 | 92029.2016 | 3.8725 | - | 6.34 | 7.47 | - | 726 | 3.8725 | 11.3425 | - | -
14319 | Amesbury Ejector SPS | - | 1.6204 | - | - | - | 0 | - | - | 13008amesbury Off Church Street STW | 13008amesbury Off Church Street STW | 168 | - | - | - | - | - | - | - | - | - | - | - | -
15144 | Pucklechurch Westerleigh Road SPS | 120 | 1.5972 | 8.4823 | - | 8.4823 | 125.4924 | 0.12 | 0.7523 | Pucklechurch . STW | Pucklechurch . STW | 166 | 0.028846 | 69021.9012 | 0.96491 | 107.07 | 107.74 | 107.81 | 118 | 128 | 0.96491 | 108.7749 | 1.7049 | 0.74
14543 | Frome Handlemakers Road SPS | 100 | 1.5972 | 5.8905 | - | 5.8905 | 21.9067 | 0.1 | 0.7523 | Frome Welshmill Lane STW | Frome Welshmill Lane STW | 166 | 0.028846 | 57518.251 | 0.21387 | 105.16 | 104.91 | 105.17 | 2 | 16 | 0.21387 | 105.3839 | 0.22387 | 0.01
14443 | Dilton Marsh St Marys Lane SPS | 120 | 1.5972 | 8.4823 | - | 8.4823 | 309.7569 | 0.12 | 0.7523 | Dilton Marsh . STW | Dilton Marsh . STW | 166 | 0.028846 | 69021.9012 | 2.3817 | 69.69 | 76.57 | 76.7 | 260 | 304 | 2.3817 | 79.0817 | 9.3917 | 7.01
14433 | Dilton Marsh Clivey SPS | 120 | 1.5972 | 8.4823 | - | 8.4823 | 336.0346 | 0.12 | 0.7523 | Dilton Marsh . STW | Dilton Marsh . STW | 166 | 0.028846 | 69021.9012 | 2.5838 | 59.56 | 68.09 | 68.35 | 326 | 336 | 2.5838 | 70.9338 | 11.3738 | 8.79
14347 | Netherhampton Flowerland SPS | 100 | 1.5972 | 5.8905 | - | 5.8905 | 1210.3176 | 0.1 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 166 | 0.028846 | 57518.251 | 11.816 | 49.85 | 47.47 | 50.07 | 4 | 1210 | 11.816 | 61.886 | 12.036 | 0.22
14325 | Downton Wick Estate SPS | 100 | 1.5972 | 5.8905 | - | 5.8905 | 183.2919 | 0.1 | 0.7523 | Downton Moot Lane STW | Downton South Lane SPS | 166 | 0.028846 | 57518.251 | 1.7894 | 35.22 | 36.61 | 36.61 | 184 | 184 | 1.7894 | 38.3994 | 3.1794 | 1.39
14098 | East Lydford . SPS | 100 | 1.5972 | 5.8905 | - | 5.8905 | 712.9775 | 0.1 | 0.7523 | Lydford Track Off High Street STW | West Lydford . SPS | 166 | 0.028846 | 57518.251 | 6.9606 | 21.99 | 29.55 | 29.71 | 690 | 708 | 6.9606 | 36.6706 | 14.6806 | 7.72
14189 | Yatesbury Nolands Farm SPS | 125 | 1.5741 | 9.2039 | - | 9.2039 | 2951.2552 | 0.125 | 0.7523 | Compton Bassett . STW | Compton Bassett . STW | 164 | 0.028846 | 71897.8138 | 21.5156 | 173.97 | 125.06 | 176.73 | 1144 | 2952 | 21.5156 | 198.2456 | 24.2756 | 2.76
15193 | Child Okeford Gold Hill SPS | 100 | 1.5741 | 5.8905 | 5.3 | 5.3 | 410.8542 | 0.1 | 0.67688 | Shillingstone . STW | Shillingstone Haywards Bridge SPS | 164 | 0.023352 | 51752.3883 | 3.263 | 47.72 | 60.81 | 61.69 | 404 | 410 | 3.263 | 64.953 | 17.233 | 13.97
14464 | Melksham Bader Park SPS | 75 | 1.5741 | 3.3134 | - | 3.3134 | 73.0918 | 0.075 | 0.7523 | Bowerhill Shails Lane STW | Bowerhill Shails Lane STW | 164 | 0.028846 | 43138.6883 | 1.0436 | 44.85 | 44.97 | 45.23 | - | 74 | 1.0436 | 46.2736 | 1.4236 | 0.38
14395 | Hatch Beauchamp . SPS | 80 | 1.5741 | 3.7699 | 4 | 4 | 226.0156 | 0.08 | 0.79821 | Hatch Beauchamp Palmer Green STW | Hatch Beauchamp Palmer Green STW | 164 | 0.032474 | 48823.0078 | 3.3262 | 39.98 | 45.55 | 45.58 | - | 226 | 3.3262 | 48.9062 | 8.9262 | 5.6
14525 | Babcary Riverside Farm SPS | 800 | 1.5741 | 376.9911 | - | 376.9911 | 362.9033 | 0.8 | 0.7523 | Babcary . STW | Babcary . STW | 164 | 0.028846 | 460146.0081 | 0.25187 | 20.6 | 20.86 | 21.11 | 354 | 362 | 0.25187 | 21.3619 | 0.76187 | 0.51
19991 | Bridgwater Huntworth Hotel SPS | 112 | 1.5741 | 7.389 | - | 7.389 | 1311.1145 | 0.112 | 0.7523 | Chilton Trinity . STW | Bridgwater Showground No2 SPS | 164 | 0.028846 | 64420.4411 | 11.0324 | 6.79 | 6.13 | 14.56 | 1212 | 1310 | 11.0324 | 25.5924 | 18.8024 | 7.77
11560 | Yeovil Kite Place SPS | 110 | 1.5741 | 7.1275 | - | 7.1275 | 106.4371 | 0.11 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Alvington Triangle SPS | 164 | 0.028846 | 63270.0761 | 0.91699 | - | - | - | - | - | 0.91699 | - | - | -
19882 | Gillingham Church View SPS | 110 | 1.5509 | 7.1275 | - | 7.1275 | 329.5402 | 0.11 | 0.7523 | Gillingham Common Mead Lane STW | Gillingham Common Mead Lane STW | 161 | 0.028846 | 63270.0761 | 2.8391 | 73.68 | 80.15 | 80.15 | 330 | 330 | 2.8391 | 82.9891 | 9.3091 | 6.47
17246 | Gillingham Lodden Farm SPS | 125 | 1.5509 | 9.2039 | - | 9.2039 | 109.9023 | 0.125 | 0.7523 | Gillingham Common Mead Lane STW | Gillingham Brickyard Lane SPS | 161 | 0.028846 | 71897.8138 | 0.80122 | 72.27 | 73.24 | 73.48 | 104 | 110 | 0.80122 | 74.2812 | 2.0112 | 1.21
14190 | East Tytherton Clovelly Cottage SPS | 75 | 1.5509 | 3.3134 | - | 3.3134 | 1438.378 | 0.075 | 0.7523 | Sutton Benger . STW | Foxham West End SPS | 161 | 0.028846 | 43138.6883 | 20.5377 | 53.06 | 53.26 | 53.47 | 174 | 1438 | 20.5377 | 74.0077 | 20.9477 | 0.41
15268 | Poole Greensleeves Avenue SPS | 100 | 1.5509 | 5.8905 | - | 5.8905 | 147.5651 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 161 | 0.028846 | 57518.251 | 1.4406 | 43.5 | 49.37 | 49.39 | 144 | 148 | 1.4406 | 50.8306 | 7.3306 | 5.89
19952 | Westbury The Ham SPS | 120 | 1.5509 | 8.4823 | - | 8.4823 | 515.4148 | 0.12 | 0.7523 | Westbury STW | Westbury STW | 161 | 0.028846 | 69021.9012 | 3.963 | - | - | - | - | - | 3.963 | - | - | -
12698 | Wellington Cades Farm SPS | 110 | 1.5278 | 7.1275 | - | 7.1275 | 70.2951 | 0.11 | 0.7523 | Wellington Tone STW | Wellington Mitchells Pool SPS | 159 | 0.028846 | 63270.0761 | 0.60562 | 60.06 | 60.26 | 60.38 | 14 | 70 | 0.60562 | 60.9856 | 0.92562 | 0.32
17245 | Blandford Westbury Way SPS | 100 | 1.5278 | 5.8905 | - | 5.8905 | 195.3026 | 0.1 | 0.7523 | Tarrant Crawford . STW | Blandford Langton Road (Blandford No 1) SPS | 159 | 0.028846 | 57518.251 | 1.9067 | 40.37 | 39.99 | 40.56 | 6 | 196 | 1.9067 | 42.4667 | 2.0967 | 0.19
14020 | Lower Stanton Drew . SPS | 100 | 1.5278 | 5.8905 | 2.3 | 2.3 | 675.6652 | 0.1 | 0.29374 | Stanton Drew . STW | Stanton Drew . STW | 159 | 0.0043978 | 22458.5836 | 1.068 | 38.82 | 38.39 | 38.82 | 0 | 676 | 1.068 | 39.888 | 1.068 | 0
17098 | Winfrith Newburgh Technology Centre No.2 SPS | 125 | 1.5278 | 9.2039 | - | 9.2039 | 978.5944 | 0.125 | 0.7523 | Wool . STW | Wool . STW | 159 | 0.028846 | 71897.8138 | 7.1343 | 21.3 | 23.43 | 23.53 | 972 | 978 | 7.1343 | 30.6643 | 9.3643 | 2.23
15674 | Eype Mount Lane SPS | 100 | 1.5278 | 5.8905 | - | 5.8905 | 427.7302 | 0.1 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 159 | 0.028846 | 57518.251 | 4.1758 | 15.59 | 67.38 | 67.38 | 428 | 428 | 4.1758 | 71.5558 | 55.9658 | 51.79
15044 | Burton Sandy Plot SPS | 100 | 1.5278 | 5.8905 | - | 5.8905 | 65.4345 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 159 | 0.028846 | 57518.251 | 0.63882 | 3.6 | 3.55 | 3.75 | 8 | 66 | 0.63882 | 4.3888 | 0.78882 | 0.15
14045 | Everleigh Everleigh Manor SPS | 120 | 1.5046 | 8.4823 | - | 8.4823 | 438.2582 | 0.12 | 0.7523 | Everleigh Haxton Road STW | Everleigh Haxton Road STW | 156 | 0.028846 | 69021.9012 | 3.3698 | 151.76 | 161.34 | 162.02 | - | 438 | 3.3698 | 165.3898 | 13.6298 | 10.26
15126 | Marden Hatfields SPS | 100 | 1.5046 | 5.8905 | - | 5.8905 | 340.0157 | 0.1 | 0.7523 | Marden . STW | Marden . STW | 156 | 0.028846 | 57518.251 | 3.3195 | 102.95 | 106.53 | 108.04 | 302 | 340 | 3.3195 | 111.3595 | 8.4095 | 5.09
14076 | Evercreech Stoney Stratton SPS | 100 | 1.5046 | 5.8905 | 6 | 6 | 381.3964 | 0.1 | 0.76628 | Evercreech . STW | Evercreech . STW | 156 | 0.029928 | 58587.6094 | 3.8601 | 85.39 | 95.54 | 95.54 | - | 382 | 3.8601 | 99.4001 | 14.0101 | 10.15
14469 | Great Hinton . SPS | 100 | 1.5046 | 5.8905 | 1.6 | 1.6 | 692.0812 | 0.1 | 0.20434 | Keevil . STW | Keevil The Street SPS | 156 | 0.0021282 | 15623.3625 | 0.54867 | 65.35 | 76.71 | 77.05 | 270 | 688 | 0.54867 | 77.5987 | 12.2487 | 11.7
10564 | Coldharbour Silent Woman Private SPS | 160 | 1.5046 | 15.0796 | - | 15.0796 | 1324.9404 | 0.16 | 0.7523 | Wareham Keysworth Drive STW | Wareham Sandford Lane SPS | 156 | 0.028846 | 92029.2016 | 7.0114 | 21.68 | 21.1 | 21.68 | - | 6 | 7.0114 | 28.6914 | 7.0114 | 0
15139 | Pilning Swanmoor Bridge SPS | 150 | 1.5046 | 13.2536 | 17 | 17 | 1130.9493 | 0.15 | 0.96495 | Redwick . STW | Pilning Fire Station SPS | 156 | 0.047458 | 110665.4844 | 10.5999 | 6.64 | 7.16 | 7.41 | - | 1130 | 10.5999 | 18.0099 | 11.3699 | 0.77
15815 | Street Bowling Green SPS | 100 | 1.5046 | 5.8905 | - | 5.8905 | 161.1096 | 0.1 | 0.7523 | Glastonbury The Beckery SSTW | Street The Mead SPS | 156 | 0.028846 | 57518.251 | 1.5729 | 6.02 | 8.95 | 8.95 | 162 | 162 | 1.5729 | 10.5229 | 4.5029 | 2.93
17035 | Lympsham Hobbs Boat SPS | 100 | 1.5046 | 5.8905 | - | 5.8905 | 626.5094 | 0.1 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Bleadon Bleadon Bridge SPS | 156 | 0.028846 | 57518.251 | 6.1164 | - | 7.03 | 8.32 | 466 | 626 | 6.1164 | 14.4364 | - | -
15330 | Chard Touches Meadow SPS | 75 | 1.4815 | 3.3134 | - | 3.3134 | 227.5961 | 0.075 | 0.7523 | Chard Peasmarsh STW | Chard Peasmarsh STW | 154 | 0.028846 | 43138.6883 | 3.2497 | 76.33 | 82.38 | 82.38 | 228 | 228 | 3.2497 | 85.6297 | 9.2997 | 6.05
15339 | Templecombe Slades Hill SPS | 100 | 1.4815 | 5.8905 | 5.7 | 5.7 | 301.4675 | 0.1 | 0.72797 | Templecombe . STW | Templecombe . STW | 154 | 0.02701 | 55658.2289 | 2.7599 | 75.03 | 89.11 | 90.17 | 282 | 302 | 2.7599 | 92.9299 | 17.8999 | 15.14
15140 | Tytherington Southlands SPS | 80 | 1.4815 | 3.7699 | - | 3.7699 | 545.7641 | 0.08 | 0.7523 | Cromhall . STW | Tytherington Stidcott SPS | 154 | 0.028846 | 46014.6008 | 7.1529 | 60.64 | 68.57 | 69.37 | 406 | 546 | 7.1529 | 76.5229 | 15.8829 | 8.73
15446 | Hillcommon Hill Common SPS | 100 | 1.4815 | 5.8905 | 8.6 | 8.6 | 784.3243 | 0.1 | 1.0983 | Milverton STW | Milverton STW | 154 | 0.061486 | 83975.5735 | 16.0869 | 53.84 | 58.97 | 59.26 | 778 | 784 | 16.0869 | 75.3469 | 21.5069 | 5.42
14642 | Lyneham Belfast Mead (Ps 10) SPS | 100 | 1.4583 | 5.8905 | - | 5.8905 | 625.9245 | 0.1 | 0.7523 | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham Preston Lane Building 488 (Ps 11 And 12) SPS | 152 | 0.028846 | 57518.251 | 6.1107 | 120.3 | 116.28 | 121.3 | - | 626 | 6.1107 | 127.4107 | 7.1107 | 1
15127 | Lydeway Clock Inn SPS | 75 | 1.4583 | 3.3134 | - | 3.3134 | 1878.7716 | 0.075 | 0.7523 | Urchfont . STW | Urchfont . STW | 152 | 0.028846 | 43138.6883 | 26.8258 | 110.46 | 114.98 | 115.8 | - | 1878 | 26.8258 | 142.6258 | 32.1658 | 5.34
17371 | Holt Springfields SPS | 110 | 1.4583 | 7.1275 | - | 7.1275 | 504.8241 | 0.11 | 0.7523 | Holt Pond Head STW | Holt Bussons Corner SPS | 152 | 0.028846 | 63270.0761 | 4.3492 | 35 | 44.66 | 44.95 | 468 | 504 | 4.3492 | 49.2992 | 14.2992 | 9.95
15047 | Ferndown Redwood Drive SPS | 100 | 1.4583 | 5.8905 | 6.5 | 6.5 | 135.2512 | 0.1 | 0.83014 | Palmersford . STW | Ferndown A31 Tricketts Cross SPS | 152 | 0.035124 | 63469.9102 | 1.6011 | 15.76 | 16.87 | 16.92 | 134 | 136 | 1.6011 | 18.5211 | 2.7611 | 1.16
17041 | Ringwood Avon Castle Drive SPS | 110 | 1.4583 | 7.1275 | - | 7.1275 | 290.4908 | 0.11 | 0.7523 | Ringwood Hampshire Hatches Lane STW | St Ives Avon Castle SPS | 152 | 0.028846 | 63270.0761 | 2.5027 | 12.51 | 30.43 | 31.03 | 244 | 290 | 2.5027 | 33.5327 | 21.0227 | 18.52
15264 | Poole Orchard Avenue SPS | 100 | 1.4583 | 5.8905 | - | 5.8905 | 8.0622 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Elgin Road SPS | 152 | 0.028846 | 57518.251 | 0.078709 | 5.38 | 5.28 | 5.38 | 0 | 8 | 0.078709 | 5.4587 | 0.078709 | 0
15102 | Marston The Plough SPS | 125 | 1.4583 | 9.2039 | - | 9.2039 | 828.6491 | 0.125 | 0.7523 | Potterne . STW | Worton Mill Road SPS | 152 | 0.028846 | 71897.8138 | 6.0411 | - | 54.75 | 56.34 | - | 520 | 6.0411 | 62.3811 | - | -
14014 | Bristol Kings Walk SPS | 100 | 1.4352 | 5.8905 | - | 5.8905 | 172.7061 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 149 | 0.028846 | 57518.251 | 1.6861 | 58.71 | 60.41 | 60.41 | 172 | 172 | 1.6861 | 62.0961 | 3.3861 | 1.7
15128 | Seend Sells Green SPS | 125 | 1.4352 | 9.2039 | - | 9.2039 | 1322.6198 | 0.125 | 0.7523 | Seend . STW | Seend . STW | 149 | 0.028846 | 71897.8138 | 9.6423 | 54.53 | 84.67 | 84.69 | 764 | 768 | 9.6423 | 94.3323 | 39.8023 | 30.16
14294 | Donyatt . SPS | 150 | 1.412 | 13.2536 | 6 | 6 | 428.0285 | 0.15 | 0.34057 | Donyatt Off A58 STW | Donyatt Off A58 STW | 147 | 0.0059117 | 39058.4063 | 0.52867 | 39.06 | 45.31 | 47.35 | - | 426 | 0.52867 | 47.8787 | 8.8187 | 8.29
15335 | South Petherton Pitway SPS | 100 | 1.412 | 5.8905 | - | 5.8905 | 233.2617 | 0.1 | 0.7523 | South Petherton North Street STW | South Petherton North Street STW | 147 | 0.028846 | 57518.251 | 2.2773 | 36.72 | 46.57 | 46.85 | 160 | 234 | 2.2773 | 49.1273 | 12.4073 | 10.13
14449 | Westwood Upper Westwood SPS | 100 | 1.3889 | 5.8905 | - | 5.8905 | 393.272 | 0.1 | 0.7523 | Westwood . STW | Westwood . STW | 144 | 0.028846 | 57518.251 | 3.8394 | 81.87 | 95.29 | 96.81 | 296 | 386 | 3.8394 | 100.6494 | 18.7794 | 14.94
15511 | Monksilver B3188 SPS | 68 | 1.3657 | 2.7238 | 2.5 | 2.5 | 2610.1672 | 0.068 | 0.69049 | Watchet . STW | Doniford . SPS | 142 | 0.024301 | 35899.2705 | 35.9179 | 83.04 | 52.19 | 120.61 | 532 | 2612 | 35.9179 | 156.5279 | 73.4879 | 37.57
14335 | Netherhampton Manor House SPS | 75 | 1.3657 | 3.3134 | - | 3.3134 | 451.6833 | 0.075 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Netherhampton Flowerland SPS | 142 | 0.028846 | 43138.6883 | 6.4493 | 49.62 | 50.06 | 50.54 | 326 | 452 | 6.4493 | 56.9893 | 7.3693 | 0.92
15226 | Thorney Hill Valley Lane SPS | 180 | 1.3657 | 19.0852 | - | 19.0852 | 434.2213 | 0.18 | 0.7523 | Christchurch Stoney Lane STW | Thorney Hill Whitelands SPS | 142 | 0.028846 | 103532.8518 | 1.974 | - | 57.41 | 67.9 | 4 | 430 | 1.974 | 69.874 | - | -
19047 | Wiveliscombe Nordens Meadows Taunton Road SPS | 100 | 1.3426 | 5.8905 | - | 5.8905 | 102.1959 | 0.1 | 0.7523 | Wiveliscombe Hillsmoor STW | Wiveliscombe Ford Road (Lion D'Angers) SPS | 140 | 0.028846 | 57518.251 | 0.99771 | 96.51 | 98.38 | 98.38 | 102 | 102 | 0.99771 | 99.3777 | 2.8677 | 1.87
14195 | Startley . SPS | 100 | 1.3426 | 5.8905 | - | 5.8905 | 798.7732 | 0.1 | 0.7523 | Sutton Benger . STW | Sutton Benger . STW | 140 | 0.028846 | 57518.251 | 7.7982 | 77.1 | 74.49 | 77.14 | 2 | 794 | 7.7982 | 84.9382 | 7.8382 | 0.04
14300 | Yeovil Pen Mill Banbury SPS | 100 | 1.3426 | 5.8905 | - | 5.8905 | 224.414 | 0.1 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Sherborne Road (Pen Mill) STW | 140 | 0.028846 | 57518.251 | 2.1909 | 28.69 | 29.92 | 30.35 | 186 | 224 | 2.1909 | 32.5409 | 3.8509 | 1.66
15516 | Bilbrook . SPS | 120 | 1.3426 | 8.4823 | 4 | 4 | 819.8941 | 0.12 | 0.35476 | Minehead Headworks STW | Blue Anchor Pill Bridge SPS | 140 | 0.0064146 | 32548.6719 | 1.4651 | 25 | 20.39 | 29.15 | 176 | 820 | 1.4651 | 30.6151 | 5.6151 | 4.15
15791 | West Moors Gundrymor Industrial Estate SPS | 150 | 1.3426 | 13.2536 | - | 13.2536 | 1304.721 | 0.15 | 0.7523 | Palmersford . STW | West Moors The Forest SPS | 140 | 0.028846 | 86277.3765 | 7.5057 | 23.22 | 26.59 | 26.59 | - | 1304 | 7.5057 | 34.0957 | 10.8757 | 3.37
15280 | Martock Coat Road SPS | 100 | 1.3426 | 5.8905 | - | 5.8905 | 237.1948 | 0.1 | 0.7523 | Martock Hurst Bow STW | Martock Hurst Bow STW | 140 | 0.028846 | 57518.251 | 2.3157 | 20.3 | 21.07 | 21.21 | 188 | 238 | 2.3157 | 23.5257 | 3.2257 | 0.91
14072 | Bleadney Bleadney Mill SPS | 80 | 1.3426 | 3.7699 | 3.5 | 3.5 | 668.7315 | 0.08 | 0.69844 | Wookey . STW | Henton Ford Lane SPS | 140 | 0.024863 | 42720.1318 | 7.5804 | 10.38 | 20.78 | 21.3 | 654 | 668 | 7.5804 | 28.8804 | 18.5004 | 10.92
15138 | Pilning Wainbridge Crescent SPS | 100 | 1.3426 | 5.8905 | - | 5.8905 | 73.6824 | 0.1 | 0.7523 | Redwick . STW | Pilning Redwick Road SPS | 140 | 0.028846 | 57518.251 | 0.71934 | 6.68 | 6.82 | 6.87 | 72 | 74 | 0.71934 | 7.5893 | 0.90934 | 0.19
15170 | Horton Kings Lane SPS | 150 | 1.3194 | 13.2536 | - | 13.2536 | 1025.6893 | 0.15 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 137 | 0.028846 | 86277.3765 | 5.9005 | 94.62 | 124.82 | 124.82 | - | 1026 | 5.9005 | 130.7205 | 36.1005 | 30.2
14025 | Filton Charlton Gardens SPS | 225 | 1.3194 | 29.8206 | - | 29.8206 | 111.0939 | 0.225 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 137 | 0.028846 | 129416.0648 | 0.37933 | 66.17 | 64.97 | 66.17 | - | 112 | 0.37933 | 66.5493 | 0.37933 | 0
15591 | Portishead Harbour Road SPS | 200 | 1.3194 | 23.5619 | - | 23.5619 | 207.6078 | 0.2 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 137 | 0.028846 | 115036.502 | 0.82428 | 6.92 | 7.01 | 7.2 | - | 208 | 0.82428 | 8.0243 | 1.1043 | 0.28
14070 | Godney . SPS | 80 | 1.3194 | 3.7699 | - | 3.7699 | 1648.8478 | 0.08 | 0.7523 | Meare . STW | Meare Turnbridge SPS | 137 | 0.028846 | 46014.6008 | 21.61 | 5.43 | 5.91 | 5.91 | 1648 | 1648 | 21.61 | 27.52 | 22.09 | 0.48
15430 | Purton Hinton Road SPS | 160 | 1.3194 | 15.0796 | - | 15.0796 | 1851.7935 | 0.16 | 0.7523 | Sharpness . STW | Sharpness Docks Road East SPS | 137 | 0.028846 | 92029.2016 | 9.7995 | - | 22.62 | 24.46 | 1762 | 1784 | 9.7995 | 34.2595 | - | -
19305 | Bishops Cannings Oak Close SPS | 120 | 1.2963 | 8.4823 | - | 8.4823 | 167.7652 | 0.12 | 0.7523 | All Cannings Lower Mill Farm STW | Horton Horton Farm SPS | 135 | 0.028846 | 69021.9012 | 1.2899 | 133.51 | 134.36 | 134.55 | - | 168 | 1.2899 | 135.8399 | 2.3299 | 1.04
15723 | Tetbury Springfields SPS | - | 1.2963 | - | 4 | 4 | 227.3573 | - | - | Tetbury . STW | Tetbury . STW | 135 | - | - | - | 117.33 | 123.09 | 123.19 | 196 | 222 | - | - | - | 5.86
15496 | Leigh Bridge Farm SPS | 100 | 1.2963 | 5.8905 | 11.8 | 11.8 | 289.737 | 0.1 | 1.507 | Thornford Bridge Halt STW | Leigh Frampton Farm SPS | 135 | 0.11576 | 115222.2985 | 11.0859 | 75 | 82.57 | 83.35 | 278 | 290 | 11.0859 | 94.4359 | 19.4359 | 8.35
14479 | Melksham Woodrow Road SPS | 50 | 1.2963 | 1.4726 | - | 1.4726 | 650.1156 | 0.05 | 0.7523 | Melksham . STW | Melksham . STW | 135 | 0.028846 | 28759.1255 | 15.9869 | 39.57 | 44.13 | 44.37 | 628 | 650 | 15.9869 | 60.3569 | 20.7869 | 4.8
10192 | Ferndown Glissons SPS | 125 | 1.2963 | 9.2039 | - | 9.2039 | 120.132 | 0.125 | 0.7523 | Kinson New Road Northbourne STW | Longham Ham Lane SPS | 135 | 0.028846 | 71897.8138 | 0.8758 | 14.64 | 17.03 | 17.1 | 62 | 120 | 0.8758 | 17.9758 | 3.3358 | 2.46
15320 | Long Sutton Knole SPS | 50 | 1.2963 | 1.4726 | 2.8 | 2.8 | 1209.9603 | 0.05 | 1.4304 | Langport Portfield Lane STW | Long Sutton Bennetts Orchard SPS | 135 | 0.10428 | 54681.7688 | 105.0813 | 12.18 | 28.79 | 28.79 | - | 1210 | 105.0813 | 133.8713 | 121.6913 | 16.61
14246 | Swanage Life Boat Station Comminutor SPS | 100 | 1.2963 | 5.8905 | - | 5.8905 | 485.4574 | 0.1 | 0.7523 | Swanage Marine Parade STW | Swanage Marine Parade STW | 135 | 0.028846 | 57518.251 | 4.7394 | 3.41 | 2.56 | 15.24 | 250 | 486 | 4.7394 | 19.9794 | 16.5694 | 11.83
17344 | Lyneham Webbs Court SPS | 100 | 1.2731 | 5.8905 | - | 5.8905 | 390.9127 | 0.1 | 0.7523 | Lyneham Preston Lane SPS | Lyneham Preston Lane SPS | 132 | 0.028846 | 57518.251 | 3.8164 | 126.95 | 130.43 | 130.66 | - | 386 | 3.8164 | 134.4764 | 7.5264 | 3.71
14170 | Brinkworth Callow Hill SPS | 95 | 1.2731 | 5.3162 | - | 5.3162 | 708.3935 | 0.095 | 0.7523 | Brinkworth . STW | Brinkworth . STW | 132 | 0.028846 | 54642.3385 | 7.3986 | 107.48 | 110.3 | 111.62 | 484 | 704 | 7.3986 | 119.0186 | 11.5386 | 4.14
14207 | Chelworth Oaksey SPS | 100 | 1.2731 | 5.8905 | - | 5.8905 | 1255.1554 | 0.1 | 0.7523 | Malmesbury . STW | Eastcourt Oatridge Farm SPS | 132 | 0.028846 | 57518.251 | 12.2537 | 99.17 | 108.18 | 108.18 | - | 1256 | 12.2537 | 120.4337 | 21.2637 | 9.01
14214 | Lea Crab Mill Lane SPS | 80 | 1.2731 | 3.7699 | - | 3.7699 | 264.5892 | 0.08 | 0.7523 | Malmesbury . STW | Lea Lea North SPS | 132 | 0.028846 | 46014.6008 | 3.4677 | 81.78 | 86.61 | 86.65 | 254 | 264 | 3.4677 | 90.1177 | 8.3377 | 4.87
14618 | Bristol Butlers Walk Crews Hole SPS | 100 | 1.2731 | 5.8905 | - | 5.8905 | 84.1023 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 132 | 0.028846 | 57518.251 | 0.82107 | 11.03 | 15.04 | 15.04 | 84 | 84 | 0.82107 | 15.8611 | 4.8311 | 4.01
17141 | Wareham Stoborough Meadows SPS | 100 | 1.2731 | 5.8905 | - | 5.8905 | 50.355 | 0.1 | 0.7523 | Wareham Keysworth Drive STW | Wareham Keysworth Drive STW | 132 | 0.028846 | 57518.251 | 0.4916 | 6.05 | 5.67 | 6.09 | 2 | 50 | 0.4916 | 6.5816 | 0.5316 | 0.04
12328 | Creech St Michael Hopkins Field Private SPS | 125 | 1.2731 | 9.2039 | - | 9.2039 | 282.8432 | 0.125 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 132 | 0.028846 | 71897.8138 | 2.062 | - | - | - | - | - | 2.062 | - | - | -
15522 | Clutton Kings Oak Meadow SPS | 75 | 1.25 | 3.3134 | - | 3.3134 | 144.6037 | 0.075 | 0.7523 | Paulton . STW | Paulton . STW | 130 | 0.028846 | 43138.6883 | 2.0647 | 110.82 | 114.88 | 114.88 | 144 | 144 | 2.0647 | 116.9447 | 6.1247 | 4.06
14549 | Royal Wootton Bassett Whitehill Lane SPS | 100 | 1.25 | 5.8905 | - | 5.8905 | 329.7289 | 0.1 | 0.7523 | Royal Wootton Bassett . STW | Royal Wootton Bassett . STW | 130 | 0.028846 | 57518.251 | 3.2191 | 100.49 | 106.61 | 106.61 | 326 | 326 | 3.2191 | 109.8291 | 9.3391 | 6.12
14450 | Coulston . SPS | 200 | 1.25 | 23.5619 | 3.4 | 3.4 | 1714.9624 | 0.2 | 0.10856 | Keevil . STW | Edington Tinhead Lower BayntINT | 130 | 0.00060064 | 16599.8227 | 0.16812 | 68.98 | 70.3 | 70.83 | - | 1712 | 0.16812 | 70.9981 | 2.0181 | 1.85
19279 | Oake Saxon Close SPS | 100 | 1.25 | 5.8905 | - | 5.8905 | 210.7212 | 0.1 | 0.7523 | Milverton STW | Oake . SPS | 130 | 0.028846 | 57518.251 | 2.0572 | 49.06 | 53.64 | 53.82 | 162 | 212 | 2.0572 | 55.8772 | 6.8172 | 4.76
14453 | Staverton Nestles SPS | 250 | 1.25 | 36.8155 | - | 36.8155 | 692.3315 | 0.25 | 0.7523 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 130 | 0.028846 | 143795.6275 | 2.0665 | 31.55 | 41.94 | 41.94 | 692 | 692 | 2.0665 | 44.0065 | 12.4565 | 10.39
15055 | Woolsbridge Industrial Estate SPS | 250 | 1.25 | 36.8155 | - | 36.8155 | 186.4911 | 0.25 | 0.7523 | Palmersford . STW | West Moors The Forest SPS | 130 | 0.028846 | 143795.6275 | 0.55665 | 17.23 | 17.85 | 17.95 | 174 | 188 | 0.55665 | 18.5067 | 1.2767 | 0.72
17093 | Locking Woolvers Way SPS | 280 | 1.25 | 46.1814 | - | 46.1814 | 3634.3176 | 0.28 | 0.7523 | Wick St Lawrence . STW | Locking Locking Village SPS | 130 | 0.028846 | 161051.1028 | 9.3916 | 5.43 | 5.35 | 7.14 | 3474 | 3606 | 9.3916 | 16.5316 | 11.1016 | 1.71
15506 | Salway Ash Vale View SPS | 100 | 1.2268 | 5.8905 | - | 5.8905 | 164.0501 | 0.1 | 0.7523 | Bridport Wych Farm STW | Salway Ash Old Stw SPS | 128 | 0.028846 | 57518.251 | 1.6016 | 74.35 | 79.85 | 79.85 | 164 | 164 | 1.6016 | 81.4516 | 7.1016 | 5.5
14274 | East Chaldon . SPS | 80 | 1.2268 | 3.7699 | 4 | 4 | 1027.3371 | 0.08 | 0.79821 | Wool . STW | Winfrith Newburgh Winfrith Church SPS | 128 | 0.032474 | 48823.0078 | 15.1188 | 54.25 | 44.29 | 56.15 | 152 | 1028 | 15.1188 | 71.2688 | 17.0188 | 1.9
17247 | Moreton Queens Drive SPS | 125 | 1.2268 | 9.2039 | - | 9.2039 | 1114.9781 | 0.125 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Crossways Redbridge SPS | 128 | 0.028846 | 71897.8138 | 8.1285 | 45.86 | 58.06 | 58.22 | 802 | 1114 | 8.1285 | 66.3485 | 20.4885 | 12.36
14649 | Taunton Lisieux Way SPS | - | 1.2268 | - | - | - | 182.8765 | - | - | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 128 | - | - | - | 13.05 | 13.33 | 13.61 | 154 | 182 | - | - | - | 0.56
15375 | Chilton Polden Broadway SPS | 100 | 1.2037 | 5.8905 | - | 5.8905 | 158.9713 | 0.1 | 0.7523 | West Huntspill STW | Chilton Polden Main SPS | 125 | 0.028846 | 57518.251 | 1.552 | 35.87 | 38.21 | 38.48 | - | 158 | 1.552 | 40.032 | 4.162 | 2.61
14119 | Wells Keward Avenue (Bishops Lea Close) SPS | 100 | 1.2037 | 5.8905 | - | 5.8905 | 137.6245 | 0.1 | 0.7523 | Wells . STW | Wells . STW | 125 | 0.028846 | 57518.251 | 1.3436 | 26.57 | 28.49 | 28.54 | 134 | 138 | 1.3436 | 29.8836 | 3.3136 | 1.97
14296 | Podimore . SPS | 80 | 1.2037 | 3.7699 | - | 3.7699 | 355.2404 | 0.08 | 0.7523 | Podimore Behind Greystones STW | Podimore Behind Greystones STW | 125 | 0.028846 | 46014.6008 | 4.6558 | 16.31 | 15.94 | 16.53 | - | 342 | 4.6558 | 21.1858 | 4.8758 | 0.22
14088 | Baltonsborough Church Lane SPS | 110 | 1.2037 | 7.1275 | - | 7.1275 | 94.5032 | 0.11 | 0.7523 | Butleigh . STW | Baltonsborough Baltonsborough Main SPS | 125 | 0.028846 | 63270.0761 | 0.81418 | 14.25 | 15.66 | 15.68 | 88 | 90 | 0.81418 | 16.4942 | 2.2442 | 1.43
14535 | Street The Withys Fielding Road SPS | - | 1.2037 | - | - | - | 106.0712 | - | - | Glastonbury The Beckery SSTW | Street Main SPS | 125 | - | - | - | 7.49 | 8.09 | 8.17 | 102 | 106 | - | - | - | 0.68
14166 | Minety Lower Moor SPS | 75 | 1.1806 | 3.3134 | - | 3.3134 | 725.2883 | 0.075 | 0.7523 | Malmesbury . STW | Minety Station Road SPS | 123 | 0.028846 | 43138.6883 | 10.356 | 87.56 | 98.68 | 98.68 | - | 724 | 10.356 | 109.036 | 21.476 | 11.12
14183 | Box Middle Hill SPS | 75 | 1.1806 | 3.3134 | - | 3.3134 | 310.0501 | 0.075 | 0.7523 | Box Mill Lane STW | Box Mill Lane SPS | 123 | 0.028846 | 43138.6883 | 4.427 | 32.55 | 40.8 | 40.8 | 310 | 310 | 4.427 | 45.227 | 12.677 | 8.25
15391 | Westonzoyland Hamrod Lane SPS | 100 | 1.1806 | 5.8905 | 5 | 5 | 309.5465 | 0.1 | 0.63857 | Chilton Trinity . STW | Westonzoyland . SPS | 123 | 0.020783 | 48823.0078 | 2.1943 | 5.27 | 6.97 | 6.98 | 308 | 310 | 2.1943 | 9.1743 | 3.9043 | 1.71
17241 | Portland Osprey Quay SPS | 100 | 1.1806 | 5.8905 | - | 5.8905 | 162.3325 | 0.1 | 0.7523 | Weymouth . STW | Portland Victoria Square SPS | 123 | 0.028846 | 57518.251 | 1.5848 | 2.09 | 3 | 4.78 | 16 | 162 | 1.5848 | 6.3648 | 4.2748 | 2.69
15096 | Devizes Old Park SPS | 125 | 1.1574 | 9.2039 | - | 9.2039 | 651.7549 | 0.125 | 0.7523 | Devizes Webbs Lane STW | Devizes Webbs Lane STW | 120 | 0.028846 | 71897.8138 | 4.7515 | 113.03 | 130.35 | 130.37 | 650 | 652 | 4.7515 | 135.1215 | 22.0915 | 17.34
14576 | Bathford Garstons SPS | 100 | 1.1574 | 5.8905 | - | 5.8905 | 84.2831 | 0.1 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 120 | 0.028846 | 57518.251 | 0.82283 | 59.59 | 62.02 | 62.02 | 84 | 84 | 0.82283 | 62.8428 | 3.2528 | 2.43
14483 | Steeple Ashton Ashton Common SPS | 100 | 1.1574 | 5.8905 | - | 5.8905 | 829.9638 | 0.1 | 0.7523 | Keevil . STW | Keevil The Street SPS | 120 | 0.028846 | 57518.251 | 8.1027 | 53.77 | 82.71 | 83.87 | 794 | 830 | 8.1027 | 91.9727 | 38.2027 | 30.1
19081 | Wimborne Clapgate SPS | 50 | 1.1574 | 1.4726 | - | 1.4726 | 531.4826 | 0.05 | 0.7523 | Wimborne Brook Road STW | Wimborne Furzehill SPS | 120 | 0.028846 | 28759.1255 | 13.0696 | 27.01 | 38.32 | 38.32 | 532 | 532 | 13.0696 | 51.3896 | 24.3796 | 11.31
17104 | Durleigh Sailing Club SPS | 110 | 1.1574 | 7.1275 | - | 7.1275 | 838.6996 | 0.11 | 0.7523 | Chilton Trinity . STW | Bridgwater West Quay Drawbridge SPS | 120 | 0.028846 | 63270.0761 | 7.2257 | 21.39 | 28.12 | 28.12 | - | 838 | 7.2257 | 35.3457 | 13.9557 | 6.73
15026 | Christchurch Rodney Drive SPS | 100 | 1.1574 | 5.8905 | - | 5.8905 | 88.6147 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Scotts Hill Lane SPS | 120 | 0.028846 | 57518.251 | 0.86512 | 6.5 | 6.95 | 6.95 | 88 | 88 | 0.86512 | 7.8151 | 1.3151 | 0.45
19949 | Westbury Northacre Industrial Park SPS | 250 | 1.1574 | 36.8155 | - | 36.8155 | 1627.2973 | 0.25 | 0.7523 | Westbury STW | Westbury STW | 120 | 0.028846 | 143795.6275 | 4.8573 | - | 62.7 | 66.79 | 1124 | 1390 | 4.8573 | 71.6473 | - | -
11501 | Tetbury Quercus Road SPS | 125 | 1.1574 | 9.2039 | - | 9.2039 | 502.8405 | 0.125 | 0.7523 | Tetbury . STW | Tetbury . STW | 120 | 0.028846 | 71897.8138 | 3.6659 | - | - | - | - | - | 3.6659 | - | - | -
14470 | Winsley Church Farm (Milbourne Close) SPS | 100 | 1.1343 | 5.8905 | - | 5.8905 | 153.684 | 0.1 | 0.7523 | Winsley . STW | Winsley . STW | 118 | 0.028846 | 57518.251 | 1.5004 | 120.85 | 123.47 | 123.47 | 146 | 146 | 1.5004 | 124.9704 | 4.1204 | 2.62
15510 | Holford . SPS | 75 | 1.1343 | 3.3134 | - | 3.3134 | 268.0324 | 0.075 | 0.7523 | Kilve Beach Car Park STW | Kilve Beach Car Park STW | 118 | 0.028846 | 43138.6883 | 3.8271 | 105.31 | 109.78 | 112.85 | 246 | 268 | 3.8271 | 116.6771 | 11.3671 | 7.54
15819 | Chard Bryer Close (Lordleaze Lane) SPS | 100 | 1.1343 | 5.8905 | - | 5.8905 | 78.2666 | 0.1 | 0.7523 | Chard Peasmarsh STW | Chard Peasmarsh STW | 118 | 0.028846 | 57518.251 | 0.7641 | 93.13 | 95.73 | 95.73 | 78 | 78 | 0.7641 | 96.4941 | 3.3641 | 2.6
15117 | Devizes Dunkirk Hill SPS | 180 | 1.1343 | 19.0852 | 14.6 | 14.6 | 403.0193 | 0.18 | 0.5755 | Devizes Webbs Lane STW | Devizes Webbs Lane STW | 118 | 0.016881 | 79201.7682 | 1.0859 | 79.62 | 119.26 | 119.26 | 400 | 400 | 1.0859 | 120.3459 | 40.7259 | 39.64
14594 | Long Load Yeobridge SPS | 80 | 1.1343 | 3.7699 | - | 3.7699 | 577.5301 | 0.08 | 0.7523 | Martock Hurst Bow STW | Long Load Church Lane SPS | 118 | 0.028846 | 46014.6008 | 7.5692 | 9.03 | 9.15 | 9.3 | 36 | 578 | 7.5692 | 16.8692 | 7.8392 | 0.27
14421 | Cutcombe . SPS | 80 | 1.1111 | 3.7699 | - | 3.7699 | 461.8558 | 0.08 | 0.7523 | Minehead Headworks STW | Minehead Headworks STW | 116 | 0.028846 | 46014.6008 | 6.0531 | 273.55 | 296.66 | 300.65 | 346 | 458 | 6.0531 | 306.7031 | 33.1531 | 27.1
14489 | Yatesbury Village SPS | 100 | 1.1111 | 5.8905 | - | 5.8905 | 914.4649 | 0.1 | 0.7523 | Compton Bassett . STW | Yatesbury Nolands Farm SPS | 116 | 0.028846 | 57518.251 | 8.9277 | 164.26 | 171.65 | 171.65 | 914 | 914 | 8.9277 | 180.5777 | 16.3177 | 7.39
15195 | Bryanston Forum View SPS | 75 | 1.1111 | 3.3134 | - | 3.3134 | 207.049 | 0.075 | 0.7523 | Tarrant Crawford . STW | Blandford St Mary Bournemouth Road SPS | 116 | 0.028846 | 43138.6883 | 2.9563 | 86.06 | 87.87 | 88.16 | 170 | 208 | 2.9563 | 91.1163 | 5.0563 | 2.1
19159 | Wickwar Amberley Way SPS | 150 | 1.1111 | 13.2536 | - | 13.2536 | 148.2684 | 0.15 | 0.7523 | Wickwar . STW | Wickwar Inlet P.S SPS | 116 | 0.028846 | 86277.3765 | 0.85295 | 76.96 | 80.07 | 80.43 | - | 148 | 0.85295 | 81.2829 | 4.3229 | 3.47
19062 | Downton Batten Road SPS | 75 | 1.1111 | 3.3134 | - | 3.3134 | 106.8575 | 0.075 | 0.7523 | Downton Moot Lane STW | Downton South Lane SPS | 116 | 0.028846 | 43138.6883 | 1.5258 | 37.29 | 37.31 | 37.64 | 66 | 106 | 1.5258 | 39.1658 | 1.8758 | 0.35
15464 | Taunton Venture Way Priorswood SPS | 175 | 1.1111 | 18.0396 | - | 18.0396 | 280.6758 | 0.175 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 116 | 0.028846 | 100656.9393 | 1.3231 | 13.1 | 13.86 | 15.74 | 58 | 280 | 1.3231 | 17.0631 | 3.9631 | 2.64
19664 | Blackford Old Court Farm SPS | - | 1.1111 | - | - | - | 127.6429 | - | - | West Huntspill STW | Blackford Blackford Moor Lane SPS | 116 | - | - | - | 10.83 | 16.29 | 16.45 | 110 | 128 | - | - | - | 5.62
14588 | West Lulworth Lulworth Outfall Ps SPS | 120 | 1.1111 | 8.4823 | 10.5 | 10.5 | 596.6782 | 0.12 | 0.93125 | Wool . STW | West Lulworth Hambury Farm SPS | 116 | 0.044201 | 85440.2637 | 6.9699 | 6.74 | 21.23 | 21.43 | 594 | 602 | 6.9699 | 28.3999 | 21.6599 | 14.69
15351 | Burnham-On-Sea Broadhurst Gardens SPS | 100 | 1.1111 | 5.8905 | - | 5.8905 | 242.8977 | 0.1 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 116 | 0.028846 | 57518.251 | 2.3713 | 5.39 | 5.88 | 5.88 | 242 | 242 | 2.3713 | 8.2513 | 2.8613 | 0.49
11680 | Bradford-On-Avon Benjamin Street SPS | 160 | 1.1111 | 15.0796 | - | 15.0796 | 548.8409 | 0.16 | 0.7523 | Bradford-On-Avon . STW | Bradford-On-Avon Barton Farm Terminal P Stn SPS | 116 | 0.028846 | 92029.2016 | 2.9044 | - | - | - | - | - | 2.9044 | - | - | -
15498 | Corscombe High Street SPS | 75 | 1.088 | 3.3134 | - | 3.3134 | 198.255 | 0.075 | 0.7523 | Corscombe Off Fudge Hill STW | Corscombe Off Fudge Hill STW | 113 | 0.028846 | 43138.6883 | 2.8308 | 123.58 | 131.58 | 131.58 | - | 198 | 2.8308 | 134.4108 | 10.8308 | 8
15523 | Camerton Sunnyvale SPS | 100 | 1.088 | 5.8905 | 3.8 | 3.8 | 118.1848 | 0.1 | 0.48531 | Cam Valley Dunkerton STW | Carlingcott Stoneage Lane SPS | 113 | 0.012005 | 37105.4859 | 0.49134 | 68.04 | 71.86 | 71.86 | 118 | 118 | 0.49134 | 72.3513 | 4.3113 | 3.82
19924 | Verwood Starlight Farm Close SPS | 110 | 1.088 | 7.1275 | - | 7.1275 | 179.1461 | 0.11 | 0.7523 | Palmersford . STW | Verwood Potterne Way SPS | 113 | 0.028846 | 63270.0761 | 1.5434 | 40.34 | 42.67 | 42.67 | 180 | 180 | 1.5434 | 44.2134 | 3.8734 | 2.33
15583 | Clevedon St Christopher Court SPS | 100 | 1.088 | 5.8905 | - | 5.8905 | 72.6056 | 0.1 | 0.7523 | Kingston Seymour Back Lane STW | Clevedon The Beach SPS | 113 | 0.028846 | 57518.251 | 0.70883 | 24.53 | 33.7 | 33.7 | 72 | 72 | 0.70883 | 34.4088 | 9.8788 | 9.17
19471 | Yatton Kenn Moor Road SPS | 150 | 1.088 | 13.2536 | - | 13.2536 | 152.3292 | 0.15 | 0.7523 | Kingston Seymour Back Lane STW | Kingston Bridge SPS | 113 | 0.028846 | 86277.3765 | 0.87631 | 6.01 | 9.41 | 9.41 | 152 | 152 | 0.87631 | 10.2863 | 4.2763 | 3.4
15324 | Charlton Horethorne Kennels SPS | 100 | 1.088 | 5.8905 | - | 5.8905 | 47.737 | 0.1 | 0.7523 | Charlton Horethorne Mount Lane STW | Charlton Horethorne Mount Lane STW | 113 | 0.028846 | 57518.251 | 0.46604 | - | 107.12 | 107.12 | - | 46 | 0.46604 | 107.586 | - | -
15286 | Milborne Port Henning Way SPS | 80 | 1.0648 | 3.7699 | - | 3.7699 | 131.4858 | 0.08 | 0.7523 | Milborne Port Venn Farm STW | Milborne Port Venn Farm STW | 111 | 0.028846 | 46014.6008 | 1.7233 | 89.35 | 91.47 | 91.74 | 94 | 132 | 1.7233 | 93.4633 | 4.1133 | 2.39
14099 | Street Walton Globe SPS | 125 | 1.0648 | 9.2039 | 5 | 5 | 573.8604 | 0.125 | 0.40868 | Glastonbury The Beckery SSTW | Street Houndwood Drove SPS | 111 | 0.0085129 | 39058.4063 | 1.277 | 12.78 | 28.24 | 28.24 | 566 | 566 | 1.277 | 29.517 | 16.737 | 15.46
14105 | Chilcompton Bennel SPS | 110 | 1.0417 | 7.1275 | - | 7.1275 | 273.7474 | 0.11 | 0.7523 | Chilcompton . STW | Chilcompton . STW | 108 | 0.028846 | 63270.0761 | 2.3584 | 167.2 | 177.18 | 177.64 | - | 280 | 2.3584 | 179.9984 | 12.7984 | 10.44
18712 | Chapmanslade West SPS | 100 | 1.0417 | 5.8905 | - | 5.8905 | 488.7123 | 0.1 | 0.7523 | Frome Welshmill Lane STW | Chapmanslade Divers Bridge SPS | 108 | 0.028846 | 57518.251 | 4.7712 | 138.79 | 141.19 | 141.43 | - | 490 | 4.7712 | 146.2012 | 7.4112 | 2.64
17475 | Orcheston Stonehenge Park SPS | 110 | 1.0417 | 7.1275 | - | 7.1275 | 442.4543 | 0.11 | 0.7523 | Shrewton . STW | Orcheston . SPS | 108 | 0.028846 | 63270.0761 | 3.8119 | 84.67 | 94.71 | 94.8 | - | 442 | 3.8119 | 98.6119 | 13.9419 | 10.13
15628 | Dorchester Herringston Road SPS | 75 | 1.0417 | 3.3134 | - | 3.3134 | 136.2942 | 0.075 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 108 | 0.028846 | 43138.6883 | 1.9461 | 63.62 | 65.87 | 65.87 | 136 | 136 | 1.9461 | 67.8161 | 4.1961 | 2.25
15706 | Poole Delph Gardens SPS | 120 | 1.0417 | 8.4823 | - | 8.4823 | 329.749 | 0.12 | 0.7523 | Poole Cabot Lane STW | Poole Greensleeves Avenue SPS | 108 | 0.028846 | 69021.9012 | 2.5354 | 41.06 | 49.34 | 49.34 | 332 | 332 | 2.5354 | 51.8754 | 10.8154 | 8.28
15774 | Beercrocombe . SPS | - | 1.0417 | - | - | - | 855.2353 | - | - | Fivehead . STW | Isle Abbotts Two Bridges SPS | 108 | - | - | - | 31.79 | 47.52 | 47.81 | 846 | 856 | - | - | - | 16.02
17039 | Enmore Number One SPS | 110 | 1.0417 | 7.1275 | - | 7.1275 | 516.4321 | 0.11 | 0.7523 | Chilton Trinity . STW | Durleigh Sailing Club SPS | 108 | 0.028846 | 63270.0761 | 4.4492 | 23.78 | 30.48 | 30.91 | - | 516 | 4.4492 | 35.3592 | 11.5792 | 7.13
15515 | Watchet Werren Close SPS | 100 | 1.0417 | 5.8905 | - | 5.8905 | 63.4098 | 0.1 | 0.7523 | Watchet . STW | Watchet Market Street (Tunnel) SPS | 108 | 0.028846 | 57518.251 | 0.61905 | 9.75 | 10.89 | 11.16 | - | 60 | 0.61905 | 11.7791 | 2.0291 | 1.41
15358 | Berrow Whitegates Yew Tree Hurn Lane SPS | 150 | 1.0417 | 13.2536 | - | 13.2536 | 271.4816 | 0.15 | 0.7523 | West Huntspill STW | Berrow Meade Farm Coast Road SPS | 108 | 0.028846 | 86277.3765 | 1.5618 | 6.51 | 7.59 | 7.63 | - | 272 | 1.5618 | 9.1918 | 2.6818 | 1.12
15526 | Hinton Charterhouse Old Quarry Midford Road SPS | 100 | 1.0185 | 5.8905 | - | 5.8905 | 518.9927 | 0.1 | 0.7523 | Freshford . STW | Freshford . STW | 106 | 0.028846 | 57518.251 | 5.0668 | 113.65 | 134.3 | 134.3 | 518 | 518 | 5.0668 | 139.3668 | 25.7168 | 20.65
14526 | Sopworth . SPS | 120 | 1.0185 | 8.4823 | - | 8.4823 | 1587.7371 | 0.12 | 0.7523 | Didmarton . STW | Didmarton . STW | 106 | 0.028846 | 69021.9012 | 12.2081 | 112.36 | 116.19 | 121.81 | 418 | 1586 | 12.2081 | 134.0181 | 21.6581 | 9.45
14441 | Warminster Bishopstrow SPS | 75 | 1.0185 | 3.3134 | - | 3.3134 | 339.361 | 0.075 | 0.7523 | Warminster . STW | Warminster Boreham Road SPS | 106 | 0.028846 | 43138.6883 | 4.8455 | 102.72 | 104.48 | 104.48 | - | 340 | 4.8455 | 109.3255 | 6.6055 | 1.76
17174 | Gillingham Barnaby Mead SPS | 125 | 1.0185 | 9.2039 | - | 9.2039 | 156.0349 | 0.125 | 0.7523 | Gillingham Common Mead Lane STW | Gillingham Buckingham Road SPS | 106 | 0.028846 | 71897.8138 | 1.1375 | 71.83 | 71.51 | 71.83 | 0 | 112 | 1.1375 | 72.9675 | 1.1375 | 0
14480 | Melksham Spa Road SPS | 150 | 1.0185 | 13.2536 | - | 13.2536 | 24.8231 | 0.15 | 0.7523 | Melksham . STW | Melksham . STW | 106 | 0.028846 | 86277.3765 | 0.1428 | 39.54 | 39.51 | 39.65 | 16 | 24 | 0.1428 | 39.7928 | 0.2528 | 0.11
15429 | Halmore . SPS | 75 | 1.0185 | 3.3134 | - | 3.3134 | 944.0119 | 0.075 | 0.7523 | Sharpness . STW | Sharpness . STW | 106 | 0.028846 | 43138.6883 | 13.479 | 14.41 | 21.44 | 21.44 | - | 938 | 13.479 | 34.919 | 20.509 | 7.03
14485 | Monkton Farleigh Farleigh Wick SPS | 50 | 0.99537 | 1.4726 | - | 1.4726 | 1252.6742 | 0.05 | 0.7523 | Saltford Mead Lane STW | Monkton Farleigh Church Farm SPS | 104 | 0.028846 | 28759.1255 | 30.8043 | 115.56 | 136.63 | 136.69 | - | 1252 | 30.8043 | 167.4943 | 51.9343 | 21.13
15693 | Fordingbridge Burgate Fields Burgate School SPS | 100 | 0.99537 | 5.8905 | - | 5.8905 | 64.2242 | 0.1 | 0.7523 | Fordingbridge Frog Lane STW | Fordingbridge Green Lane SPS | 104 | 0.028846 | 57518.251 | 0.627 | 30.63 | 30.49 | 30.74 | 22 | 64 | 0.627 | 31.367 | 0.737 | 0.11
14379 | Fiddington . SPS | 100 | 0.99537 | 5.8905 | 5.3 | 5.3 | 949.6534 | 0.1 | 0.67688 | Nether Stowey . STW | Nether Stowey . STW | 104 | 0.023352 | 51752.3883 | 7.5422 | 24.48 | 43.8 | 44.57 | - | 948 | 7.5422 | 52.1122 | 27.6322 | 20.09
15040 | Christchurch Wilverley Road SPS | 100 | 0.99537 | 5.8905 | - | 5.8905 | 2.6929 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Scotts Hill Lane SPS | 104 | 0.028846 | 57518.251 | 0.02629 | 7.42 | 7.43 | 7.43 | 2 | 2 | 0.02629 | 7.4563 | 0.03629 | 0.01
15615 | High Littleton Beaufort Park Gores Yard SPS | 100 | 0.97222 | 5.8905 | - | 5.8905 | 255.7262 | 0.1 | 0.7523 | Paulton . STW | Paulton . STW | 101 | 0.028846 | 57518.251 | 2.4966 | 136.1 | 139.1 | 139.3 | 226 | 256 | 2.4966 | 141.7966 | 5.6966 | 3.2
14048 | Beechingstoke . SPS | 100 | 0.97222 | 5.8905 | - | 5.8905 | 1570.7113 | 0.1 | 0.7523 | Marden . STW | Marden Hatfields SPS | 101 | 0.028846 | 57518.251 | 15.3344 | 106.61 | 105.06 | 110.01 | 1026 | 1566 | 15.3344 | 125.3444 | 18.7344 | 3.4
15123 | Seend Bell Inn / Bell Hill SPS | 120 | 0.97222 | 8.4823 | 4 | 4 | 315.9054 | 0.12 | 0.35476 | Seend . STW | Seend . STW | 101 | 0.0064146 | 32548.6719 | 0.56449 | 73.56 | 92.28 | 92.56 | - | 318 | 0.56449 | 93.1245 | 19.5645 | 19
14150 | Great Somerford Dauntsey Road SPS | 115 | 0.97222 | 7.7902 | - | 7.7902 | 453.307 | 0.115 | 0.7523 | Great Somerford . STW | Great Somerford Frog Lane SPS | 101 | 0.028846 | 66145.9887 | 3.6847 | 58.62 | 59.23 | 59.95 | 320 | 450 | 3.6847 | 63.6347 | 5.0147 | 1.33
15475 | Thornford Blackbirds SPS | 100 | 0.97222 | 5.8905 | - | 5.8905 | 93.3866 | 0.1 | 0.7523 | Thornford Bridge Halt STW | Thornford Bridge Halt STW | 101 | 0.028846 | 57518.251 | 0.91171 | 54.32 | 54.86 | 54.86 | - | 94 | 0.91171 | 55.7717 | 1.4517 | 0.54
14023 | Bristol Ironmould Lane SPS | 100 | 0.97222 | 5.8905 | - | 5.8905 | 154.0052 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Broomhill Road SPS | 101 | 0.028846 | 57518.251 | 1.5035 | 48.94 | 52.96 | 53.13 | 142 | 154 | 1.5035 | 54.6335 | 5.6935 | 4.19
14540 | Bradford-On-Avon Weavers Brook / St Aldhelms SPS | 150 | 0.97222 | 13.2536 | - | 13.2536 | 503.543 | 0.15 | 0.7523 | Bradford-On-Avon . STW | Bradford-On-Avon Barton Farm Terminal P Stn SPS | 101 | 0.028846 | 86277.3765 | 2.8967 | 44.25 | 52.67 | 52.74 | - | 504 | 2.8967 | 55.6367 | 11.3867 | 8.49
14318 | Downton Mesh Ponds SPS | 100 | 0.97222 | 5.8905 | - | 5.8905 | 276.5804 | 0.1 | 0.7523 | Downton Moot Lane STW | Downton South Lane SPS | 101 | 0.028846 | 57518.251 | 2.7002 | 36.05 | 36.16 | 36.34 | 258 | 276 | 2.7002 | 39.0402 | 2.9902 | 0.29
15433 | Berkeley Berkeley Heath SPS | 75 | 0.97222 | 3.3134 | - | 3.3134 | 554.5059 | 0.075 | 0.7523 | Sharpness . STW | Berkeley Mobley SPS | 101 | 0.028846 | 43138.6883 | 7.9175 | 19.99 | 29.39 | 29.39 | - | 550 | 7.9175 | 37.3075 | 17.3175 | 9.4
14003 | Bath Newbridge Caravan Site SPS | 100 | 0.97222 | 5.8905 | - | 5.8905 | 143.1482 | 0.1 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 101 | 0.028846 | 57518.251 | 1.3975 | 16.91 | 18.43 | 18.43 | 144 | 144 | 1.3975 | 19.8275 | 2.9175 | 1.52
15692 | Isle Brewers . SPS | 100 | 0.97222 | 5.8905 | - | 5.8905 | 1190.3568 | 0.1 | 0.7523 | Fivehead . STW | Isle Abbotts Two Bridges SPS | 101 | 0.028846 | 57518.251 | 11.6211 | 11.74 | 17.07 | 17.08 | - | 1190 | 11.6211 | 28.7011 | 16.9611 | 5.34
17190 | Guys Marsh . SPS | 180 | 0.97222 | 19.0852 | - | 19.0852 | 1928.5774 | 0.18 | 0.7523 | Shaftesbury Gears Mill STW | Shaftesbury Gears Mill STW | 101 | 0.028846 | 103532.8518 | 8.7674 | - | 126.59 | 126.68 | - | 1918 | 8.7674 | 135.4474 | - | -
15782 | Keynsham Dapps Hill SPS | 100 | 0.94907 | 5.8905 | - | 5.8905 | 62.8756 | 0.1 | 0.7523 | Keynsham . STW | Keynsham Keynsham Low Level SPS | 99 | 0.028846 | 57518.251 | 0.61384 | 14.22 | 14.87 | 15.72 | 48 | 62 | 0.61384 | 16.3338 | 2.1138 | 1.5
19986 | Weymouth Greenhill SPS | 100 | 0.94907 | 5.8905 | - | 5.8905 | 81.0838 | 0.1 | 0.7523 | Weymouth . STW | Weymouth Radipole SPS | 99 | 0.028846 | 57518.251 | 0.7916 | 2.15 | 4.27 | 4.38 | 80 | 82 | 0.7916 | 5.1716 | 3.0216 | 2.23
12285 | Creech St Michael Sweeting Close SPS | 110 | 0.94907 | 7.1275 | - | 7.1275 | 263.2432 | 0.11 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 99 | 0.028846 | 63270.0761 | 2.2679 | - | - | - | - | - | 2.2679 | - | - | -
19950 | Malmesbury Park Road SPS | 120 | 0.92592 | 8.4823 | - | 8.4823 | 107.8033 | 0.12 | 0.7523 | Malmesbury . STW | Malmesbury St Johns Street SPS | 96 | 0.028846 | 69021.9012 | 0.8289 | 72.74 | 73.94 | 73.94 | 106 | 106 | 0.8289 | 74.7689 | 2.0289 | 1.2
14463 | Atworth Purlpit SPS | 100 | 0.92592 | 5.8905 | - | 5.8905 | 126.1208 | 0.1 | 0.7523 | Melksham . STW | Melksham . STW | 96 | 0.028846 | 57518.251 | 1.2313 | 51.39 | 53.93 | 53.93 | 126 | 126 | 1.2313 | 55.1613 | 3.7713 | 2.54
14284 | Hardington Mandeville Bendford Bridge SPS | 100 | 0.92592 | 5.8905 | - | 5.8905 | 463.2061 | 0.1 | 0.7523 | Hardington Mandeville Wimborough Lane STW | Hardington Mandeville Wimborough Lane STW | 96 | 0.028846 | 57518.251 | 4.5222 | 44.06 | 47.5 | 47.5 | - | 464 | 4.5222 | 52.0222 | 7.9622 | 3.44
14542 | Coat Cripple Street (Old Stw Site) SPS | 100 | 0.92592 | 5.8905 | 2.2 | 2.2 | 1253.3055 | 0.1 | 0.28097 | Martock Hurst Bow STW | Martock Hurst Bow STW | 96 | 0.0040237 | 21482.1234 | 1.8197 | 13.4 | 13.61 | 18.67 | 366 | 1254 | 1.8197 | 20.4897 | 7.0897 | 5.27
15607 | Kewstoke Norton Lane SPS | 100 | 0.92592 | 5.8905 | - | 5.8905 | 868.591 | 0.1 | 0.7523 | Wick St Lawrence . STW | Kewstoke Crooks Lane SPS | 96 | 0.028846 | 57518.251 | 8.4798 | 6.42 | 5.63 | 7.18 | 218 | 868 | 8.4798 | 15.6598 | 9.2398 | 0.76
15527 | Dunkerton Brooklands SPS | 100 | 0.90278 | 5.8905 | 3.8 | 3.8 | 1036.6194 | 0.1 | 0.48531 | Cam Valley Dunkerton STW | Cam Valley Dunkerton STW | 94 | 0.012005 | 37105.4859 | 4.3097 | 53.55 | 65.43 | 65.43 | 1036 | 1036 | 4.3097 | 69.7397 | 16.1897 | 11.88
15786 | North Petherton Newton Road SPS | 75 | 0.90278 | 3.3134 | - | 3.3134 | 186.795 | 0.075 | 0.7523 | North Petherton . STW | North Petherton . STW | 94 | 0.028846 | 43138.6883 | 2.6671 | 34.38 | 37.18 | 37.18 | 186 | 186 | 2.6671 | 39.8471 | 5.4671 | 2.8
14393 | Hillfarrance . SPS | 100 | 0.90278 | 5.8905 | - | 5.8905 | 1605.818 | 0.1 | 0.7523 | Bradford On Tone . STW | Bradford On Tone . STW | 94 | 0.028846 | 57518.251 | 15.6772 | 31.21 | 30.68 | 32.79 | 678 | 1604 | 15.6772 | 48.4672 | 17.2572 | 1.58
19959 | Wimborne Henbest Close SPS | 80 | 0.90278 | 3.7699 | - | 3.7699 | 108.0147 | 0.08 | 0.7523 | Wimborne Brook Road STW | Wimborne Hayes Lane Colehill SPS | 94 | 0.028846 | 46014.6008 | 1.4157 | 16.74 | 17.66 | 17.7 | 106 | 108 | 1.4157 | 19.1157 | 2.3757 | 0.96
12715 | Yeovil Southfield Drive SPS | 125 | 0.90278 | 9.2039 | - | 9.2039 | 177.9694 | 0.125 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Sherborne Road (Pen Mill) STW | 94 | 0.028846 | 71897.8138 | 1.2975 | - | - | - | - | - | 1.2975 | - | - | -
15772 | Peasedown St John Wellow Lane SPS | 250 | 0.87963 | 36.8155 | 70 | 70 | 1069.3888 | 0.25 | 1.4304 | Cam Valley Dunkerton STW | Cam Valley Dunkerton STW | 92 | 0.10428 | 273408.8438 | 11.2969 | 137.87 | 169.68 | 169.7 | 1062 | 1070 | 11.2969 | 180.9969 | 43.1269 | 31.83
15107 | Wilsford . SPS | 100 | 0.87963 | 5.8905 | - | 5.8905 | 1176.2898 | 0.1 | 0.7523 | Marden . STW | Marden . STW | 92 | 0.028846 | 57518.251 | 11.4838 | 103 | 105.02 | 106.54 | 840 | 1174 | 11.4838 | 118.0238 | 15.0238 | 3.54
19951 | Calne Dalgety Site Quemerford SPS | 100 | 0.87963 | 5.8905 | - | 5.8905 | 12.3846 | 0.1 | 0.7523 | Calne . STW | Calne . STW | 92 | 0.028846 | 57518.251 | 0.12091 | 79.42 | 79.17 | 79.49 | - | 12 | 0.12091 | 79.6109 | 0.19091 | 0.07
17431 | Chalbury Tower Close SPS | 90 | 0.87963 | 4.7713 | - | 4.7713 | 301.8219 | 0.09 | 0.7523 | Gaunts Common . STW | Gaunts Common Horseshoes SPS | 92 | 0.028846 | 51766.4259 | 3.3851 | 61.84 | 67.48 | 67.87 | - | 302 | 3.3851 | 71.2551 | 9.4151 | 6.03
14061 | Bristol Marshfield Park SPS | 50 | 0.87963 | 1.4726 | - | 1.4726 | 85.3353 | 0.05 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 92 | 0.028846 | 28759.1255 | 2.0985 | 48.38 | 49.11 | 49.11 | 86 | 86 | 2.0985 | 51.2085 | 2.8285 | 0.73
15887 | Bath Newton Road SPS | 100 | 0.87963 | 5.8905 | - | 5.8905 | 254.4418 | 0.1 | 0.7523 | Saltford Mead Lane STW | Bath Ea Depot SPS | 92 | 0.028846 | 57518.251 | 2.484 | 35.15 | 49.34 | 49.34 | 254 | 254 | 2.484 | 51.824 | 16.674 | 14.19
14242 | Morden Hectors Corner SPS | 100 | 0.87963 | 5.8905 | - | 5.8905 | 361.9874 | 0.1 | 0.7523 | Blackheath . STW | Morden Cock And Bottle SPS | 92 | 0.028846 | 57518.251 | 3.534 | 35 | 41.05 | 45.27 | - | 362 | 3.534 | 48.804 | 13.804 | 10.27
15703 | Babcary Orchard Cottage SPS | 100 | 0.87963 | 5.8905 | - | 5.8905 | 235.2886 | 0.1 | 0.7523 | Babcary . STW | Babcary Riverside Farm SPS | 92 | 0.028846 | 57518.251 | 2.2971 | 21.69 | 21.9 | 23.25 | 160 | 236 | 2.2971 | 25.5471 | 3.8571 | 1.56
15562 | Weymouth Bowleaze Cove SPS | 150 | 0.87963 | 13.2536 | - | 13.2536 | 116.5154 | 0.15 | 0.7523 | Weymouth . STW | Weymouth Preston Fisherbridge Estate SPS | 92 | 0.028846 | 86277.3765 | 0.67028 | 4.75 | 11.42 | 11.42 | 116 | 116 | 0.67028 | 12.0903 | 7.3403 | 6.67
15148 | Acton Turville Badminton Station SPS | 95 | 0.85648 | 5.3162 | - | 5.3162 | 356.8283 | 0.095 | 0.7523 | Great Badminton . STW | Acton Turville School Luckington Road SPS | 89 | 0.028846 | 54642.3385 | 3.7268 | 119.51 | 128.36 | 128.44 | 344 | 358 | 3.7268 | 132.1668 | 12.6568 | 8.93
17632 | Portland Easton Square SPS | 100 | 0.85648 | 5.8905 | - | 5.8905 | 16.3997 | 0.1 | 0.7523 | Weymouth . STW | Portland Victoria Square SPS | 89 | 0.028846 | 57518.251 | 0.16011 | 80.21 | 81.05 | 81.06 | 6 | 8 | 0.16011 | 81.2201 | 1.0101 | 0.85
15809 | Curry Rivel Westfield Ejector Station SPS | 150 | 0.85648 | 13.2536 | - | 13.2536 | 88.8745 | 0.15 | 0.7523 | Langport Portfield Lane STW | Drayton Ducks Lane SPS | 89 | 0.028846 | 86277.3765 | 0.51127 | 54.45 | 57.84 | 57.84 | 88 | 88 | 0.51127 | 58.3513 | 3.9013 | 3.39
15225 | Fordingbridge Horseport SPS | 75 | 0.85648 | 3.3134 | - | 3.3134 | 159.2319 | 0.075 | 0.7523 | Fordingbridge Frog Lane STW | Fordingbridge Frog Lane STW | 89 | 0.028846 | 43138.6883 | 2.2736 | 25.93 | 25.56 | 25.98 | 2 | 152 | 2.2736 | 28.2536 | 2.3236 | 0.05
14292 | Ilchester Ilchester Mead SPS | 100 | 0.85648 | 5.8905 | - | 5.8905 | 666.9618 | 0.1 | 0.7523 | Ilchester Pill Bridge Lane STW | Ilchester Ilchester Main SPS | 89 | 0.028846 | 57518.251 | 6.5114 | 11.77 | 12.11 | 19.29 | 476 | 666 | 6.5114 | 25.8014 | 14.0314 | 7.52
15603 | St Georges Goosey Lane SPS | 80 | 0.85648 | 3.7699 | - | 3.7699 | 30.5163 | 0.08 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 89 | 0.028846 | 46014.6008 | 0.39995 | 5.43 | 5.56 | 5.91 | 18 | 30 | 0.39995 | 6.31 | 0.87995 | 0.48
15025 | Christchurch Links Drive SPS | 100 | 0.85648 | 5.8905 | - | 5.8905 | 150.3287 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Lodge Road SPS | 89 | 0.028846 | 57518.251 | 1.4676 | 4.97 | 5.96 | 5.96 | 150 | 150 | 1.4676 | 7.4276 | 2.4576 | 0.99
13216 | Monkton Deverill High Street SPS | 100 | 0.83333 | 5.8905 | - | 5.8905 | 429.9633 | 0.1 | 0.7523 | Monkton Deverill Hindon Road STW | Monkton Deverill Hindon Road STW | 87 | 0.028846 | 57518.251 | 4.1976 | 127.36 | 132.18 | 132.18 | 426 | 426 | 4.1976 | 136.3776 | 9.0176 | 4.82
14314 | Amesbury South Mill Lane SPS | 75 | 0.83333 | 3.3134 | - | 3.3134 | 105.0267 | 0.075 | 0.7523 | 13008amesbury Off Church Street STW | Amesbury Flower Lane SPS | 87 | 0.028846 | 43138.6883 | 1.4996 | 67.59 | 69.28 | 69.28 | 106 | 106 | 1.4996 | 70.7796 | 3.1896 | 1.69
19175 | Alderbury Firs Road SPS | 100 | 0.83333 | 5.8905 | - | 5.8905 | 84.522 | 0.1 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Alderbury Home Farm SPS | 87 | 0.028846 | 57518.251 | 0.82517 | 67.18 | 67.97 | 67.97 | 84 | 84 | 0.82517 | 68.7952 | 1.6152 | 0.79
17137 | Crossways Hybris Business Park SPS | 100 | 0.83333 | 5.8905 | - | 5.8905 | 401.4619 | 0.1 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 87 | 0.028846 | 57518.251 | 3.9194 | 53.07 | 59.91 | 61.65 | 374 | 402 | 3.9194 | 65.5694 | 12.4994 | 8.58
14352 | Laverstock Drakes Store SPS | 100 | 0.83333 | 5.8905 | - | 5.8905 | 73.7983 | 0.1 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 87 | 0.028846 | 57518.251 | 0.72047 | 48.43 | 49.62 | 49.62 | - | 74 | 0.72047 | 50.3405 | 1.9105 | 1.19
14454 | Midford Boathouse SPS | 50 | 0.83333 | 1.4726 | - | 1.4726 | 721.3156 | 0.05 | 0.7523 | Freshford . STW | Freshford . STW | 87 | 0.028846 | 28759.1255 | 17.7378 | 25.78 | 32.1 | 32.1 | 722 | 722 | 17.7378 | 49.8378 | 24.0578 | 6.32
15622 | Clevedon Marine Parade SPS | 150 | 0.83333 | 13.2536 | 42 | 42 | 46.6686 | 0.15 | 2.384 | Kingston Seymour Back Lane STW | Clevedon The Beach SPS | 87 | 0.28968 | 273408.8438 | 2.6096 | 10.73 | 28.14 | 28.14 | - | 44 | 2.6096 | 30.7496 | 20.0196 | 17.41
14034 | Hurn Moors Close SPS | 100 | 0.83333 | 5.8905 | - | 5.8905 | 63.0317 | 0.1 | 0.7523 | Hurn Moors Close STW | Hurn Moors Close STW | 87 | 0.028846 | 57518.251 | 0.61536 | 7.68 | 10.09 | 10.13 | 60 | 64 | 0.61536 | 10.7454 | 3.0654 | 2.45
15803 | Bleadon Bleadon Mill SPS | 100 | 0.83333 | 5.8905 | - | 5.8905 | 30.4149 | 0.1 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Bleadon Bleadon Bridge SPS | 87 | 0.028846 | 57518.251 | 0.29693 | 7.39 | 7.19 | 7.49 | 12 | 30 | 0.29693 | 7.7869 | 0.39693 | 0.1
15458 | Stoke St Gregory Curload SPS | 50 | 0.83333 | 1.4726 | 2.2 | 2.2 | 532.9852 | 0.05 | 1.1239 | Stoke St Gregory . STW | Stoke St Gregory . STW | 87 | 0.064379 | 42964.2469 | 28.7878 | 5.19 | 30.7 | 30.7 | 534 | 534 | 28.7878 | 59.4878 | 54.2978 | 25.51
19725 | Kimmeridge . SPS | 120 | 0.83333 | 8.4823 | - | 8.4823 | 3545.5178 | 0.12 | 0.7523 | Corfe Castle Wytch Farm Road STW | Church Knowle Animal Sanctuary SPS | 87 | 0.028846 | 69021.9012 | 27.2615 | - | 50.15 | 108.99 | - | 3522 | 27.2615 | 136.2515 | - | -
15535 | Peasedown St John New Buildings / Whitebrook Lane SPS | 75 | 0.81018 | 3.3134 | 3.9 | 3.9 | 398.7411 | 0.075 | 0.88548 | Cam Valley Dunkerton STW | Cam Valley Dunkerton STW | 84 | 0.039963 | 50775.9281 | 7.8335 | 117.45 | 158.83 | 158.83 | 398 | 398 | 7.8335 | 166.6635 | 49.2135 | 41.38
14451 | Westwood Lower Westwood SPS | 100 | 0.81018 | 5.8905 | - | 5.8905 | 438.4294 | 0.1 | 0.7523 | Westwood . STW | Westwood . STW | 84 | 0.028846 | 57518.251 | 4.2803 | 65.22 | 74.46 | 74.46 | - | 438 | 4.2803 | 78.7403 | 13.5203 | 9.24
15267 | Poole Queen Anne Drive SPS | 100 | 0.81018 | 5.8905 | - | 5.8905 | 295.989 | 0.1 | 0.7523 | Wimborne Brook Road STW | Canford Magna Canford Main SPS | 84 | 0.028846 | 57518.251 | 2.8897 | 38.59 | 45.24 | 45.4 | 282 | 296 | 2.8897 | 48.2897 | 9.6997 | 6.81
19818 | Blagdon Hill . SPS | 90 | 0.78704 | 4.7713 | - | 4.7713 | 416.8057 | 0.09 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Pitminster Weir SPS | 82 | 0.028846 | 51766.4259 | 4.6747 | 110.11 | 112.52 | 112.54 | 408 | 410 | 4.6747 | 117.2147 | 7.1047 | 2.43
15095 | Stert Fullaway Farm SPS | 100 | 0.78704 | 5.8905 | - | 5.8905 | 890.6002 | 0.1 | 0.7523 | Urchfont . STW | Lydeway Clock Inn SPS | 82 | 0.028846 | 57518.251 | 8.6947 | 109.21 | 110.46 | 111.76 | 432 | 888 | 8.6947 | 120.4547 | 11.2447 | 2.55
14620 | Pewsey Salisbury Road SPS | 150 | 0.78704 | 13.2536 | - | 13.2536 | 292.6589 | 0.15 | 0.7523 | Pewsey Salisbury Road STW | Pewsey Salisbury Road STW | 82 | 0.028846 | 86277.3765 | 1.6836 | 106.45 | 106.66 | 107.81 | 46 | 274 | 1.6836 | 109.4936 | 3.0436 | 1.36
15129 | Potterne Wick SPS | 125 | 0.78704 | 9.2039 | 6.4 | 6.4 | 755.6778 | 0.125 | 0.52312 | Potterne . STW | Potterne . STW | 82 | 0.013948 | 49994.76 | 2.7128 | 71.5 | 105.96 | 108.72 | - | 744 | 2.7128 | 111.4328 | 39.9328 | 37.22
14192 | Upper Seagry Upper Seagry SPS | 50 | 0.78704 | 1.4726 | - | 1.4726 | 177.7268 | 0.05 | 0.7523 | Sutton Benger . STW | Sutton Benger . STW | 82 | 0.028846 | 28759.1255 | 4.3705 | 65.21 | 74.71 | 77.18 | 176 | 304 | 4.3705 | 81.5505 | 16.3405 | 11.97
14445 | Wingfield Wingfield Common SPS | 38 | 0.78704 | 0.85059 | - | 0.85059 | 297.2494 | 0.038 | 0.7523 | Trowbridge Bradford Road STW | Wingfield Church Lane SPS | 82 | 0.028846 | 21856.9354 | 10.622 | 56.21 | 55.79 | 56.31 | - | 298 | 10.622 | 66.932 | 10.722 | 0.1
15445 | Nynehead . SPS | 75 | 0.78704 | 3.3134 | - | 3.3134 | 623.6662 | 0.075 | 0.7523 | Nynehead . STW | Nynehead . STW | 82 | 0.028846 | 43138.6883 | 8.905 | 47.77 | 62.58 | 64.94 | 528 | 624 | 8.905 | 73.845 | 26.075 | 17.17
15459 | Rumwell . SPS | 100 | 0.78704 | 5.8905 | 6.93 | 6.93 | 438.4523 | 0.1 | 0.88506 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Mountway Bishops Hull SPS | 82 | 0.039925 | 67668.6888 | 5.8847 | 40.35 | 67.34 | 67.36 | 436 | 438 | 5.8847 | 73.2447 | 32.8947 | 27.01
17548 | Abbots Leigh . SPS | 125 | 0.78704 | 9.2039 | - | 9.2039 | 624.7712 | 0.125 | 0.7523 | Avonmouth Kingsweston Lane STW | Pill Avon Road SPS | 82 | 0.028846 | 71897.8138 | 4.5548 | 30.44 | 31.42 | 31.61 | 602 | 624 | 4.5548 | 36.1648 | 5.7248 | 1.17
15087 | St Leonards Wayside Road No 2 SPS | 100 | 0.78704 | 5.8905 | - | 5.8905 | 556.5195 | 0.1 | 0.7523 | Palmersford . STW | St Leonards Wayside Road No 1 SPS | 82 | 0.028846 | 57518.251 | 5.4331 | 19.1 | 22.22 | 22.22 | 556 | 556 | 5.4331 | 27.6531 | 8.5531 | 3.12
14591 | Compton Bishop Big Tree Close SPS | 80 | 0.78704 | 3.7699 | - | 3.7699 | 1067.2748 | 0.08 | 0.7523 | Cheddar . STW | Cross Cross West Old Coach Road SPS | 82 | 0.028846 | 46014.6008 | 13.9878 | 13.95 | 8.51 | 18.97 | 80 | 1068 | 13.9878 | 32.9578 | 19.0078 | 5.02
19283 | Baltonsborough Perrys Leat Mill Street SPS | 120 | 0.78704 | 8.4823 | - | 8.4823 | 372.7183 | 0.12 | 0.7523 | Butleigh . STW | Baltonsborough Baltonsborough Main SPS | 82 | 0.028846 | 69021.9012 | 2.8658 | 13.35 | 15.71 | 15.71 | 366 | 366 | 2.8658 | 18.5758 | 5.2258 | 2.36
17031 | Lympsham Rectory Way SPS | 110 | 0.78704 | 7.1275 | - | 7.1275 | 359.9852 | 0.11 | 0.7523 | West Huntspill STW | Lympsham Worthy Crescent SPS | 82 | 0.028846 | 63270.0761 | 3.1014 | 5.69 | 5.68 | 5.9 | 292 | 360 | 3.1014 | 9.0014 | 3.3114 | 0.21
10234 | Sturminster Marshall Henbury House Gardens SPS | - | 0.78704 | - | - | - | 0 | - | - | - | - | 82 | - | - | - | - | - | - | - | - | - | - | - | -
19925 | Woodfalls Elmfield Close SPS | 100 | 0.76389 | 5.8905 | - | 5.8905 | 101.098 | 0.1 | 0.7523 | Downton Moot Lane STW | Downton Moot Lane STW | 80 | 0.028846 | 57518.251 | 0.98699 | 107.66 | 111.99 | 111.99 | 102 | 102 | 0.98699 | 112.977 | 5.317 | 4.33
19178 | South Petherton Lampreys Lane SPS | 100 | 0.76389 | 5.8905 | - | 5.8905 | 147.2658 | 0.1 | 0.7523 | South Petherton North Street STW | South Petherton North Street STW | 80 | 0.028846 | 57518.251 | 1.4377 | 39.79 | 40.65 | 40.74 | 128 | 148 | 1.4377 | 42.1777 | 2.3877 | 0.95
14007 | Bath Darlington Road SPS | 100 | 0.76389 | 5.8905 | - | 5.8905 | 154.5292 | 0.1 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 80 | 0.028846 | 57518.251 | 1.5086 | 35.94 | 48.29 | 48.29 | 154 | 154 | 1.5086 | 49.7986 | 13.8586 | 12.35
15612 | Backwell Backwell Common SPS | 80 | 0.76389 | 3.7699 | - | 3.7699 | 312.2129 | 0.08 | 0.7523 | Kingston Seymour Back Lane STW | Kenn Kenn Pier SPS | 80 | 0.028846 | 46014.6008 | 4.0919 | 12.43 | 13.29 | 14.17 | 208 | 312 | 4.0919 | 18.2619 | 5.8319 | 1.74
19781 | Lympsham Boat Lane SPS | 110 | 0.76389 | 7.1275 | - | 7.1275 | 124.1715 | 0.11 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Lympsham Hobbs Boat SPS | 80 | 0.028846 | 63270.0761 | 1.0698 | 6.03 | 6.47 | 6.54 | - | 122 | 1.0698 | 7.6098 | 1.5798 | 0.51
15529 | Timsbury Somerset Folly SPS | 50 | 0.74074 | 1.4726 | - | 1.4726 | 148.2139 | 0.05 | 0.7523 | Cam Valley Dunkerton STW | Carlingcott Stoneage Lane SPS | 77 | 0.028846 | 28759.1255 | 3.6447 | 154.18 | 154.56 | 154.86 | 14 | 148 | 3.6447 | 158.5047 | 4.3247 | 0.68
14203 | Broadtown Thornhill SPS | 100 | 0.74074 | 5.8905 | - | 5.8905 | 779.729 | 0.1 | 0.7523 | Royal Wootton Bassett . STW | Broadtown Cotmarsh Farm SPS | 77 | 0.028846 | 57518.251 | 7.6123 | 99.56 | 100.87 | 102.9 | 256 | 774 | 7.6123 | 110.5123 | 10.9523 | 3.34
12325 | Milborne Port Lion Drive Private SPS | 80 | 0.74074 | 3.7699 | - | 3.7699 | 110.7059 | 0.08 | 0.7523 | Milborne Port Venn Farm STW | Milborne Port Venn Farm STW | 77 | 0.028846 | 46014.6008 | 1.4509 | 77.48 | 78.23 | 78.23 | 24 | 24 | 1.4509 | 79.6809 | 2.2009 | 0.75
14168 | Lower Seagry . SPS | 100 | 0.74074 | 5.8905 | - | 5.8905 | 1405.1848 | 0.1 | 0.7523 | Sutton Benger . STW | Sutton Benger . STW | 77 | 0.028846 | 57518.251 | 13.7184 | 56.5 | 74.49 | 74.84 | 1350 | 1404 | 13.7184 | 88.5584 | 32.0584 | 18.34
15646 | Pitcombe Vale Road SPS | 100 | 0.74074 | 5.8905 | - | 5.8905 | 406.9425 | 0.1 | 0.7523 | Bruton Gants Mill Lane STW | Bruton Gants Mill Lane STW | 77 | 0.028846 | 57518.251 | 3.9729 | 54.51 | 63.13 | 63.25 | - | 406 | 3.9729 | 67.2229 | 12.7129 | 8.74
14264 | East Knighton . SPS | 100 | 0.74074 | 5.8905 | 1 | 1 | 336.8914 | 0.1 | 0.12771 | Wool . STW | East Knighton Blacknoll SPS | 77 | 0.00083134 | 9764.6016 | 0.11076 | 30.88 | 42.19 | 42.25 | 334 | 336 | 0.11076 | 42.3608 | 11.4808 | 11.37
19404 | Nailsea Parish Brook Road (Watery Lane Kingshill Park) SPS | 100 | 0.74074 | 5.8905 | - | 5.8905 | 174.6813 | 0.1 | 0.7523 | Kingston Seymour Back Lane STW | Kenn Kenn Pier SPS | 77 | 0.028846 | 57518.251 | 1.7054 | 6.55 | 9.06 | 10.12 | 166 | 174 | 1.7054 | 11.8254 | 5.2754 | 3.57
14569 | Malmesbury Avon Silk Mills Also S0569 SPS | 100 | 0.71759 | 5.8905 | - | 5.8905 | 64.3517 | 0.1 | 0.7523 | Malmesbury . STW | Malmesbury St Johns Street SPS | 75 | 0.028846 | 57518.251 | 0.62825 | 71.09 | 71.53 | 72.53 | 44 | 64 | 0.62825 | 73.1582 | 2.0682 | 1.44
18715 | Buckhorn Weston Court Cottages SPS | 100 | 0.71759 | 5.8905 | - | 5.8905 | 300.7493 | 0.1 | 0.7523 | Marnhull Common STW | Buckhorn Weston Filley Brook Kington Magna Rd SPS | 75 | 0.028846 | 57518.251 | 2.9361 | 68.42 | 72.85 | 72.94 | 288 | 300 | 2.9361 | 75.8761 | 7.4561 | 4.52
15175 | Frampton Cotterell Medway Drive SPS | 100 | 0.71759 | 5.8905 | - | 5.8905 | 15.0448 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 75 | 0.028846 | 57518.251 | 0.14688 | 55.67 | 55.85 | 55.85 | 16 | 16 | 0.14688 | 55.9969 | 0.32688 | 0.18
15316 | Barton St David Tootal Bridge SPS | 110 | 0.71759 | 7.1275 | 2.4 | 2.4 | 673.41 | 0.11 | 0.25332 | Butleigh . STW | Barton St David . SPS | 75 | 0.0032706 | 21304.5852 | 0.70776 | 14.81 | 19.04 | 20.39 | 526 | 666 | 0.70776 | 21.0978 | 6.2878 | 5.58
14090 | Butleigh Wootton . SPS | 63 | 0.71759 | 2.3379 | - | 2.3379 | 1604.3897 | 0.063 | 0.7523 | Butleigh . STW | Butleigh . STW | 75 | 0.028846 | 36236.4981 | 28.9069 | 14.08 | 30.79 | 33.09 | 408 | 1604 | 28.9069 | 61.9969 | 47.9169 | 19.01
15683 | Burton Bradstock Annings Lane SPS | 100 | 0.71759 | 5.8905 | - | 5.8905 | 423.6934 | 0.1 | 0.7523 | Bridport Wych Farm STW | Burton Bradstock Burton Freshwater SPS | 75 | 0.028846 | 57518.251 | 4.1364 | 12.11 | 14.05 | 14.05 | - | 420 | 4.1364 | 18.1864 | 6.0764 | 1.94
15648 | Portland Portland Bill SPS | 80 | 0.71759 | 3.7699 | 5.5 | 5.5 | 1984.5596 | 0.08 | 1.0975 | Weymouth . STW | Portland Southwell SPS | 75 | 0.061396 | 67131.6358 | 54.5548 | 9.45 | 44.22 | 44.22 | 1984 | 1984 | 54.5548 | 98.7748 | 89.3248 | 34.77
15357 | West Huntspill Grove Road SPS | 100 | 0.71759 | 5.8905 | - | 5.8905 | 36.9924 | 0.1 | 0.7523 | West Huntspill STW | West Huntspill STW | 75 | 0.028846 | 57518.251 | 0.36115 | 6.56 | 6.02 | 6.56 | 0 | 36 | 0.36115 | 6.9211 | 0.36115 | 0
15395 | Bason Bridge Church Road SPS | 150 | 0.71759 | 13.2536 | - | 13.2536 | 56.9069 | 0.15 | 0.7523 | West Huntspill STW | East Huntspill Hackness Road SPS | 75 | 0.028846 | 86277.3765 | 0.32737 | 4.77 | 4.89 | 5.36 | 22 | 56 | 0.32737 | 5.6874 | 0.91737 | 0.59
14109 | Oakhill Fosse Road SPS | 100 | 0.69444 | 5.8905 | - | 5.8905 | 766.3592 | 0.1 | 0.7523 | Oakhill . STW | Oakhill . STW | 72 | 0.028846 | 57518.251 | 7.4818 | 201.35 | 215.28 | 215.28 | - | 766 | 7.4818 | 222.7618 | 21.4118 | 13.93
14204 | Calne Studley SPS | 150 | 0.69444 | 13.2536 | - | 13.2536 | 308.1725 | 0.15 | 0.7523 | Calne . STW | Calne . STW | 72 | 0.028846 | 86277.3765 | 1.7728 | 83.51 | 104.83 | 104.83 | 308 | 308 | 1.7728 | 106.6028 | 23.0928 | 21.32
14155 | Gastard Coppershell SPS | 100 | 0.69444 | 5.8905 | - | 5.8905 | 177.8487 | 0.1 | 0.7523 | Thingley Coppershell Lane STW | Thingley Coppershell Lane STW | 72 | 0.028846 | 57518.251 | 1.7363 | 82.07 | 85.87 | 85.87 | 178 | 178 | 1.7363 | 87.6063 | 5.5363 | 3.8
15113 | Rowde Marsh Lane SPS | 100 | 0.69444 | 5.8905 | - | 5.8905 | 1288.5877 | 0.1 | 0.7523 | Potterne . STW | Poulshot Townsend SPS | 72 | 0.028846 | 57518.251 | 12.5801 | 70.39 | 68.06 | 70.6 | 62 | 1288 | 12.5801 | 83.1801 | 12.7901 | 0.21
14062 | Bristol Crown Gardens SPS | 100 | 0.69444 | 5.8905 | - | 5.8905 | 8.6025 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 72 | 0.028846 | 57518.251 | 0.083984 | 43.17 | 43.25 | 43.25 | 8 | 8 | 0.083984 | 43.334 | 0.16398 | 0.08
14275 | Corfe Castle Halves Cottages SPS | 100 | 0.69444 | 5.8905 | 8 | 8 | 23.2487 | 0.1 | 1.0217 | Corfe Castle Wytch Farm Road STW | Corfe Castle Studland Road SPS | 72 | 0.053206 | 78116.8125 | 0.41364 | 35.52 | 37.38 | 37.38 | 24 | 24 | 0.41364 | 37.7936 | 2.2736 | 1.86
14258 | Bere Regis Elder Road SPS | 100 | 0.69444 | 5.8905 | - | 5.8905 | 68.6926 | 0.1 | 0.7523 | Blackheath . STW | Bere Regis Court Farm Southbrook SPS | 72 | 0.028846 | 57518.251 | 0.67063 | 35.5 | 35.26 | 35.89 | 46 | 68 | 0.67063 | 36.5606 | 1.0606 | 0.39
14135 | Hullavington Parklands SPS | 75 | 0.67129 | 3.3134 | - | 3.3134 | 137.6144 | 0.075 | 0.7523 | Hullavington . STW | Hullavington . STW | 70 | 0.028846 | 43138.6883 | 1.9649 | 100.29 | 103.19 | 103.33 | - | 138 | 1.9649 | 105.2949 | 5.0049 | 3.04
15177 | Wick Rock Road SPS | 150 | 0.67129 | 13.2536 | - | 13.2536 | 174.9613 | 0.15 | 0.7523 | Wick Manor Road STW | Wick Manor Road STW | 70 | 0.028846 | 86277.3765 | 1.0065 | 82.31 | 84.69 | 84.88 | 122 | 174 | 1.0065 | 85.8865 | 3.5765 | 2.57
15489 | Leigh Yetminster Road SPS | 100 | 0.67129 | 5.8905 | - | 5.8905 | 398.7123 | 0.1 | 0.7523 | Thornford Bridge Halt STW | Leigh Frampton Farm SPS | 70 | 0.028846 | 57518.251 | 3.8925 | 72.1 | 82.57 | 82.57 | - | 398 | 3.8925 | 86.4625 | 14.3625 | 10.47
14137 | Great Somerford Hollow Street SPS | 100 | 0.67129 | 5.8905 | - | 5.8905 | 186.8255 | 0.1 | 0.7523 | Great Somerford . STW | Great Somerford Frog Lane SPS | 70 | 0.028846 | 57518.251 | 1.8239 | 65.1 | 67.97 | 67.97 | 186 | 186 | 1.8239 | 69.7939 | 4.6939 | 2.87
15779 | Stocklinch Stockyard SPS | - | 0.67129 | - | - | - | 336.712 | - | - | Ilminster Ashwell STW | Ilford Ilford Bridges SPS | 70 | - | - | - | 28.46 | 34.61 | 34.61 | - | 336 | - | - | - | 6.15
14452 | Freshford New Inn SPS | 120 | 0.67129 | 8.4823 | 5 | 5 | 348.2563 | 0.12 | 0.44345 | Freshford . STW | Freshford . STW | 70 | 0.010023 | 40685.8399 | 0.95722 | 27.6 | 38.66 | 38.66 | 356 | 356 | 0.95722 | 39.6172 | 12.0172 | 11.06
15720 | Norton Fitzwarren Stembridge Way SPS | 75 | 0.67129 | 3.3134 | - | 3.3134 | 126.9858 | 0.075 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Silk Mills SPS | 70 | 0.028846 | 43138.6883 | 1.8132 | 23.17 | 25.17 | 25.31 | 122 | 126 | 1.8132 | 27.1232 | 3.9532 | 2.14
19294 | Martock Oakland Road SPS | 100 | 0.67129 | 5.8905 | - | 5.8905 | 191.4752 | 0.1 | 0.7523 | Martock Hurst Bow STW | Martock Hurst Bow STW | 70 | 0.028846 | 57518.251 | 1.8693 | 18.48 | 20.41 | 20.42 | 186 | 192 | 1.8693 | 22.2893 | 3.8093 | 1.94
17032 | Lympsham Pavilion SPS | 100 | 0.67129 | 5.8905 | - | 5.8905 | 104.0642 | 0.1 | 0.7523 | West Huntspill STW | Lympsham Worthy Crescent SPS | 70 | 0.028846 | 57518.251 | 1.0159 | 5.67 | 5.9 | 5.91 | - | 104 | 1.0159 | 6.9259 | 1.2559 | 0.24
14600 | Highbridge Tylers End SPS | 225 | 0.67129 | 29.8206 | - | 29.8206 | 852.9696 | 0.225 | 0.7523 | West Huntspill STW | Highbridge Newton SPS | 70 | 0.028846 | 129416.0648 | 2.9124 | 5.31 | 5.94 | 11.12 | 730 | 852 | 2.9124 | 14.0324 | 8.7224 | 5.81
17550 | Bridgeyate London Road SPS | 110 | 0.67129 | 7.1275 | - | 7.1275 | 240.1925 | 0.11 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 70 | 0.028846 | 63270.0761 | 2.0693 | - | 61.21 | 61.21 | 236 | 236 | 2.0693 | 63.2793 | - | -
15132 | Wilcot Canal Close SPS | 80 | 0.64815 | 3.7699 | - | 3.7699 | 144.1037 | 0.08 | 0.7523 | Pewsey Salisbury Road STW | Pewsey Wilcot Lodge SPS | 68 | 0.028846 | 46014.6008 | 1.8886 | 129.75 | 130.64 | 132.31 | 104 | 144 | 1.8886 | 134.1986 | 4.4486 | 2.56
17272 | Alderton . SPS | 115 | 0.64815 | 7.7902 | - | 7.7902 | 426.3535 | 0.115 | 0.7523 | Alderton . STW | Alderton . STW | 68 | 0.028846 | 66145.9887 | 3.4656 | 122.19 | 125.3 | 125.3 | - | 422 | 3.4656 | 128.7656 | 6.5756 | 3.11
15565 | Portishead Blackberry Lane (Valley Road) SPS | 100 | 0.64815 | 5.8905 | - | 5.8905 | 285.5953 | 0.1 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Black Nore (Nautical School) SPS | 68 | 0.028846 | 57518.251 | 2.7882 | 91.28 | 104.49 | 105.13 | 236 | 286 | 2.7882 | 107.9182 | 16.6382 | 13.85
17864 | Amesbury Mills Way SPS | 125 | 0.64815 | 9.2039 | - | 9.2039 | 1122.5737 | 0.125 | 0.7523 | 13008amesbury Off Church Street STW | Amesbury Flower Lane SPS | 68 | 0.028846 | 71897.8138 | 8.1839 | 90.56 | 90.64 | 93.78 | 64 | 1122 | 8.1839 | 101.9639 | 11.4039 | 3.22
15781 | Calne Beaversbrook Farm SPS | 150 | 0.64815 | 13.2536 | - | 13.2536 | 89.8654 | 0.15 | 0.7523 | Calne . STW | Calne . STW | 68 | 0.028846 | 86277.3765 | 0.51697 | 79.5 | 80.52 | 80.75 | 6 | 80 | 0.51697 | 81.267 | 1.767 | 1.25
15141 | Rangeworthy Patch Elm Lane SPS | 80 | 0.64815 | 3.7699 | - | 3.7699 | 280.9703 | 0.08 | 0.7523 | Cromhall . STW | Rangeworthy Berrows Mead SPS | 68 | 0.028846 | 46014.6008 | 3.6824 | 69.39 | 69.77 | 70 | 98 | 280 | 3.6824 | 73.6824 | 4.2924 | 0.61
17438 | Gaunts Common Hill Farm SPS | 90 | 0.64815 | 4.7713 | - | 4.7713 | 362.2972 | 0.09 | 0.7523 | Gaunts Common . STW | Gaunts Common . STW | 68 | 0.028846 | 51766.4259 | 4.0634 | 53.23 | 64.19 | 64.19 | - | 362 | 4.0634 | 68.2534 | 15.0234 | 10.96
14481 | Melksham Shaw Hill SPS | 51 | 0.64815 | 1.5321 | - | 1.5321 | 334.9347 | 0.051 | 0.7523 | Melksham . STW | Melksham . STW | 68 | 0.028846 | 29334.308 | 8.0187 | 47.47 | 56.02 | 56.11 | 314 | 336 | 8.0187 | 64.1287 | 16.6587 | 8.64
17833 | Taunton Mill Rise S105a SPS | - | 0.64815 | - | - | - | 9.2167 | - | - | Minehead Headworks STW | Minehead Mart Road SPS | 68 | - | - | - | 32.14 | 32.35 | 32.35 | 10 | 10 | - | - | - | 0.21
19654 | Kingsbury Episcopi The Avenue SPS | - | 0.64815 | - | - | - | 32.1118 | - | - | Martock Hurst Bow STW | Kingsbury Episcopi . SPS | 68 | - | - | - | 13.17 | 13.66 | 13.66 | 32 | 32 | - | - | - | 0.49
14574 | Hewish Palmers Elm SPS | 80 | 0.64815 | 3.7699 | - | 3.7699 | 684.5188 | 0.08 | 0.7523 | Wick St Lawrence . STW | Weston-Super-Mare Field Near Full Quart PSP | 68 | 0.028846 | 46014.6008 | 8.9714 | 5.56 | 5.23 | 5.7 | - | 676 | 8.9714 | 14.6714 | 9.1114 | 0.14
11936 | Coleford Mackintosh View SPS | 125 | 0.64815 | 9.2039 | - | 9.2039 | 190.2009 | 0.125 | 0.7523 | Coleford . STW | Coleford . STW | 68 | 0.028846 | 71897.8138 | 1.3866 | - | - | - | - | - | 1.3866 | - | - | -
19407 | Alton Barnes Honey Street SPS | 100 | 0.625 | 5.8905 | - | 5.8905 | 377.6058 | 0.1 | 0.7523 | Pewsey Salisbury Road STW | Woodborough Ps1 . SPS | 65 | 0.028846 | 57518.251 | 3.6865 | 125.81 | 129.34 | 131.21 | 264 | 378 | 3.6865 | 134.8965 | 9.0865 | 5.4
15581 | Backwell Backwell Green SPS | 50 | 0.625 | 1.4726 | - | 1.4726 | 483.8019 | 0.05 | 0.7523 | Kingston Seymour Back Lane STW | Kenn Kenn Pier SPS | 65 | 0.028846 | 28759.1255 | 11.8971 | 18.49 | 41.44 | 41.44 | 484 | 484 | 11.8971 | 53.3371 | 34.8471 | 22.95
14063 | Kingswood Swineford SPS | 120 | 0.625 | 8.4823 | - | 8.4823 | 672.7044 | 0.12 | 0.7523 | Avonmouth Kingsweston Lane STW | Bitton . SPS | 65 | 0.028846 | 69021.9012 | 5.1724 | 12.78 | 17.05 | 18.76 | - | 672 | 5.1724 | 23.9324 | 11.1524 | 5.98
17405 | Ferndown Gladelands SPS | 80 | 0.625 | 3.7699 | - | 3.7699 | 57.0345 | 0.08 | 0.7523 | Palmersford . STW | Ferndown A31 Tricketts Cross SPS | 65 | 0.028846 | 46014.6008 | 0.7475 | 12.18 | 13.23 | 13.23 | 58 | 58 | 0.7475 | 13.9775 | 1.7975 | 1.05
15174 | Hawkesbury Upton Pool Farm SPS | 100 | 0.60185 | 5.8905 | - | 5.8905 | 259.3186 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Hawkesbury Upton Britain Bottom SPS | 63 | 0.028846 | 57518.251 | 2.5317 | 187.8 | 197.14 | 197.14 | - | 260 | 2.5317 | 199.6717 | 11.8717 | 9.34
14534 | Hinton Blewitt Glanville Farm SPS | - | 0.60185 | - | - | - | 156.1136 | - | - | Hinton Blewett . STW | Hinton Blewett . STW | 63 | - | - | - | 135.43 | 134.81 | 135.77 | 4 | 156 | - | - | - | 0.34
19629 | Charlton Musgrove Dibbens Row SPS | 125 | 0.60185 | 9.2039 | - | 9.2039 | 213.4647 | 0.125 | 0.7523 | Charlton Musgrove Barrow Lane STW | Charlton Musgrove Barrow Lane STW | 63 | 0.028846 | 71897.8138 | 1.5562 | 105.12 | 108.15 | 108.23 | - | 214 | 1.5562 | 109.7862 | 4.6662 | 3.11
14458 | North Bradley Churchlands SPS | 120 | 0.60185 | 8.4823 | 6 | 6 | 198.4349 | 0.12 | 0.53214 | Trowbridge Bradford Road STW | Trowbridge Terminal At Bradford Road SPS | 63 | 0.014433 | 48823.0078 | 0.77675 | 48.35 | 51.47 | 51.81 | 170 | 198 | 0.77675 | 52.5868 | 4.2368 | 3.46
19953 | Bristol Imperial Grounds Brislington SPS | 100 | 0.60185 | 5.8905 | - | 5.8905 | 48.2373 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Dalby Ave SPS | 63 | 0.028846 | 57518.251 | 0.47093 | 30.22 | 30.09 | 30.33 | 20 | 48 | 0.47093 | 30.8009 | 0.58093 | 0.11
19699 | Bovington Lytchett Lane SPS | 125 | 0.60185 | 9.2039 | 10 | 10 | 280.411 | 0.125 | 0.81737 | Wool . STW | Bovington Terminal SPS | 63 | 0.034052 | 78116.8125 | 2.4048 | 19.64 | 27.61 | 27.76 | 242 | 280 | 2.4048 | 30.1648 | 10.5248 | 8.12
14571 | Sandford Organford Road SPS | 80 | 0.60185 | 3.7699 | - | 3.7699 | 558.1285 | 0.08 | 0.7523 | Wareham Keysworth Drive STW | Sandford Heath Cottages SPS | 63 | 0.028846 | 46014.6008 | 7.3149 | 10.91 | 16.79 | 16.79 | 554 | 554 | 7.3149 | 24.1049 | 13.1949 | 5.88
15423 | Purton Waterworks SPS | 100 | 0.60185 | 5.8905 | - | 5.8905 | 307.7561 | 0.1 | 0.7523 | Sharpness . STW | Purton Hinton Road SPS | 63 | 0.028846 | 57518.251 | 3.0045 | 9.88 | 12.82 | 12.82 | - | 304 | 3.0045 | 15.8245 | 5.9445 | 2.94
15594 | Clevedon Marshalls Field SPS | 75 | 0.60185 | 3.3134 | - | 3.3134 | 6.3242 | 0.075 | 0.7523 | Kingston Seymour Back Lane STW | Clevedon Clevedon Main SPS | 63 | 0.028846 | 43138.6883 | 0.090299 | 5.66 | 5.78 | 5.78 | 6 | 6 | 0.090299 | 5.8703 | 0.2103 | 0.12
15478 | Charminster Cocklands SPS | 100 | 0.5787 | 5.8905 | - | 5.8905 | 658.9549 | 0.1 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Charminster North Street SPS | 60 | 0.028846 | 57518.251 | 6.4332 | 66.25 | 73.57 | 73.57 | 658 | 658 | 6.4332 | 80.0032 | 13.7532 | 7.32
14143 | Great Somerford West Street SPS | 100 | 0.5787 | 5.8905 | - | 5.8905 | 111.9713 | 0.1 | 0.7523 | Great Somerford . STW | Great Somerford Frog Lane SPS | 60 | 0.028846 | 57518.251 | 1.0931 | 64.82 | 65.11 | 65.15 | 120 | 122 | 1.0931 | 66.2431 | 1.4231 | 0.33
15254 | Poole Ashwood Drive SPS | 100 | 0.5787 | 5.8905 | - | 5.8905 | 172.4728 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 60 | 0.028846 | 57518.251 | 1.6838 | 48.3 | 69.96 | 69.96 | 172 | 172 | 1.6838 | 71.6438 | 23.3438 | 21.66
15533 | Monkton Combe Mill Lane SPS | 60 | 0.5787 | 2.1206 | - | 2.1206 | 136.9918 | 0.06 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 60 | 0.028846 | 34510.9506 | 2.635 | 35.06 | 47.73 | 47.73 | 136 | 136 | 2.635 | 50.365 | 15.305 | 12.67
19536 | Nailsea Elm Farm SPS | 100 | 0.5787 | 5.8905 | - | 5.8905 | 47.8523 | 0.1 | 0.7523 | Kingston Seymour Back Lane STW | Kenn Kenn Pier SPS | 60 | 0.028846 | 57518.251 | 0.46717 | 18.03 | 18.4 | 18.4 | 48 | 48 | 0.46717 | 18.8672 | 0.83717 | 0.37
17489 | Longham High Mead Lane SPS | 125 | 0.5787 | 9.2039 | - | 9.2039 | 401.3975 | 0.125 | 0.7523 | Kinson New Road Northbourne STW | Longham Bridge House SPS | 60 | 0.028846 | 71897.8138 | 2.9263 | 14.13 | 14.54 | 14.68 | 390 | 402 | 2.9263 | 17.6063 | 3.4763 | 0.55
15315 | Huish Episcopi Wagg Bridge SPS | 100 | 0.5787 | 5.8905 | 0.25 | 0.25 | 675.0828 | 0.1 | 0.031928 | Langport Portfield Lane STW | Huish Episcopi Wagg Drove SPS | 60 | 5.1959e-05 | 2441.1504 | 0.018413 | 12.46 | 10.67 | 12.67 | 10 | 676 | 0.018413 | 12.6884 | 0.22841 | 0.21
14298 | Chilton Cantelo School SPS | 102 | 0.55555 | 6.1285 | - | 6.1285 | 1019.5822 | 0.102 | 0.7523 | Chilton Cantelo Hornsey Bridge STW | Chilton Cantelo Hornsey Bridge STW | 58 | 0.028846 | 58668.616 | 9.6983 | 21.84 | 22.47 | 22.57 | 110 | 1020 | 9.6983 | 32.2683 | 10.4283 | 0.73
15008 | Bournemouth Ringwood Road SPS | 75 | 0.55555 | 3.3134 | - | 3.3134 | 53.4065 | 0.075 | 0.7523 | Kinson New Road Northbourne STW | Bournemouth Kinson Main Millhams Road SPS | 58 | 0.028846 | 43138.6883 | 0.76256 | 15.78 | 21.4 | 21.6 | 48 | 54 | 0.76256 | 22.3626 | 6.5826 | 5.82
15410 | Horsey Chedzoy Lane Bridgwater SPS | 100 | 0.55555 | 5.8905 | - | 5.8905 | 312.5782 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Horsey Bath Road SPS | 58 | 0.028846 | 57518.251 | 3.0516 | 6.74 | 6.48 | 6.85 | 4 | 312 | 3.0516 | 9.9016 | 3.1616 | 0.11
15722 | Wellington Poole Brickyard SPS | 160 | 0.55555 | 15.0796 | - | 15.0796 | 661.994 | 0.16 | 0.7523 | Wellington Tone STW | Wellington Tone STW | 58 | 0.028846 | 92029.2016 | 3.5032 | - | 57.13 | 57.13 | 678 | 678 | 3.5032 | 60.6332 | - | -
15734 | Wellington Lowmoor Trading Estate 1 SPS | 110 | 0.55555 | 7.1275 | - | 7.1275 | 36.7671 | 0.11 | 0.7523 | Wellington Tone STW | Wellington Tone STW | 58 | 0.028846 | 63270.0761 | 0.31676 | - | 51.83 | 51.83 | 142 | 142 | 0.31676 | 52.1468 | - | -
15708 | Corscombe Corscombe Court SPS | 75 | 0.53241 | 3.3134 | - | 3.3134 | 551.4512 | 0.075 | 0.7523 | Corscombe Off Fudge Hill STW | Corscombe Off Fudge Hill STW | 56 | 0.028846 | 43138.6883 | 7.8738 | 108.59 | 126.75 | 128.38 | - | 552 | 7.8738 | 136.2538 | 27.6638 | 19.79
15169 | Hillesley Kilcott Lane SPS | 120 | 0.53241 | 8.4823 | - | 8.4823 | 200.4031 | 0.12 | 0.7523 | Charfield . STW | Charfield . STW | 56 | 0.028846 | 69021.9012 | 1.5409 | 95.28 | 105.17 | 105.17 | - | 218 | 1.5409 | 106.7109 | 11.4309 | 9.89
14144 | Malmesbury Perry Green SPS | 80 | 0.53241 | 3.7699 | - | 3.7699 | 578.4722 | 0.08 | 0.7523 | Malmesbury . STW | Malmesbury Noahs Ark SPS | 56 | 0.028846 | 46014.6008 | 7.5815 | 79.64 | 78.18 | 92.31 | 396 | 1274 | 7.5815 | 99.8915 | 20.2515 | 12.67
15154 | Westerleigh Kidney Hill SPS | 100 | 0.53241 | 5.8905 | - | 5.8905 | 432.3571 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 56 | 0.028846 | 57518.251 | 4.221 | 64.14 | 78.44 | 78.44 | 432 | 432 | 4.221 | 82.661 | 18.521 | 14.3
15401 | Mudgley Mudgley Cross SPS | 90 | 0.53241 | 4.7713 | - | 4.7713 | 1628.48 | 0.09 | 0.7523 | Wedmore . STW | Wedmore . STW | 56 | 0.028846 | 51766.4259 | 18.2644 | 61.71 | 52.4 | 71.99 | 430 | 1626 | 18.2644 | 90.2544 | 28.5444 | 10.28
14476 | Semington Littlemarsh SPS | 100 | 0.53241 | 5.8905 | - | 5.8905 | 201.971 | 0.1 | 0.7523 | Bowerhill Shails Lane STW | Semington Semington Brook SPS | 56 | 0.028846 | 57518.251 | 1.9718 | 46.6 | 49.7 | 50.17 | 154 | 202 | 1.9718 | 52.1418 | 5.5418 | 3.57
15300 | Merriott Boozer Pitt SPS | 80 | 0.53241 | 3.7699 | - | 3.7699 | 450.7023 | 0.08 | 0.7523 | Merriott B3165 STW | Merriott B3165 STW | 56 | 0.028846 | 46014.6008 | 5.907 | 44.99 | 51.43 | 51.7 | 426 | 450 | 5.907 | 57.607 | 12.617 | 6.71
15476 | Chideock Giles Close SPS | 100 | 0.53241 | 5.8905 | - | 5.8905 | 153.6922 | 0.1 | 0.7523 | Chideock Mill Lane STW | Chideock Mill Lane STW | 56 | 0.028846 | 57518.251 | 1.5005 | 23.72 | 29.66 | 29.75 | 152 | 154 | 1.5005 | 31.2505 | 7.5305 | 6.03
10565 | North Trigon North Trigon Sewage Pumping Station SPS | 100 | 0.53241 | 5.8905 | - | 5.8905 | 740.2464 | 0.1 | 0.7523 | Wareham Keysworth Drive STW | Coldharbour Silent Woman Private SPS | 56 | 0.028846 | 57518.251 | 7.2268 | 23.42 | 30.59 | 30.75 | - | 740 | 7.2268 | 37.9768 | 14.5568 | 7.33
15213 | Ringwood Parkside Industrial Estate SPS | 75 | 0.53241 | 3.3134 | - | 3.3134 | 21.2126 | 0.075 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Bickerley SPS | 56 | 0.028846 | 43138.6883 | 0.30288 | 14.15 | 14.81 | 14.81 | - | 22 | 0.30288 | 15.1129 | 0.96288 | 0.66
15015 | Bournemouth Muscliff Lane SPS | 75 | 0.53241 | 3.3134 | - | 3.3134 | 330.7224 | 0.075 | 0.7523 | Holdenhurst Riverside Avenue STW | Holdenhurst Riverside Avenue STW | 56 | 0.028846 | 43138.6883 | 4.7222 | 12.62 | 17.15 | 17.35 | 290 | 330 | 4.7222 | 22.0722 | 9.4522 | 4.73
14413 | Chideock Seatown SPS | 125 | 0.53241 | 9.2039 | 9.7 | 9.7 | 786.9849 | 0.125 | 0.79285 | Chideock Mill Lane STW | Chideock Mill Lane STW | 56 | 0.032039 | 75773.3081 | 6.3583 | 5.44 | 14.49 | 16.02 | 382 | 786 | 6.3583 | 22.3783 | 16.9383 | 10.58
15697 | Salway Ash Salway Drive SPS | 100 | 0.50926 | 5.8905 | - | 5.8905 | 51.5114 | 0.1 | 0.7523 | Bridport Wych Farm STW | Salway Ash Old Stw SPS | 53 | 0.028846 | 57518.251 | 0.50289 | 77.85 | 79.85 | 79.85 | 52 | 52 | 0.50289 | 80.3529 | 2.5029 | 2
14209 | Calne Castle Street SPS | 100 | 0.50926 | 5.8905 | - | 5.8905 | 32.6915 | 0.1 | 0.7523 | Calne . STW | Calne . STW | 53 | 0.028846 | 57518.251 | 0.31916 | 74.35 | 76.18 | 76.26 | 30 | 32 | 0.31916 | 76.5792 | 2.2292 | 1.91
14313 | Stapleford Overstreet SPS | 32 | 0.50926 | 0.60319 | - | 0.60319 | 238.8173 | 0.032 | 0.7523 | Wishford Wilton Road STW | Stapleford Pelican Inn SPS | 53 | 0.028846 | 18405.8403 | 10.8126 | 62.85 | 63.16 | 63.79 | 192 | 238 | 10.8126 | 74.6026 | 11.7526 | 0.94
14473 | Bradford-On-Avon Woolley Green SPS | 100 | 0.50926 | 5.89 | - | 3.3134 | 357.4784 | 0.1 | 0.7523 | Bradford-On-Avon . STW | Bradford-On-Avon Barton Farm Terminal P Stn SPS | 53 | 0.028846 | 43138.6883 | 5.1042 | 62.32 | 65.71 | 65.71 | 358 | 358 | 5.1042 | 70.8142 | 8.4942 | 3.39
15208 | Shillingstone Honeysuckle Gardens SPS | 75 | 0.50926 | 3.3134 | - | 3.3134 | 131.7762 | 0.075 | 0.7523 | Shillingstone . STW | Shillingstone . STW | 53 | 0.028846 | 43138.6883 | 1.8816 | 47.67 | 49.46 | 49.91 | 98 | 132 | 1.8816 | 51.7916 | 4.1216 | 2.24
17170 | Ringstead . SPS | 100 | 0.50926 | 5.8905 | - | 5.8905 | 297.2346 | 0.1 | 0.7523 | Ringstead Ringstead Bay STW | Ringstead Ringstead Bay STW | 53 | 0.028846 | 57518.251 | 2.9018 | 9.87 | 15.24 | 15.24 | - | 298 | 2.9018 | 18.1418 | 8.2718 | 5.37
15699 | Charmouth Newlands Bridge SPS | 100 | 0.50926 | 5.8905 | - | 5.8905 | 265.9018 | 0.1 | 0.7523 | Charmouth Headworks/Sea Outfall STW | Charmouth Headworks/Sea Outfall STW | 53 | 0.028846 | 57518.251 | 2.5959 | 7.23 | 8.58 | 8.64 | 264 | 266 | 2.5959 | 11.2359 | 4.0059 | 1.41
17323 | Locking Fir Tree Avenue SPS | 250 | 0.50926 | 36.8155 | - | 36.8155 | 366.9049 | 0.25 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Uphill . SPS | 53 | 0.028846 | 143795.6275 | 1.0952 | 5.59 | 5.15 | 5.69 | - | 366 | 1.0952 | 6.7852 | 1.1952 | 0.1
14345 | Woodfalls Little Woodfalls Drive SPS | 80 | 0.48611 | 3.7699 | - | 3.7699 | 41.8847 | 0.08 | 0.7523 | Downton Moot Lane STW | Downton Moot Lane STW | 51 | 0.028846 | 46014.6008 | 0.54895 | 111.62 | 113.02 | 113.14 | 34 | 42 | 0.54895 | 113.6889 | 2.0689 | 1.52
17214 | Hazelbury Bryan Woodlands SPS | 100 | 0.48611 | 5.8905 | - | 5.8905 | 117.946 | 0.1 | 0.7523 | Hazelbury Bryan . STW | Hazelbury Bryan . STW | 51 | 0.028846 | 57518.251 | 1.1515 | 95.46 | 95.49 | 95.53 | 12 | 118 | 1.1515 | 96.6815 | 1.2215 | 0.07
19102 | Bristol Bifield Road SPS | 100 | 0.48611 | 5.8905 | - | 5.8905 | 18.7934 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Dalby Ave SPS | 51 | 0.028846 | 57518.251 | 0.18347 | 84.01 | 85.13 | 85.26 | 14 | 18 | 0.18347 | 85.4435 | 1.4335 | 1.25
15420 | North Nibley Mill End SPS | 100 | 0.48611 | 5.8905 | - | 5.8905 | 180.0448 | 0.1 | 0.7523 | North Nibley . STW | North Nibley . STW | 51 | 0.028846 | 57518.251 | 1.7577 | 65.57 | 79.31 | 79.31 | - | 180 | 1.7577 | 81.0677 | 15.4977 | 13.74
15485 | Crossways Egdon Glen SPS | 75 | 0.48611 | 3.3134 | - | 3.3134 | 175.3621 | 0.075 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Crossways Redbridge SPS | 51 | 0.028846 | 43138.6883 | 2.5039 | 53.46 | 58.12 | 58.12 | 176 | 176 | 2.5039 | 60.6239 | 7.1639 | 4.66
15288 | East Coker Marsh SPS | 80 | 0.48611 | 3.7699 | - | 3.7699 | 201.104 | 0.08 | 0.7523 | East Coker Moor Lane STW | East Coker Moor Lane STW | 51 | 0.028846 | 46014.6008 | 2.6357 | 53.27 | 52.62 | 53.27 | 0 | 202 | 2.6357 | 55.9057 | 2.6357 | 0
15031 | Christchurch Amberwood Gardens SPS | 100 | 0.48611 | 5.8905 | - | 5.8905 | 3.9051 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Somerford Bridge SPS | 51 | 0.028846 | 57518.251 | 0.038124 | 37.03 | 36.93 | 37.03 | 0 | 4 | 0.038124 | 37.0681 | 0.038124 | 0
19706 | Keynsham Wellsway SPS | 100 | 0.48611 | 5.8905 | - | 5.8905 | 95.243 | 0.1 | 0.7523 | Keynsham . STW | Keynsham . STW | 51 | 0.028846 | 57518.251 | 0.92983 | 29.89 | 30.7 | 30.7 | 96 | 96 | 0.92983 | 31.6298 | 1.7398 | 0.81
15503 | Chickerell Montevideo SPS | 150 | 0.48611 | 13.2536 | - | 13.2536 | 107.6774 | 0.15 | 0.7523 | Weymouth . STW | Weymouth Radipole SPS | 51 | 0.028846 | 86277.3765 | 0.61944 | 23.44 | 30.06 | 30.06 | 108 | 108 | 0.61944 | 30.6794 | 7.2394 | 6.62
14009 | Norton Fitzwarren Wassail View (Manor Farm) SPS | 100 | 0.48611 | 5.8905 | - | 5.8905 | 57.9476 | 0.1 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Silk Mills SPS | 51 | 0.028846 | 57518.251 | 0.56573 | 23.03 | 23.26 | 23.35 | 52 | 58 | 0.56573 | 23.9157 | 0.88573 | 0.32
15020 | Highcliffe Bute Drive SPS | 100 | 0.48611 | 5.8905 | - | 5.8905 | 103.0114 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Somerford Bridge SPS | 51 | 0.028846 | 57518.251 | 1.0057 | 21.79 | 28.85 | 28.85 | 104 | 104 | 1.0057 | 29.8557 | 8.0657 | 7.06
17175 | Puriton Downend Terrace SPS | 90 | 0.48611 | 4.7713 | 5 | 5 | 348.7046 | 0.09 | 0.78836 | West Huntspill STW | Puriton Rye SPS | 51 | 0.031677 | 54247.7865 | 4.2861 | 9.37 | 14.44 | 14.63 | 346 | 348 | 4.2861 | 18.9161 | 9.5461 | 5.26
15179 | Pilning Shaymoor Lane SPS | 50 | 0.48611 | 1.4726 | - | 1.4726 | 557.4543 | 0.05 | 0.7523 | Redwick . STW | Pilning Swanmoor Bridge SPS | 51 | 0.028846 | 28759.1255 | 13.7083 | 7.16 | 5.94 | 7.16 | 0 | 558 | 13.7083 | 20.8683 | 13.7083 | 0
19542 | Avonmouth Cabot Park No.1 SPS | 350 | 0.48611 | 72.1585 | - | 72.1585 | 487.637 | 0.35 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Kingsweston Lane STW | 51 | 0.028846 | 201313.8786 | 0.95002 | 7.16 | 7.09 | 8.46 | 360 | 488 | 0.95002 | 9.41 | 2.25 | 1.3
15813 | Devizes John Rennie Close SPS | - | 0.48611 | - | - | - | 54.6684 | - | - | Devizes Webbs Lane STW | Devizes Webbs Lane STW | 51 | - | - | - | - | - | - | - | - | - | - | - | -
15120 | Allington . SPS | 100 | 0.46296 | 5.8905 | - | 5.8905 | 975.9614 | 0.1 | 0.7523 | All Cannings Lower Mill Farm STW | All Cannings . SPS | 48 | 0.028846 | 57518.251 | 9.528 | 127.74 | 124.66 | 135.42 | 530 | 976 | 9.528 | 144.948 | 17.208 | 7.68
15289 | Yeovil Marsh Lane SPS | 100 | 0.46296 | 5.8905 | - | 5.8905 | 284.7681 | 0.1 | 0.7523 | Yeovil Without Off Stone Lane STW | Yeovil Without Off Stone Lane STW | 48 | 0.028846 | 57518.251 | 2.7801 | 99.02 | 108.5 | 108.5 | 284 | 284 | 2.7801 | 111.2801 | 12.2601 | 9.48
14121 | Stubhampton Main Street SPS | 50 | 0.46296 | 1.4726 | - | 1.4726 | 147.4362 | 0.05 | 0.7523 | Stubhampton . STW | Stubhampton . STW | 48 | 0.028846 | 28759.1255 | 3.6256 | 81.78 | 90.68 | 91.8 | - | 144 | 3.6256 | 95.4256 | 13.6456 | 10.02
19992 | North Petherton Parkfield Close SPS | 100 | 0.46296 | 5.8905 | - | 5.8905 | 93.7521 | 0.1 | 0.7523 | North Petherton . STW | North Petherton . STW | 48 | 0.028846 | 57518.251 | 0.91528 | 33.16 | 33.93 | 33.93 | 94 | 94 | 0.91528 | 34.8453 | 1.6853 | 0.77
15022 | Highcliffe ¦ Marryat Court SPS | 100 | 0.46296 | 5.8905 | - | 5.8905 | 110.3501 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Somerford Bridge SPS | 48 | 0.028846 | 57518.251 | 1.0773 | 24.02 | 29.47 | 29.47 | 110 | 110 | 1.0773 | 30.5473 | 6.5273 | 5.45
15217 | Bransgore Neacroft No 2 SPS | 220 | 0.46296 | 28.51 | - | 28.51 | 238.8242 | 0.22 | 0.7523 | Christchurch Stoney Lane STW | Bransgore Neacroft No 3 SPS | 48 | 0.028846 | 126540.1522 | 0.83923 | 19.59 | 21.81 | 22.6 | 56 | 238 | 0.83923 | 23.4392 | 3.8492 | 3.01
15538 | Keynsham Abbey Park SPS | 63 | 0.46296 | 2.3379 | - | 2.3379 | 300.934 | 0.063 | 0.7523 | Keynsham . STW | Keynsham Keynsham High Level SPS | 48 | 0.028846 | 36236.4981 | 5.422 | 10.97 | 12.4 | 12.78 | 124 | 296 | 5.422 | 18.202 | 7.232 | 1.81
17345 | Claverham Lower Claverham SPS | 110 | 0.46296 | 7.1275 | - | 7.1275 | 814.2691 | 0.11 | 0.7523 | Kingston Seymour Back Lane STW | Kingston Bridge SPS | 48 | 0.028846 | 63270.0761 | 7.0152 | 7.4 | 18.04 | 18.04 | 814 | 814 | 7.0152 | 25.0552 | 17.6552 | 10.64
15600 | Kingston Seymour Fairfield (Kingston Seymour West) SPS | 75 | 0.46296 | 3.3134 | - | 3.3134 | 390.0598 | 0.075 | 0.7523 | Kingston Seymour Back Lane STW | Kingston Seymour Rustic Farm (Kingston Seymour Central) SPS | 48 | 0.028846 | 43138.6883 | 5.5694 | 5.42 | 5.6 | 5.85 | 246 | 390 | 5.5694 | 11.4194 | 5.9994 | 0.43
17243 | Christchurch Monkswell Green SPS | 110 | 0.46296 | 7.1275 | - | 7.1275 | 61.2905 | 0.11 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Purewell SPS | 48 | 0.028846 | 63270.0761 | 0.52804 | 2.12 | 2.3 | 2.3 | 62 | 62 | 0.52804 | 2.828 | 0.70804 | 0.18
14103 | Coleford Upper Merryfield SPS | 80 | 0.43981 | 3.7699 | - | 3.7699 | 206.8976 | 0.08 | 0.7523 | Coleford . STW | Coleford . STW | 46 | 0.028846 | 46014.6008 | 2.7116 | 170.67 | 172.62 | 172.65 | 204 | 206 | 2.7116 | 175.3616 | 4.6916 | 1.98
14250 | Lytchett Matravers Hopmans Close SPS | 100 | 0.43981 | 5.8905 | - | 5.8905 | 112.3658 | 0.1 | 0.7523 | Blackheath . STW | Lytchett Matravers Bulbury Lane SPS | 46 | 0.028846 | 57518.251 | 1.097 | 83.72 | 90.91 | 90.91 | - | 110 | 1.097 | 92.007 | 8.287 | 7.19
15687 | Wimborne Lonnen Road Wood View Colehill SPS | 100 | 0.43981 | 5.8905 | - | 5.8905 | 91.1626 | 0.1 | 0.7523 | Wimborne Brook Road STW | Wimborne Pilford Heath SPS | 46 | 0.028846 | 57518.251 | 0.89 | 36.81 | 42.97 | 42.99 | - | 92 | 0.89 | 43.88 | 7.07 | 6.18
15502 | Bradford Abbas Compton Road SPS | 150 | 0.43981 | 13.2536 | - | 13.2536 | 144.2946 | 0.15 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Pen Mill Banbury SPS | 46 | 0.028846 | 86277.3765 | 0.83009 | 31.68 | 33.41 | 33.87 | 128 | 144 | 0.83009 | 34.7001 | 3.0201 | 2.19
14093 | West Pennard Page Lane SPS | 80 | 0.43981 | 3.7699 | 5 | 5 | 97.98 | 0.08 | 0.99777 | Butleigh . STW | West Pennard Havyatt SPS | 46 | 0.050741 | 61028.7598 | 2.2333 | 28.71 | 32.75 | 32.75 | 98 | 98 | 2.2333 | 34.9833 | 6.2733 | 4.04
15209 | Spetisbury Crawford Bridge SPS | 120 | 0.43981 | 8.4823 | 7 | 7 | 116.9964 | 0.12 | 0.62083 | Tarrant Crawford . STW | Spetisbury No 3 SPS | 46 | 0.019645 | 56960.1758 | 0.61822 | 27.18 | 36.99 | 36.99 | 116 | 116 | 0.61822 | 37.6082 | 10.4282 | 9.81
15222 | Bransgore Burley Road (The Dell) SPS | 100 | 0.43981 | 5.8905 | - | 5.8905 | 79.766 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Bransgore Wiltshire Gardens SPS | 46 | 0.028846 | 57518.251 | 0.77873 | 12.76 | 15.25 | 15.48 | 70 | 80 | 0.77873 | 16.2587 | 3.4987 | 2.72
14086 | Meare Homeway Corner SPS | 80 | 0.43981 | 3.7699 | - | 3.7699 | 702.1984 | 0.08 | 0.7523 | Meare . STW | Meare Oxenpill SPS | 46 | 0.028846 | 46014.6008 | 9.2031 | 8.12 | 8.76 | 8.97 | 686 | 704 | 9.2031 | 18.1731 | 10.0531 | 0.85
15378 | Pawlett Vicarage Lane SPS | 100 | 0.43981 | 5.8905 | 3 | 3 | 275.8736 | 0.1 | 0.38314 | West Huntspill STW | Pawlett Main Road SPS | 46 | 0.007482 | 29293.8047 | 0.72626 | 6.45 | 17.68 | 17.68 | 276 | 276 | 0.72626 | 18.4063 | 11.9563 | 11.23
15185 | Little Badminton Well Lane SPS | 50 | 0.41667 | 1.4726 | - | 1.4726 | 1162.1033 | 0.05 | 0.7523 | Great Badminton . STW | Great Badminton . STW | 44 | 0.028846 | 28759.1255 | 28.5771 | 127.6 | 126.87 | 136.77 | 342 | 1162 | 28.5771 | 165.3471 | 37.7471 | 9.17
14154 | Sherston Gaston Lane SPS | 100 | 0.41667 | 5.8905 | - | 5.8905 | 88.5498 | 0.1 | 0.7523 | Sherston . STW | Sherston . STW | 44 | 0.028846 | 57518.251 | 0.86449 | 113.02 | 113.36 | 113.45 | - | 88 | 0.86449 | 114.3145 | 1.2945 | 0.43
19125 | Radstock Chapel Lawns Clandown SPS | 100 | 0.41667 | 5.8905 | - | 5.8905 | 39.5877 | 0.1 | 0.7523 | Radstock Mill Lane STW | Radstock Mill Lane STW | 44 | 0.028846 | 57518.251 | 0.38648 | 89.69 | 93.42 | 93.42 | 40 | 40 | 0.38648 | 93.8065 | 4.1165 | 3.73
15000 | Compton Martin Undertown Lane SPS | 120 | 0.41667 | 8.4823 | - | 8.4823 | 144.5473 | 0.12 | 0.7523 | Ubley Frog Lane STW | Ubley Frog Lane STW | 44 | 0.028846 | 69021.9012 | 1.1114 | 86.38 | 93.37 | 93.37 | 144 | 144 | 1.1114 | 94.4814 | 8.1014 | 6.99
17131 | Pleck . SPS | 90 | 0.41667 | 4.7713 | - | 4.7713 | 498.4257 | 0.09 | 0.7523 | Marnhull Common STW | Marnhull Common STW | 44 | 0.028846 | 51766.4259 | 5.5902 | 82.77 | 88.79 | 89.97 | - | 498 | 5.5902 | 95.5602 | 12.7902 | 7.2
14136 | Lea Cresswell Lane SPS | 100 | 0.41667 | 5.8905 | - | 5.8905 | 429.5245 | 0.1 | 0.7523 | Malmesbury . STW | Lea Lea North SPS | 44 | 0.028846 | 57518.251 | 4.1933 | 79.5 | 85.68 | 86.11 | 384 | 428 | 4.1933 | 90.3033 | 10.8033 | 6.61
14134 | Whitsbury Lower Grove SPS | 100 | 0.41667 | 5.8905 | - | 5.8905 | 167.6414 | 0.1 | 0.7523 | Whitsbury . STW | Whitsbury . STW | 44 | 0.028846 | 57518.251 | 1.6366 | 78.78 | 91.27 | 91.27 | 168 | 168 | 1.6366 | 92.9066 | 14.1266 | 12.49
15540 | Freshford Staples Hill SPS | 50 | 0.41667 | 1.4726 | - | 1.4726 | 1571.5898 | 0.05 | 0.7523 | Westwood . STW | Westwood . STW | 44 | 0.028846 | 28759.1255 | 38.6468 | 69.57 | 64.99 | 95.9 | 240 | 1572 | 38.6468 | 134.5468 | 64.9768 | 26.33
15135 | Yate Broad Lane SPS | 100 | 0.41667 | 5.8905 | - | 5.8905 | 192.3448 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Yate North Road SPS | 44 | 0.028846 | 57518.251 | 1.8778 | 67.75 | 69.15 | 69.15 | 192 | 192 | 1.8778 | 71.0278 | 3.2778 | 1.4
15652 | Halstock Street Farm SPS | 100 | 0.41667 | 5.8905 | - | 5.8905 | 213.7922 | 0.1 | 0.7523 | Halstock Watery Lane STW | Halstock Watery Lane STW | 44 | 0.028846 | 57518.251 | 2.0872 | 67.65 | 73.4 | 73.4 | - | 214 | 2.0872 | 75.4872 | 7.8372 | 5.75
14068 | Glastonbury Bushycombe SPS | 100 | 0.41667 | 5.8905 | - | 5.8905 | 134.9619 | 0.1 | 0.7523 | Glastonbury The Beckery SSTW | Glastonbury Porchestall SPS | 44 | 0.028846 | 57518.251 | 1.3176 | 48.25 | 57.89 | 58.19 | 122 | 134 | 1.3176 | 59.5076 | 11.2576 | 9.94
17374 | Holt March Farm SPS | 110 | 0.41667 | 7.1275 | - | 7.1275 | 178.008 | 0.11 | 0.7523 | Holt Pond Head STW | Holt Pond Head STW | 44 | 0.028846 | 63270.0761 | 1.5336 | 42.76 | 45.11 | 45.11 | - | 178 | 1.5336 | 46.6436 | 3.8836 | 2.35
19655 | Somerton Etsome Terrace SPS | 80 | 0.41667 | 3.7699 | - | 3.7699 | 168.9755 | 0.08 | 0.7523 | Somerton Barpool Lane STW | Somerton Barpool Lane STW | 44 | 0.028846 | 46014.6008 | 2.2146 | 41.45 | 43.65 | 43.75 | 166 | 168 | 2.2146 | 45.9646 | 4.5146 | 2.3
17573 | Wool East Burton Road SPS | 80 | 0.41667 | 3.7699 | - | 3.7699 | 191.8837 | 0.08 | 0.7523 | Wool . STW | Wool Railway Cottages SPS | 44 | 0.028846 | 46014.6008 | 2.5149 | 17.49 | 16.02 | 17.49 | 0 | 192 | 2.5149 | 20.0049 | 2.5149 | 0
14241 | Sandford Morden Road SPS | 150 | 0.41667 | 13.2536 | - | 13.2536 | 163.2131 | 0.15 | 0.7523 | Wareham Keysworth Drive STW | Wareham Keysworth Drive STW | 44 | 0.028846 | 86277.3765 | 0.93892 | 8.4 | 13.39 | 13.39 | 164 | 164 | 0.93892 | 14.3289 | 5.9289 | 4.99
15688 | Bridgwater Hamp Ward SPS | 100 | 0.41667 | 5.8905 | - | 5.8905 | 147.1239 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Blake Gardens SPS | 44 | 0.028846 | 57518.251 | 1.4363 | 7.09 | 6.56 | 7.47 | 90 | 148 | 1.4363 | 8.9063 | 1.8163 | 0.38
15387 | Chedzoy Fishers Farm SPS | 150 | 0.41667 | 13.2536 | - | 13.2536 | 508.335 | 0.15 | 0.7523 | Chilton Trinity . STW | Chedzoy Ward Lane SPS | 44 | 0.028846 | 86277.3765 | 2.9243 | 5.37 | 7.65 | 7.65 | - | 508 | 2.9243 | 10.5743 | 5.2043 | 2.28
11478 | Calne Oxford Road SPS | 125 | 0.41667 | 9.2039 | - | 9.2039 | 319.7603 | 0.125 | 0.7523 | Compton Bassett . STW | Calne Abberd Lane SPS | 44 | 0.028846 | 71897.8138 | 2.3312 | - | - | - | - | - | 2.3312 | - | - | -
15676 | Shaftesbury Tollgate Park SPS | 100 | 0.39352 | 5.8905 | - | 5.8905 | 283.9183 | 0.1 | 0.7523 | Shaftesbury Gears Mill STW | Shaftesbury Gears Mill STW | 41 | 0.028846 | 57518.251 | 2.7718 | 230.72 | 234.19 | 234.19 | - | 284 | 2.7718 | 236.9618 | 6.2418 | 3.47
14316 | East Knoyle Underhill SPS | 50 | 0.39352 | 1.4726 | - | 1.4726 | 805.1532 | 0.05 | 0.7523 | East Knoyle Millbrook Lane STW | East Knoyle Shaftesbury Road SPS | 41 | 0.028846 | 28759.1255 | 19.7994 | 132.37 | 162.67 | 163.51 | - | 806 | 19.7994 | 183.3094 | 50.9394 | 31.14
14348 | Woodfalls Lodge Drove SPS | 100 | 0.39352 | 5.8905 | - | 5.8905 | 55.845 | 0.1 | 0.7523 | Downton Moot Lane STW | Downton Moot Lane STW | 41 | 0.028846 | 57518.251 | 0.5452 | 110.58 | 111.61 | 111.61 | 56 | 56 | 0.5452 | 112.1552 | 1.5752 | 1.03
14310 | Netheravon Support Weapons Wing SPS | 150 | 0.39352 | 13.2536 | - | 13.2536 | 719.1415 | 0.15 | 0.7523 | Netheravon . STW | Netheravon . STW | 41 | 0.028846 | 86277.3765 | 4.137 | 80.57 | 90.99 | 91.1 | 714 | 720 | 4.137 | 95.237 | 14.667 | 10.53
13126 | Fontmell Magna Collyers Rise (Fontmell Magna 1) SPS | 80 | 0.39352 | 3.7699 | - | 3.7699 | 294.3408 | 0.08 | 0.7523 | Fontmell Magna Orchard Close (Fontmell Magna 2) STW | Fontmell Magna Orchard Close (Fontmell Magna 2) STW | 41 | 0.028846 | 46014.6008 | 3.8577 | 76.47 | 81.35 | 81.74 | - | 294 | 3.8577 | 85.5977 | 9.1277 | 5.27
19284 | Yate Nibley Village SPS | - | 0.39352 | - | - | - | 43.0848 | - | - | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 41 | - | - | - | 66.37 | 67.86 | 67.86 | 44 | 44 | - | - | - | 1.49
15719 | High Ham . SPS | 150 | 0.39352 | 13.2536 | - | 13.2536 | 456.8265 | 0.15 | 0.7523 | Langport Portfield Lane STW | Low Ham Moretons Lane SPS | 41 | 0.028846 | 86277.3765 | 2.628 | 54.72 | 96.86 | 97.98 | - | 456 | 2.628 | 100.608 | 45.888 | 43.26
15118 | Seend New Buldings SPS | 100 | 0.39352 | 5.8905 | - | 5.8905 | 336.487 | 0.1 | 0.7523 | Seend . STW | Seend Barge Inn SPS | 41 | 0.028846 | 57518.251 | 3.285 | 47.26 | 48.28 | 52.01 | 164 | 336 | 3.285 | 55.295 | 8.035 | 4.75
15463 | Bradford On Tone Tone Green SPS | 75 | 0.39352 | 3.3134 | 0.5 | 0.5 | 189.1761 | 0.075 | 0.11352 | Bradford On Tone . STW | Bradford On Tone . STW | 41 | 0.00065686 | 6509.7344 | 0.073491 | 30.21 | 41.65 | 41.65 | 192 | 192 | 0.073491 | 41.7235 | 11.5135 | 11.44
17091 | Pill Eden Office Park Ham Green SPS | 150 | 0.39352 | 13.2536 | - | 13.2536 | 328.4448 | 0.15 | 0.7523 | Avonmouth Kingsweston Lane STW | Pill Avon Road SPS | 41 | 0.028846 | 86277.3765 | 1.8894 | 27.04 | 28.56 | 28.56 | 328 | 328 | 1.8894 | 30.4494 | 3.4094 | 1.52
15418 | Pawlett Chapel Road SPS | 100 | 0.39352 | 5.8905 | - | 5.8905 | 218.3828 | 0.1 | 0.7523 | West Huntspill STW | Pawlett Main Road SPS | 41 | 0.028846 | 57518.251 | 2.132 | 22.27 | 27.28 | 27.28 | 218 | 218 | 2.132 | 29.412 | 7.142 | 5.01
15449 | Meare Green Wrantage SPS | 100 | 0.39352 | 5.8905 | 1 | 1 | 571.325 | 0.1 | 0.12771 | Meare Green . STW | Meare Green . STW | 41 | 0.00083134 | 9764.6016 | 0.18783 | 17.3 | 19.31 | 20.9 | - | 572 | 0.18783 | 21.0878 | 3.7878 | 3.6
15294 | Martock Matfurlong Close Off Water Street SPS | 100 | 0.39352 | 5.8905 | - | 5.8905 | 4.4562 | 0.1 | 0.7523 | Martock Hurst Bow STW | Martock Hurst Bow STW | 41 | 0.028846 | 57518.251 | 0.043505 | 16.32 | 16.46 | 16.46 | 4 | 4 | 0.043505 | 16.5035 | 0.1835 | 0.14
14624 | Saltford Mead Lane SPS | 762 | 0.39352 | 342.0275 | 7 | 7 | 1363.4237 | 0.762 | 0.015397 | Saltford Mead Lane STW | Saltford Mead Lane STW | 41 | 1.2082e-05 | 8970.1064 | 0.00071339 | 13.63 | 17.33 | 20.7 | 1066 | 1362 | 0.00071339 | 20.7007 | 7.0707 | 7.07
15159 | Pilning New Passage SPS | 75 | 0.39352 | 3.3134 | - | 3.3134 | 280.2509 | 0.075 | 0.7523 | Redwick . STW | Redwick . STW | 41 | 0.028846 | 43138.6883 | 4.0015 | 7.99 | 6.99 | 7.99 | 0 | 280 | 4.0015 | 11.9915 | 4.0015 | 0
19106 | Congresbury Station Close Weston Road SPS | 80 | 0.39352 | 3.7699 | - | 3.7699 | 239.0983 | 0.08 | 0.7523 | Wick St Lawrence . STW | Wick St Lawrence . STW | 41 | 0.028846 | 46014.6008 | 3.1337 | 7.49 | 4.54 | 7.51 | 2 | 240 | 3.1337 | 10.6437 | 3.1537 | 0.02
14369 | Mere Dead Maids Quarry SPS | 100 | 0.37037 | 5.8905 | - | 5.8905 | 105.4727 | 0.1 | 0.7523 | Mere Rook Street STW | Mere Rook Street STW | 39 | 0.028846 | 57518.251 | 1.0297 | 110.5 | 109.81 | 110.5 | 0 | 106 | 1.0297 | 111.5297 | 1.0297 | 0
14224 | Lytchett Matravers Wimborne Road SPS | 100 | 0.37037 | 5.8905 | - | 5.8905 | 312.2578 | 0.1 | 0.7523 | Blackheath . STW | Lytchett Matravers Flowers Drove SPS | 39 | 0.028846 | 57518.251 | 3.0485 | 77.28 | 80.01 | 80.01 | - | 312 | 3.0485 | 83.0585 | 5.7785 | 2.73
14163 | East Tytherton Barns Bridge SPS | 100 | 0.37037 | 5.8905 | - | 5.8905 | 308.7804 | 0.1 | 0.7523 | Sutton Benger . STW | East Tytherton Clovelly Cottage SPS | 39 | 0.028846 | 57518.251 | 3.0145 | 51.37 | 53.79 | 54.31 | 212 | 314 | 3.0145 | 57.3245 | 5.9545 | 2.94
15732 | Shillingstone Spencer Gardens SPS | - | 0.37037 | - | - | - | 108.2972 | - | - | Shillingstone . STW | Shillingstone . STW | 39 | - | - | - | 47.64 | 49.19 | 49.19 | 108 | 108 | - | - | - | 1.55
17114 | Verwood Merryfield Close SPS | 150 | 0.37037 | 13.2536 | - | 13.2536 | 158.0173 | 0.15 | 0.7523 | Palmersford . STW | Verwood Potterne Way SPS | 39 | 0.028846 | 86277.3765 | 0.90903 | 44.27 | 48.52 | 48.52 | 158 | 158 | 0.90903 | 49.429 | 5.159 | 4.25
19273 | Alhampton Wayside Cottage SPS | 125 | 0.37037 | 9.2039 | - | 9.2039 | 210.0282 | 0.125 | 0.7523 | Ditcheat . STW | Alhampton Main SPS | 39 | 0.028846 | 71897.8138 | 1.5312 | 43.61 | 45.67 | 45.67 | - | 210 | 1.5312 | 47.2012 | 3.5912 | 2.06
14230 | Bovington Cranes Moor SPS | 100 | 0.37037 | 5.8905 | - | 5.8905 | 61.5867 | 0.1 | 0.7523 | Wool . STW | Bovington Terminal SPS | 39 | 0.028846 | 57518.251 | 0.60125 | 25.4 | 27.26 | 27.26 | 62 | 62 | 0.60125 | 27.8613 | 2.4613 | 1.86
15694 | Weymouth Bincleaves SPS | 100 | 0.37037 | 5.8905 | - | 5.8905 | 114.3685 | 0.1 | 0.7523 | Weymouth . STW | Weymouth Radipole SPS | 39 | 0.028846 | 57518.251 | 1.1165 | 21.41 | 27.37 | 27.37 | 114 | 114 | 1.1165 | 28.4865 | 7.0765 | 5.96
14022 | Bristol Hedgemead View SPS | - | 0.37037 | - | - | - | 9.8032 | - | - | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 39 | - | - | - | 15.52 | 17.94 | 17.94 | 10 | 10 | - | - | - | 2.42
14592 | Wedmore The Lerburne SPS | - | 0.37037 | - | - | - | 52.785 | - | - | Wedmore . STW | Wedmore . STW | 39 | - | - | - | 10.55 | 11.59 | 11.59 | 58 | 58 | - | - | - | 1.04
15359 | Lympsham Church Road SPS | 75 | 0.37037 | 3.3134 | - | 3.3134 | 558.6999 | 0.075 | 0.7523 | West Huntspill STW | Lympsham Innsbruck SPS | 39 | 0.028846 | 43138.6883 | 7.9773 | 6.02 | 5.86 | 6.07 | 44 | 558 | 7.9773 | 14.0473 | 8.0273 | 0.05
15413 | Durleigh Enmore Road Reservoir SPS | 125 | 0.37037 | 9.2039 | - | 9.2039 | 338.4191 | 0.125 | 0.7523 | Chilton Trinity . STW | Bridgwater West Quay Drawbridge SPS | 39 | 0.028846 | 71897.8138 | 2.4672 | - | 25.45 | 28.77 | 284 | 332 | 2.4672 | 31.2372 | - | -
14000 | Taunton Riverside SPS | - | 0.37037 | - | - | - | 0 | - | - | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 39 | - | - | - | - | - | - | - | - | - | - | - | -
15119 | Conock . SPS | 100 | 0.34722 | 5.8905 | - | 5.8905 | 628.0992 | 0.1 | 0.7523 | Marden . STW | Chirton Small Street SPS | 36 | 0.028846 | 57518.251 | 6.132 | 114.57 | 112.01 | 114.57 | - | 626 | 6.132 | 120.702 | 6.132 | 0
14177 | Calstone Wellington . SPS | 100 | 0.34722 | 5.8905 | - | 5.8905 | 268.9309 | 0.1 | 0.7523 | Compton Bassett . STW | Calne Rough Leaze SPS | 36 | 0.028846 | 57518.251 | 2.6255 | 107.04 | 115.04 | 115.06 | - | 268 | 2.6255 | 117.6855 | 10.6455 | 8.02
15513 | Williton Tower Hill SPS | 100 | 0.34722 | 5.8905 | - | 5.8905 | 215.9656 | 0.1 | 0.7523 | Watchet . STW | Doniford . SPS | 36 | 0.028846 | 57518.251 | 2.1084 | 54.27 | 57.44 | 57.44 | 216 | 216 | 2.1084 | 59.5484 | 5.2784 | 3.17
10344 | Yeovil Great Mead SPS | 100 | 0.34722 | 5.8905 | - | 5.8905 | 174.8218 | 0.1 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Sherborne Road (Pen Mill) STW | 36 | 0.028846 | 57518.251 | 1.7067 | 33 | 38.5 | 38.5 | 74 | 74 | 1.7067 | 40.2067 | 7.2067 | 5.5
17373 | Holt Holt Vale Farm SPS | 110 | 0.34722 | 7.1275 | - | 7.1275 | 1095.0518 | 0.11 | 0.7523 | Holt Pond Head STW | Holt Pond Head STW | 36 | 0.028846 | 63270.0761 | 9.4343 | 29.38 | 33.98 | 42.37 | - | 1096 | 9.4343 | 51.8043 | 22.4243 | 12.99
17462 | Langport Huish Lea SPS | - | 0.34722 | - | - | - | 4.0749 | - | - | Langport Portfield Lane STW | Langport Westover SPS | 36 | - | - | - | 20.05 | 20.03 | 20.05 | 0 | 4 | - | - | - | 0
15808 | Isle Brewers Westport Road SPS | 150 | 0.34722 | 13.2536 | - | 13.2536 | 617.0029 | 0.15 | 0.7523 | Ilminster Ashwell STW | Ilminster Westport SPS | 36 | 0.028846 | 86277.3765 | 3.5494 | 13.32 | 9.43 | 13.62 | - | 618 | 3.5494 | 17.1694 | 3.8494 | 0.3
15403 | Bridgwater Wylds Road Foul SPS | 100 | 0.34722 | 5.8905 | - | 5.8905 | 573.5006 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Bristol Road SPS | 36 | 0.028846 | 57518.251 | 5.5989 | 6.63 | 6.29 | 7.24 | 230 | 574 | 5.5989 | 12.8389 | 6.2089 | 0.61
14074 | Shepton Mallet Fosse Lane Charlton SPS | 120 | 0.32407 | 8.4823 | 16.5 | 16.5 | 58.768 | 0.12 | 1.4634 | Shepton Mallet Darshill STW | Shepton Mallet Darshill STW | 34 | 0.10915 | 134263.2715 | 1.6716 | 156.1 | 161.41 | 161.44 | 54 | 58 | 1.6716 | 163.1116 | 7.0116 | 5.34
15198 | Gillingham Clarendon Close SPS | 100 | 0.32407 | 5.8905 | - | 5.8905 | 86.9721 | 0.1 | 0.7523 | Gillingham Common Mead Lane STW | Gillingham Buckingham Road SPS | 34 | 0.028846 | 57518.251 | 0.84908 | 87.14 | 88.89 | 88.93 | - | 86 | 0.84908 | 89.7791 | 2.6391 | 1.79
15220 | Bransgore Dial Close SPS | 100 | 0.32407 | 5.8905 | - | 5.8905 | 141.69 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Bransgore Wiltshire Gardens SPS | 34 | 0.028846 | 57518.251 | 1.3833 | 57.62 | 60.19 | 60.95 | 98 | 142 | 1.3833 | 62.3333 | 4.7133 | 3.33
15142 | Winterbourne Swan Lane SPS | 100 | 0.32407 | 5.8905 | - | 5.8905 | 141.5703 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 34 | 0.028846 | 57518.251 | 1.3821 | 56.37 | 62.65 | 62.65 | 142 | 142 | 1.3821 | 64.0321 | 7.6621 | 6.28
10310 | Westbury Broadway North SPS | 80 | 0.32407 | 3.7699 | - | 3.7699 | 238.6474 | 0.08 | 0.7523 | Westbury STW | Westbury Washington Road SPS | 34 | 0.028846 | 46014.6008 | 3.1277 | 51.36 | 50.73 | 51.4 | 156 | 238 | 3.1277 | 54.5277 | 3.1677 | 0.04
15336 | Chilton Cantelo Lower Chilton Cantelo SPS | 75 | 0.32407 | 3.3134 | - | 3.3134 | 564.9505 | 0.075 | 0.7523 | Chilton Cantelo Hornsey Bridge STW | Chilton Cantelo School SPS | 34 | 0.028846 | 43138.6883 | 8.0666 | 21.02 | 21.82 | 22.22 | 356 | 564 | 8.0666 | 30.2866 | 9.2666 | 1.2
19687 | Cross Chardet Close SPS | 100 | 0.32407 | 5.8905 | - | 5.8905 | 31.78 | 0.1 | 0.7523 | Cheddar . STW | Cross Cross East SPS | 34 | 0.028846 | 57518.251 | 0.31026 | 7 | 8.65 | 8.65 | 32 | 32 | 0.31026 | 8.9603 | 1.9603 | 1.65
15032 | Mudeford Mudeford Quay SPS | 100 | 0.32407 | 5.8905 | - | 5.8905 | 422.7619 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Mudeford Mudeford Gardens SPS | 34 | 0.028846 | 57518.251 | 4.1273 | 1.53 | 3.2 | 3.2 | 422 | 422 | 4.1273 | 7.3273 | 5.7973 | 1.67
12620 | Bath Granville Road SPS | 150 | 0.32407 | 13.2536 | - | 13.2536 | 252.6898 | 0.15 | 0.7523 | Saltford Mead Lane STW | Saltford Mead Lane STW | 34 | 0.028846 | 86277.3765 | 1.4537 | - | - | - | - | - | 1.4537 | - | - | -
12420 | Oakdale Dorchester Road SPS | 90 | 0.32407 | 4.7713 | - | 4.7713 | 91.6564 | 0.09 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 34 | 0.028846 | 51766.4259 | 1.028 | - | - | - | - | - | 1.028 | - | - | -
15514 | Lawford Stickle Hill SPS | 50 | 0.30093 | 1.4726 | - | 1.4726 | 378.7782 | 0.05 | 0.7523 | Crowcombe . STW | Crowcombe . STW | 32 | 0.028846 | 28759.1255 | 9.3145 | 136.03 | 140.85 | 141.19 | 182 | 378 | 9.3145 | 150.5045 | 14.4745 | 5.16
15187 | Old Down Fox Inn SPS | 75 | 0.30093 | 3.3134 | - | 3.3134 | 62.6673 | 0.075 | 0.7523 | Tockington Moor Lane STW | Tockington Moor Lane STW | 32 | 0.028846 | 43138.6883 | 0.89479 | 81.71 | 83.14 | 83.14 | 36 | 36 | 0.89479 | 84.0348 | 2.3248 | 1.43
15292 | Henstridge Park Lane (Riverside Gardens) Henstridge No 1 SPS | 80 | 0.30093 | 3.7699 | - | 3.7699 | 81.0134 | 0.08 | 0.7523 | Marnhull Common STW | Henstridge Marsh Lane (Henstridge No 2) SPS | 32 | 0.028846 | 46014.6008 | 1.0618 | 79.54 | 84.46 | 84.46 | - | 82 | 1.0618 | 85.5218 | 5.9818 | 4.92
14446 | Wingfield Pomeroy Lane SPS | 38 | 0.30093 | 0.85059 | - | 0.85059 | 313.3655 | 0.038 | 0.7523 | Trowbridge Bradford Road STW | Wingfield Church Lane SPS | 32 | 0.028846 | 21856.9354 | 11.1979 | 59.66 | 56.25 | 59.81 | 60 | 314 | 11.1979 | 71.0079 | 11.3479 | 0.15
14461 | Broughton Gifford The Common SPS | 100 | 0.30093 | 5.8905 | - | 5.8905 | 161.9654 | 0.1 | 0.7523 | Melksham . STW | Broughton Gifford The Green SPS | 32 | 0.028846 | 57518.251 | 1.5812 | 48.63 | 54.15 | 54.3 | 140 | 162 | 1.5812 | 55.8812 | 7.2512 | 5.67
19771 | Horton Queens Copse (Formerly Holtwood) SPS | 90 | 0.30093 | 4.7713 | - | 4.7713 | 840.5774 | 0.09 | 0.7523 | Gaunts Common . STW | Gaunts Common Horseshoes SPS | 32 | 0.028846 | 51766.4259 | 9.4276 | 47.27 | 59.02 | 59.25 | - | 840 | 9.4276 | 68.6776 | 21.4076 | 11.98
14573 | Warmley Horsecroft Gardens / Wraxall Road SPS | 100 | 0.30093 | 5.8905 | - | 5.8905 | 43.8629 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 32 | 0.028846 | 57518.251 | 0.42822 | 43.78 | 45.3 | 45.3 | 44 | 44 | 0.42822 | 45.7282 | 1.9482 | 1.52
14630 | Haselbury Plucknett . SPS | 80 | 0.30093 | 3.7699 | - | 3.7699 | 109.2993 | 0.08 | 0.7523 | Haselbury Plucknett New Lane STW | Haselbury Plucknett New Lane STW | 32 | 0.028846 | 46014.6008 | 1.4325 | 35.94 | 38.26 | 38.26 | - | 110 | 1.4325 | 39.6925 | 3.7525 | 2.32
15517 | Stogursey Knighton SPS | 75 | 0.30093 | 3.3134 | - | 3.3134 | 283.7328 | 0.075 | 0.7523 | Stogursey . STW | Shurton . SPS | 32 | 0.028846 | 43138.6883 | 4.0512 | 23.28 | 28.18 | 28.19 | 252 | 284 | 4.0512 | 32.2412 | 8.9612 | 4.91
14114 | Glastonbury Edgarley Millfield School SPS | 100 | 0.30093 | 5.8905 | 8 | 8 | 1042.1524 | 0.1 | 1.0217 | Glastonbury The Beckery SSTW | Glastonbury Porchestall SPS | 32 | 0.053206 | 78116.8125 | 18.5418 | 18.5 | 58.32 | 58.32 | 1036 | 1036 | 18.5418 | 76.8618 | 58.3618 | 39.82
17040 | Ringwood Windmill Lane SPS | 110 | 0.30093 | 7.1275 | - | 7.1275 | 290.9428 | 0.11 | 0.7523 | Ringwood Hampshire Hatches Lane STW | St Ives Avon Castle SPS | 32 | 0.028846 | 63270.0761 | 2.5066 | 14.7 | 18.55 | 18.79 | 108 | 290 | 2.5066 | 21.2966 | 6.5966 | 4.09
15326 | Ilchester The Mead Pill Bridge Lane SPS | 80 | 0.30093 | 3.7699 | - | 3.7699 | 95.6637 | 0.08 | 0.7523 | Ilchester Pill Bridge Lane STW | Ilchester Ilchester Main SPS | 32 | 0.028846 | 46014.6008 | 1.2538 | 11.67 | 12.39 | 12.39 | 96 | 96 | 1.2538 | 13.6438 | 1.9738 | 0.72
15181 | Pilning Pilning School SPS | 50 | 0.30093 | 1.4726 | - | 1.4726 | 316.6035 | 0.05 | 0.7523 | Redwick . STW | Pilning Pilning Church The Green SPS | 32 | 0.028846 | 28759.1255 | 7.7856 | 7.21 | 7.18 | 7.38 | 6 | 316 | 7.7856 | 15.1656 | 7.9556 | 0.17
15649 | West Huntspill Rose Farm SPS | 100 | 0.30093 | 5.8905 | - | 5.8905 | 156.5164 | 0.1 | 0.7523 | West Huntspill STW | West Huntspill STW | 32 | 0.028846 | 57518.251 | 1.528 | 5.75 | 5.76 | 6.5 | 106 | 156 | 1.528 | 8.028 | 2.278 | 0.75
15795 | Bath Hazelton Gardens SPS | 100 | 0.27778 | 5.8905 | - | 5.8905 | 58.7657 | 0.1 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 29 | 0.028846 | 57518.251 | 0.57371 | 164.94 | 165.7 | 165.7 | 58 | 58 | 0.57371 | 166.2737 | 1.3337 | 0.76
17255 | Gillingham Park Farm SPS | 100 | 0.27778 | 5.8905 | - | 5.8905 | 156.045 | 0.1 | 0.7523 | Gillingham Common Mead Lane STW | Gillingham Brickyard Lane SPS | 29 | 0.028846 | 57518.251 | 1.5234 | 77.94 | 82.61 | 82.62 | 144 | 156 | 1.5234 | 84.1434 | 6.2034 | 4.68
17584 | Stogursey Paddons Farm SPS | 100 | 0.27778 | 5.8905 | - | 5.8905 | 70.0867 | 0.1 | 0.7523 | Stogursey . STW | Stogursey . STW | 29 | 0.028846 | 57518.251 | 0.68424 | 26.83 | 29.54 | 29.74 | 66 | 70 | 0.68424 | 30.4242 | 3.5942 | 2.91
15295 | Limington Glanfield Terrace SPS | 60 | 0.27778 | 2.1206 | - | 2.1206 | 378.8875 | 0.06 | 0.7523 | Chilton Cantelo Hornsey Bridge STW | Limington Main SPS | 29 | 0.028846 | 34510.9506 | 7.2879 | 20.83 | 23.48 | 23.94 | 336 | 378 | 7.2879 | 31.2279 | 10.3979 | 3.11
17765 | Poole 107 Lilliput Road SPS | 90 | 0.27778 | 4.7713 | - | 4.7713 | 175.3719 | 0.09 | 0.7523 | Poole Cabot Lane STW | Poole Shore Road SPS | 29 | 0.028846 | 51766.4259 | 1.9669 | 20.74 | 36.59 | 36.59 | 176 | 176 | 1.9669 | 38.5569 | 17.8169 | 15.85
17244 | West Moors Blackfield Farm SPS | 100 | 0.27778 | 5.8905 | - | 5.8905 | 136.577 | 0.1 | 0.7523 | Palmersford . STW | West Moors Pennington Copse SPS | 29 | 0.028846 | 57518.251 | 1.3334 | 18.76 | 19.28 | 19.37 | 114 | 136 | 1.3334 | 20.7034 | 1.9434 | 0.61
15460 | Meare Green Stoke St Gregory SPS | 80 | 0.27778 | 3.7699 | 0.4 | 0.4 | 78.188 | 0.08 | 0.079821 | Stoke St Gregory . STW | Stoke St Gregory No 1 Lane End SPS | 29 | 0.00032474 | 4882.3008 | 0.014636 | 16.73 | 18.45 | 18.82 | 46 | 76 | 0.014636 | 18.8346 | 2.1046 | 2.09
15558 | Weymouth Swimming Pool Knightsdale Road SPS | 150 | 0.27778 | 13.2536 | - | 13.2536 | 42.297 | 0.15 | 0.7523 | Weymouth . STW | Weymouth Radipole SPS | 29 | 0.028846 | 86277.3765 | 0.24332 | 1.75 | 2.41 | 2.45 | 4 | 42 | 0.24332 | 2.6933 | 0.94332 | 0.7
15624 | Timsbury Crowcombe Lane SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 149.2616 | 0.1 | 0.7523 | Cam Valley Dunkerton STW | Carlingcott Stoneage Lane SPS | 27 | 0.028846 | 57518.251 | 1.4572 | 143.51 | 144.18 | 144.18 | 150 | 150 | 1.4572 | 145.6372 | 2.1272 | 0.67
14156 | Yatton Keynell Tiddly Wink SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 398.2778 | 0.1 | 0.7523 | Long Dean . STW | Long Dean . STW | 27 | 0.028846 | 57518.251 | 3.8883 | 121.85 | 125.49 | 125.6 | 338 | 398 | 3.8883 | 129.4883 | 7.6383 | 3.75
14160 | Sherston The Tarters SPS | 95 | 0.25463 | 5.3162 | - | 5.3162 | 72.4734 | 0.095 | 0.7523 | Sherston . STW | Sherston . STW | 27 | 0.028846 | 54642.3385 | 0.75692 | 110.21 | 112.23 | 112.23 | 66 | 66 | 0.75692 | 112.9869 | 2.7769 | 2.02
14005 | Bath Englishcombe Rise (Previously Whiteway Avenue) SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 51.7777 | 0.1 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 27 | 0.028846 | 57518.251 | 0.50549 | 106.56 | 114.66 | 114.66 | 52 | 52 | 0.50549 | 115.1655 | 8.6055 | 8.1
19301 | Weston-Super-Mare Worlebury Hill Road SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 161.9491 | 0.1 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Uphill . SPS | 27 | 0.028846 | 57518.251 | 1.5811 | 93.5 | 95.23 | 95.23 | 162 | 162 | 1.5811 | 96.8111 | 3.3111 | 1.73
14140 | Hullavington Bradfield SPS | 75 | 0.25463 | 3.3134 | - | 3.3134 | 307.3517 | 0.075 | 0.7523 | Hullavington . STW | Hullavington . STW | 27 | 0.028846 | 43138.6883 | 4.3885 | 83.22 | 89.58 | 89.58 | 308 | 308 | 4.3885 | 93.9685 | 10.7485 | 6.36
19409 | Winterbourne Flaxpits Lane (Burghley Court) SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 113.9556 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 27 | 0.028846 | 57518.251 | 1.1125 | 66.94 | 68.46 | 68.54 | 96 | 114 | 1.1125 | 69.6525 | 2.7125 | 1.6
15455 | Wellington Wharf Cottages SPS | 80 | 0.25463 | 3.7699 | - | 3.7699 | 63.1965 | 0.08 | 0.7523 | Wellington Tone STW | Wellington Tone STW | 27 | 0.028846 | 46014.6008 | 0.82826 | 48.15 | 49.06 | 49.3 | 58 | 64 | 0.82826 | 50.1283 | 1.9783 | 1.15
14321 | Downton Waterside SPS | 75 | 0.25463 | 3.3134 | - | 3.3134 | 21.0285 | 0.075 | 0.7523 | Downton Moot Lane STW | Downton South Lane SPS | 27 | 0.028846 | 43138.6883 | 0.30025 | 36.15 | 37.11 | 37.31 | 12 | 22 | 0.30025 | 37.6103 | 1.4603 | 1.16
19768 | Sturminster Marshall Parklea SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 2.8525 | 0.1 | 0.7523 | Tarrant Crawford . STW | Sturminster Marshall High Street SPS | 27 | 0.028846 | 57518.251 | 0.027848 | 25.92 | 25.93 | 25.93 | 2 | 2 | 0.027848 | 25.9578 | 0.037848 | 0.01
14117 | Street Petvine Close Portway Also S0118 SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 53.3814 | 0.1 | 0.7523 | Glastonbury The Beckery SSTW | Street Main SPS | 27 | 0.028846 | 57518.251 | 0.52115 | 24.47 | 24.74 | 24.74 | 54 | 54 | 0.52115 | 25.2611 | 0.79115 | 0.27
15599 | Weston-Super-Mare Capri Villas SPS | 50 | 0.25463 | 1.4726 | - | 1.4726 | 357.3193 | 0.05 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Weston-Super-Mare Accommodation Road Bleadon STW | 27 | 0.028846 | 28759.1255 | 8.7868 | 19.62 | 27.46 | 27.46 | 358 | 358 | 8.7868 | 36.2468 | 16.6268 | 7.84
19779 | Portishead Woodlands Road SPS | 63 | 0.25463 | 2.3379 | - | 2.3379 | 297.7473 | 0.063 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Lake Grounds SPS | 27 | 0.028846 | 36236.4981 | 5.3646 | 17.14 | 31.18 | 31.18 | 298 | 298 | 5.3646 | 36.5446 | 19.4046 | 14.04
17633 | Bournemouth Queens Park Avenue SPS | 110 | 0.25463 | 7.1275 | - | 7.1275 | 23.3952 | 0.11 | 0.7523 | Holdenhurst Riverside Avenue STW | Holdenhurst Riverside Avenue STW | 27 | 0.028846 | 63270.0761 | 0.20156 | 15.39 | 15.35 | 15.47 | 2 | 12 | 0.20156 | 15.6716 | 0.28156 | 0.08
19403 | Compton Dundon Street Road SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 437.317 | 0.1 | 0.7523 | Somerton Barpool Lane STW | Compton Dundon Ham Lane SPS | 27 | 0.028846 | 57518.251 | 4.2694 | 12.42 | 11.56 | 12.44 | 4 | 440 | 4.2694 | 16.7094 | 4.2894 | 0.02
14602 | Creech St Michael Bull Street SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 289.5221 | 0.1 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 27 | 0.028846 | 57518.251 | 2.8265 | 9.19 | 9.28 | 9.95 | 274 | 290 | 2.8265 | 12.7765 | 3.5865 | 0.76
17319 | Brean Beach SPS | 80 | 0.25463 | 3.7699 | - | 3.7699 | 24.4227 | 0.08 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Brean Sunnyside Warren Farm SPS | 27 | 0.028846 | 46014.6008 | 0.32009 | 8.17 | 7.32 | 8.25 | 2 | 24 | 0.32009 | 8.5701 | 0.40009 | 0.08
19506 | Severn Beach Western Approach SPS | 125 | 0.25463 | 9.2039 | - | 9.2039 | 1107.4095 | 0.125 | 0.7523 | Redwick . STW | Severn Beach . SPS | 27 | 0.028846 | 71897.8138 | 8.0734 | 6.89 | 6.28 | 8.5 | 82 | 1108 | 8.0734 | 16.5734 | 9.6834 | 1.61
14280 | Lytchett Minster Slough Lane SPS | 100 | 0.25463 | 5.8905 | - | 5.8905 | 148.6012 | 0.1 | 0.7523 | Lytchett Minster Lytchett Bay STW | Lytchett Minster Lytchett Bay STW | 27 | 0.028846 | 57518.251 | 1.4508 | 5.1 | 9.39 | 9.39 | 148 | 148 | 1.4508 | 10.8408 | 5.7408 | 4.29
14370 | Maiden Bradley Frome Road SPS | 37 | 0.23148 | 0.80641 | - | 0.80641 | 468.2657 | 0.037 | 0.7523 | Maiden Bradley . STW | Maiden Bradley . STW | 24 | 0.028846 | 21281.7529 | 17.3566 | 171.23 | 197.35 | 197.35 | - | 468 | 17.3566 | 214.7066 | 43.4766 | 26.12
12497 | Wiveliscombe Styles SPS | 125 | 0.23148 | 9.2039 | - | 9.2039 | 43.3665 | 0.125 | 0.7523 | Wiveliscombe Styles STW | Wiveliscombe Styles STW | 24 | 0.028846 | 71897.8138 | 0.31616 | 101.63 | 103.08 | 103.08 | 44 | 44 | 0.31616 | 103.3962 | 1.7662 | 1.45
15619 | Brinkworth St Micheals Close SPS | 115 | 0.23148 | 7.7902 | - | 7.7902 | 49.8618 | 0.115 | 0.7523 | Brinkworth . STW | Brinkworth . STW | 24 | 0.028846 | 66145.9887 | 0.40531 | 92.47 | 93.5 | 93.53 | 46 | 48 | 0.40531 | 93.9353 | 1.4653 | 1.06
14201 | Malmesbury Station Yard SPS | 100 | 0.23148 | 5.8905 | - | 5.8905 | 68.8774 | 0.1 | 0.7523 | Malmesbury . STW | Malmesbury St Johns Street SPS | 24 | 0.028846 | 57518.251 | 0.67243 | 72.04 | 71.03 | 72.04 | 0 | 70 | 0.67243 | 72.7124 | 0.67243 | 0
19168 | Bishops Lydeard Railway Station SPS | 50 | 0.23148 | 1.4726 | - | 1.4726 | 531.2086 | 0.05 | 0.7523 | Bishops Lydeard . STW | Bishops Lydeard . STW | 24 | 0.028846 | 28759.1255 | 13.0629 | 53.67 | 55.45 | 57.3 | 312 | 532 | 13.0629 | 70.3629 | 16.6929 | 3.63
15223 | Burley Moorhill SPS | 100 | 0.23148 | 5.8905 | - | 5.8905 | 317.7711 | 0.1 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Burley Esdaile Lane SPS | 24 | 0.028846 | 57518.251 | 3.1023 | 50.97 | 55.61 | 55.94 | 316 | 318 | 3.1023 | 59.0423 | 8.0723 | 4.97
15536 | Wellow Mill Hill SPS | 100 | 0.23148 | 5.8905 | 5 | 5 | 124.7451 | 0.1 | 0.63857 | Wellow . STW | Wellow . STW | 24 | 0.020783 | 48823.0078 | 0.88427 | 45.12 | 54.92 | 54.92 | 124 | 124 | 0.88427 | 55.8043 | 10.6843 | 9.8
17125 | Frampton Cotterell Mill Lane SPS | 63 | 0.23148 | 2.3379 | - | 2.3379 | 89.742 | 0.063 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 24 | 0.028846 | 36236.4981 | 1.6169 | 42.8 | 42.78 | 42.85 | 82 | 90 | 1.6169 | 44.4669 | 1.6669 | 0.05
14424 | Farringdon . SPS | 50 | 0.23148 | 1.4726 | - | 1.4726 | 1266.0768 | 0.05 | 0.7523 | Stogursey . STW | Stogursey . STW | 24 | 0.028846 | 28759.1255 | 31.1339 | 36.4 | 25.18 | 48.43 | 312 | 1266 | 31.1339 | 79.5639 | 43.1639 | 12.03
15367 | Cannington Mill Close SPS | 80 | 0.23148 | 3.7699 | - | 3.7699 | 28.1581 | 0.08 | 0.7523 | Cannington . STW | Cannington . STW | 24 | 0.028846 | 46014.6008 | 0.36904 | 13.06 | 13.48 | 13.52 | 22 | 28 | 0.36904 | 13.889 | 0.82904 | 0.46
19544 | Avonmouth Cabot Park No.3 SPS | 200 | 0.23148 | 23.5619 | - | 23.5619 | 208.6568 | 0.2 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Cabot Park No.1 SPS | 24 | 0.028846 | 115036.502 | 0.82844 | 7.25 | 8.04 | 8.09 | - | 208 | 0.82844 | 8.9184 | 1.6684 | 0.84
15657 | West Huntspill White Cottage SPS | 100 | 0.23148 | 5.8905 | - | 5.8905 | 55.47 | 0.1 | 0.7523 | West Huntspill STW | West Huntspill STW | 24 | 0.028846 | 57518.251 | 0.54154 | 6.09 | 5.61 | 6.09 | 0 | 56 | 0.54154 | 6.6315 | 0.54154 | 0
17583 | Bagley Snake Lane SPS | 80 | 0.20833 | 3.7699 | - | 3.7699 | 1043.8052 | 0.08 | 0.7523 | Wedmore . STW | Mudgley Mudgley Cross SPS | 22 | 0.028846 | 46014.6008 | 13.6802 | 67.5 | 69.54 | 71.76 | 420 | 1044 | 13.6802 | 85.4402 | 17.9402 | 4.26
17715 | Bath Bailbrook Lane SPS | 90 | 0.20833 | 4.7713 | - | 4.7713 | 128.5977 | 0.09 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 22 | 0.028846 | 51766.4259 | 1.4423 | 59.62 | 60.72 | 60.72 | 110 | 110 | 1.4423 | 62.1623 | 2.5423 | 1.1
14477 | Melksham Westlands Lane SPS | 32 | 0.20833 | 0.60319 | - | 0.60319 | 423.5547 | 0.032 | 0.7523 | Melksham . STW | Melksham . STW | 22 | 0.028846 | 18405.8403 | 19.1766 | 50.31 | 57.49 | 57.93 | 306 | 424 | 19.1766 | 77.1066 | 26.7966 | 7.62
15682 | Ashcott Bradley Lane (Taunton Road) SPS | 50 | 0.20833 | 1.4726 | - | 1.4726 | 552.8889 | 0.05 | 0.7523 | Chilton Trinity . STW | Pedwell . SPS | 22 | 0.028846 | 28759.1255 | 13.596 | 33.36 | 37.8 | 38.11 | 510 | 552 | 13.596 | 51.706 | 18.346 | 4.75
19789 | Corfe Mullen Admiralty Source SPS | 110 | 0.20833 | 7.1275 | - | 7.1275 | 1366.8776 | 0.11 | 0.7523 | Corfe Mullen Dorchester Road STW | Corfe Mullen Pardys Hill SPS | 22 | 0.028846 | 63270.0761 | 11.7761 | 23.2 | 42.17 | 42.17 | 1366 | 1366 | 11.7761 | 53.9461 | 30.7461 | 18.97
17201 | Portishead Masonic Lodge SPS | 80 | 0.20833 | 3.7699 | - | 3.7699 | 45.2885 | 0.08 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Port Marine SPS | 22 | 0.028846 | 46014.6008 | 0.59356 | 9.82 | 18.44 | 18.44 | 46 | 46 | 0.59356 | 19.0336 | 9.2136 | 8.62
15427 | Purton No 5 Berkely Arms SPS | - | 0.20833 | - | - | - | 214.2662 | - | - | Sharpness . STW | Purton Hinton Road SPS | 22 | - | - | - | 9.53 | 9.32 | 11 | 180 | 204 | - | - | - | 1.47
19543 | Avonmouth Cabot Park No.2 SPS | 100 | 0.20833 | 5.8905 | - | 5.8905 | 705.8722 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Cabot Park No.1 SPS | 22 | 0.028846 | 57518.251 | 6.8912 | 7.13 | 7.75 | 7.87 | 16 | 696 | 6.8912 | 14.7612 | 7.6312 | 0.74
17320 | Brean Down SPS | 80 | 0.20833 | 3.7699 | - | 3.7699 | 1435.7886 | 0.08 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Brean Beach SPS | 22 | 0.028846 | 46014.6008 | 18.8176 | 6.36 | 8.29 | 8.74 | 1404 | 1436 | 18.8176 | 27.5576 | 21.1976 | 2.38
15006 | Bournemouth No 2 SPS | 150 | 0.20833 | 13.2536 | - | 13.2536 | 68.9351 | 0.15 | 0.7523 | Holdenhurst Riverside Avenue STW | Bournemouth No 1 SPS | 22 | 0.028846 | 86277.3765 | 0.39656 | 5.39 | 5.32 | 5.39 | 0 | 68 | 0.39656 | 5.7866 | 0.39656 | 0
15337 | Penselwood Great Hill SPS | 76 | 0.18518 | 3.4023 | - | 3.4023 | 121.7088 | 0.076 | 0.7523 | Bourton Silton STW | Penselwood Penn Mill SPS | 20 | 0.028846 | 43713.8708 | 1.7075 | 185.2 | 198.74 | 198.74 | - | 122 | 1.7075 | 200.4475 | 15.2475 | 13.54
15112 | Lydeway Marsh Farm SPS | 100 | 0.18518 | 5.8905 | - | 5.8905 | 215.6894 | 0.1 | 0.7523 | Urchfont . STW | Lydeway Clock Inn SPS | 20 | 0.028846 | 57518.251 | 2.1057 | 110.23 | 110.46 | 111.3 | 180 | 216 | 2.1057 | 113.4057 | 3.1757 | 1.07
14194 | Compton Bassett Breach Farm SPS | 50 | 0.18518 | 1.4726 | - | 1.4726 | 342.672 | 0.05 | 0.7523 | Compton Bassett . STW | Compton Bassett The Pond SPS | 20 | 0.028846 | 28759.1255 | 8.4266 | 101.47 | 102.18 | 102.18 | - | 342 | 8.4266 | 110.6066 | 9.1366 | 0.71
19177 | Dinton Tyndale Meadows SPS | 100 | 0.18518 | 5.8905 | - | 5.8905 | 57.5898 | 0.1 | 0.7523 | Fovant . STW | Dinton Bratch Lane SPS | 20 | 0.028846 | 57518.251 | 0.56223 | 80.71 | 83 | 83 | 58 | 58 | 0.56223 | 83.5622 | 2.8522 | 2.29
14436 | Dilton Marsh Fairhaven SPS | 120 | 0.18518 | 8.4823 | - | 8.4823 | 134.8547 | 0.12 | 0.7523 | Westbury STW | Dilton Marsh Pen Knapp SPS | 20 | 0.028846 | 69021.9012 | 1.0369 | 68.5 | 74.29 | 74.29 | 134 | 134 | 1.0369 | 75.3269 | 6.8269 | 5.79
15312 | Odcombe No 3 SPS | 32 | 0.18518 | 0.60319 | - | 0.60319 | 232.3032 | 0.032 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Odcombe No 1 SPS | 20 | 0.028846 | 18405.8403 | 10.5176 | 68.18 | 81.62 | 81.62 | - | 232 | 10.5176 | 92.1376 | 23.9576 | 13.44
14066 | Hanham Sally On The Barn SPS | 100 | 0.18518 | 5.8905 | - | 5.8905 | 195.6779 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 20 | 0.028846 | 57518.251 | 1.9103 | 50.38 | 63.94 | 63.94 | 196 | 196 | 1.9103 | 65.8503 | 15.4703 | 13.56
13261 | Sandylands . SPS | 80 | 0.18518 | 3.7699 | - | 3.7699 | 72.9766 | 0.08 | 0.7523 | Wellington Tone STW | Wellington Tone STW | 20 | 0.028846 | 46014.6008 | 0.95644 | 47.84 | 48.04 | 48.04 | 36 | 36 | 0.95644 | 48.9964 | 1.1564 | 0.2
10309 | Castle Cary Trading Estate Torbay Road SPS | - | 0.18518 | - | - | - | 80.4548 | - | - | Castle Cary Near Dimmer STW | Castle Cary Near Dimmer STW | 20 | - | - | - | 47.79 | 50 | 50.14 | 70 | 80 | - | - | - | 2.35
15360 | Wedmore Sand SPS | 75 | 0.18518 | 3.3134 | - | 3.3134 | 731.7894 | 0.075 | 0.7523 | Wedmore . STW | Wedmore . STW | 20 | 0.028846 | 43138.6883 | 10.4488 | 46.74 | 29.16 | 49.97 | 130 | 732 | 10.4488 | 60.4188 | 13.6788 | 3.23
15323 | Limington Fairview Terrace SPS | 60 | 0.18518 | 2.1206 | - | 2.1206 | 461.1371 | 0.06 | 0.7523 | Chilton Cantelo Hornsey Bridge STW | Limington Main SPS | 20 | 0.028846 | 34510.9506 | 8.87 | 28.47 | 26.33 | 29.59 | - | 462 | 8.87 | 38.46 | 9.99 | 1.12
19793 | Pill Rock Cottages SPS | 110 | 0.18518 | 7.1275 | - | 7.1275 | 534.434 | 0.11 | 0.7523 | Avonmouth Kingsweston Lane STW | Pill Ham Green Hospital No.1 Station SPS | 20 | 0.028846 | 63270.0761 | 4.6043 | 12.23 | 29.71 | 29.71 | 534 | 534 | 4.6043 | 34.3143 | 22.0843 | 17.48
15398 | Bridgwater Friarn Lawn SPS | 100 | 0.18518 | 5.8905 | - | 5.8905 | 99.5004 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Blake Gardens SPS | 20 | 0.028846 | 57518.251 | 0.97139 | 9.55 | 12.12 | 12.21 | 88 | 100 | 0.97139 | 13.1814 | 3.6314 | 2.66
17203 | Bristol Broad Quay SPS | 90 | 0.18518 | 4.7713 | - | 4.7713 | 55.9139 | 0.09 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 20 | 0.028846 | 51766.4259 | 0.62711 | 8.18 | 8.95 | 9.02 | 38 | 56 | 0.62711 | 9.6471 | 1.4671 | 0.84
17240 | Otterhampton Dame Withycombe Villas SPS | 90 | 0.18518 | 4.7713 | - | 4.7713 | 249.0123 | 0.09 | 0.7523 | Combwich Quay Road SPS | Combwich Brookside SPS | 20 | 0.028846 | 51766.4259 | 2.7928 | 6.93 | 6.89 | 8.08 | 24 | 250 | 2.7928 | 10.8728 | 3.9428 | 1.15
15601 | Kingston Seymour Pool Farm SPS | 75 | 0.18518 | 3.3134 | - | 3.3134 | 428.3544 | 0.075 | 0.7523 | Kingston Seymour Back Lane STW | Kingston Seymour Fairfield (Kingston Seymour West) SPS | 20 | 0.028846 | 43138.6883 | 6.1162 | 5.6 | 5.54 | 5.66 | 422 | 428 | 6.1162 | 11.7762 | 6.1762 | 0.06
15307 | South Petherton West Street SPS | 75 | 0.18518 | 3.3134 | - | 3.3134 | 22.6826 | 0.075 | 0.7523 | South Petherton North Street STW | South Petherton North Street STW | 20 | 0.028846 | 43138.6883 | 0.32387 | - | - | - | - | - | 0.32387 | - | - | -
14001 | Bath Southstoke Road SPS | 100 | 0.16204 | 5.8905 | - | 5.8905 | 233.4516 | 0.1 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 17 | 0.028846 | 57518.251 | 2.2791 | 150.17 | 160.31 | 160.31 | - | 234 | 2.2791 | 162.5891 | 12.4191 | 10.14
15534 | Timsbury The Hook SPS | 75 | 0.16204 | 3.3134 | - | 3.3134 | 52.3812 | 0.075 | 0.7523 | Cam Valley Dunkerton STW | Carlingcott Stoneage Lane SPS | 17 | 0.028846 | 43138.6883 | 0.74792 | 135.33 | 138 | 138 | 52 | 52 | 0.74792 | 138.7479 | 3.4179 | 2.67
14367 | Mere Mere Causeway SPS | 75 | 0.16204 | 3.3134 | - | 3.3134 | 197.8612 | 0.075 | 0.7523 | Mere Rook Street STW | Mere Edgebridge SPS | 17 | 0.028846 | 43138.6883 | 2.8251 | 96.6 | 99.96 | 100.47 | 166 | 198 | 2.8251 | 103.2951 | 6.6951 | 3.87
15121 | Compton Enford SPS | 35 | 0.16204 | 0.72158 | - | 0.72158 | 688.2249 | 0.035 | 0.7523 | Netheravon . STW | Marston The Plough SPS | 17 | 0.028846 | 20131.3879 | 27.5349 | 90.45 | 92.66 | 93.39 | 650 | 688 | 27.5349 | 120.9249 | 30.4749 | 2.94
14182 | Heddington Beacon Hill SPS | 50 | 0.16204 | 1.4726 | - | 1.4726 | 277.9917 | 0.05 | 0.7523 | Calne . STW | Broads Green . SPS | 17 | 0.028846 | 28759.1255 | 6.8361 | 87.76 | 90.51 | 90.65 | - | 278 | 6.8361 | 97.4861 | 9.7261 | 2.89
14491 | Westbury Leigh Mill Lane SPS | 50 | 0.16204 | 1.4726 | - | 1.4726 | 58.1951 | 0.05 | 0.7523 | Westbury STW | Westbury STW | 17 | 0.028846 | 28759.1255 | 1.4311 | 71.43 | 71.57 | 71.57 | 58 | 58 | 1.4311 | 73.0011 | 1.5711 | 0.14
14629 | Wincanton Bennets Field SPS | 75 | 0.16204 | 3.3134 | - | 3.3134 | 60.1628 | 0.075 | 0.7523 | Wincanton . STW | Wincanton . STW | 17 | 0.028846 | 43138.6883 | 0.85903 | 70.94 | 71.67 | 71.67 | 60 | 60 | 0.85903 | 72.529 | 1.589 | 0.73
15204 | Iwerne Minster Oakwood Drive SPS | 80 | 0.16204 | 3.7699 | - | 3.7699 | 139.4928 | 0.08 | 0.7523 | Iwerne Minster . STW | Iwerne Minster . STW | 17 | 0.028846 | 46014.6008 | 1.8282 | 68.69 | 69.49 | 69.49 | 140 | 140 | 1.8282 | 71.3182 | 2.6282 | 0.8
14167 | Lacock Corsham Road SPS | 75 | 0.16204 | 3.3134 | - | 3.3134 | 18.2869 | 0.075 | 0.7523 | Lacock . STW | Lacock Nethercote Hill SPS | 17 | 0.028846 | 43138.6883 | 0.26111 | 61.51 | 61.65 | 61.65 | 18 | 18 | 0.26111 | 61.9111 | 0.40111 | 0.14
15814 | Chippenham Methuen Park Bath Road SPS | 100 | 0.16204 | 5.8905 | - | 5.8905 | 157.756 | 0.1 | 0.7523 | Chippenham Blackwell Hams STW | Chippenham Blackwell Hams STW | 17 | 0.028846 | 57518.251 | 1.5401 | 55.69 | 57.28 | 57.32 | 154 | 158 | 1.5401 | 58.8601 | 3.1701 | 1.63
15550 | Weymouth Markham House Wyke Road SPS | 100 | 0.16204 | 5.8905 | - | 5.8905 | 403.7808 | 0.1 | 0.7523 | Weymouth . STW | Weymouth Radipole SPS | 17 | 0.028846 | 57518.251 | 3.942 | 44.1 | 51.26 | 54.57 | 52 | 404 | 3.942 | 58.512 | 14.412 | 10.47
15308 | West Chinnock Snails Hill SPS | 50 | 0.16204 | 1.4726 | - | 1.4726 | 266.4288 | 0.05 | 0.7523 | South Petherton North Street STW | West Chinnock Garage SPS | 17 | 0.028846 | 28759.1255 | 6.5517 | 40.47 | 50.64 | 51.69 | - | 266 | 6.5517 | 58.2417 | 17.7717 | 11.22
14478 | Melksham Northbrook Road SPS | 100 | 0.16204 | 5.8905 | - | 5.8905 | 35.752 | 0.1 | 0.7523 | Melksham . STW | Melksham . STW | 17 | 0.028846 | 57518.251 | 0.34904 | 37.12 | 37.37 | 37.4 | 30 | 36 | 0.34904 | 37.749 | 0.62904 | 0.28
14235 | Bovington Duncan Crescent SPS | 100 | 0.16204 | 5.8905 | 7 | 7 | 234.9027 | 0.1 | 0.894 | Wool . STW | Bovington Rhine Road SPS | 17 | 0.040736 | 68352.211 | 3.2155 | 28.64 | 33.17 | 33.43 | - | 234 | 3.2155 | 36.6455 | 8.0055 | 4.79
14448 | Limpley Stoke Crowe Hill SPS | 30 | 0.16204 | 0.53014 | - | 0.53014 | 300.2612 | 0.03 | 0.7523 | Freshford . STW | Freshford . STW | 17 | 0.028846 | 17255.4753 | 14.8663 | 28.49 | 32.1 | 32.75 | 8 | 300 | 14.8663 | 47.6163 | 19.1263 | 4.26
19257 | Bridgwater Huntworth Business Park SPS | 100 | 0.16204 | 5.8905 | - | 5.8905 | 1153.5918 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Taunton Road SPS | 17 | 0.028846 | 57518.251 | 11.2622 | 9.98 | 6.86 | 12.11 | 140 | 1154 | 11.2622 | 23.3722 | 13.3922 | 2.13
17415 | Porlock Caravan Site SPS | 100 | 0.16204 | 5.8905 | - | 5.8905 | 164.4733 | 0.1 | 0.7523 | Porlock Sparkhayes Lane STW | Porlock Sparkhayes Lane STW | 17 | 0.028846 | 57518.251 | 1.6057 | - | - | - | - | - | 1.6057 | - | - | -
17891 | Ham O/S The Dairy SPS | - | 0.16204 | - | - | - | 443.6391 | - | - | Bradford On Tone . STW | Bradford On Tone Hockholler A38 SPS | 17 | - | - | - | - | - | - | - | - | - | - | - | -
19587 | Dunball Clyce SPS | - | 0.16204 | - | - | - | 0 | - | - | Dunball Clyce SPS | - | 17 | - | - | - | - | - | - | - | - | - | - | - | -
15110 | Etchilhampton Mixon Close SPS | 100 | 0.13889 | 5.8905 | - | 5.8905 | 30.581 | 0.1 | 0.7523 | Etchilhampton Manor Farm STW | Etchilhampton Manor Farm STW | 15 | 0.028846 | 57518.251 | 0.29855 | 124.5 | 124.69 | 124.69 | - | 26 | 0.29855 | 124.9886 | 0.48855 | 0.19
15332 | Crewkerne Hardy Court SPS | 75 | 0.13889 | 3.3134 | - | 3.3134 | 20.9918 | 0.075 | 0.7523 | Crewkerne Trading Estate Crewkerne East STW | Crewkerne Trading Estate Crewkerne East STW | 15 | 0.028846 | 43138.6883 | 0.29973 | 105.32 | 105.96 | 105.96 | 20 | 20 | 0.29973 | 106.2597 | 0.93973 | 0.64
15518 | Kilve Hilltop Lane SPS | 100 | 0.13889 | 5.8905 | - | 5.8905 | 117.8814 | 0.1 | 0.7523 | Kilve Beach Car Park STW | Kilve Beach Car Park STW | 15 | 0.028846 | 57518.251 | 1.1508 | 83.86 | 92.15 | 92.51 | 110 | 116 | 1.1508 | 93.6608 | 9.8008 | 8.65
15108 | Potterne Court Hill SPS | 100 | 0.13889 | 5.8905 | - | 5.8905 | 331.3472 | 0.1 | 0.7523 | Potterne . STW | Potterne . STW | 15 | 0.028846 | 57518.251 | 3.2349 | 78.55 | 91.61 | 91.61 | - | 332 | 3.2349 | 94.8449 | 16.2949 | 13.06
17083 | Bristol New Station Road SPS | - | 0.13889 | - | - | - | 7.0606 | - | - | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 15 | - | - | - | 63.89 | 64.07 | 64.07 | 8 | 8 | - | - | - | 0.18
17556 | Wimborne Cobbs Road SPS | 90 | 0.13889 | 4.7713 | - | 4.7713 | 183.5939 | 0.09 | 0.7523 | Wimborne Brook Road STW | Wimborne Brook Road No 1 SPS | 15 | 0.028846 | 51766.4259 | 2.0591 | 63.31 | 68.07 | 68.07 | 184 | 184 | 2.0591 | 70.1291 | 6.8191 | 4.76
14277 | Wool Bindon Lane SPS | 80 | 0.13889 | 3.7699 | - | 3.7699 | 90.7805 | 0.08 | 0.7523 | Wool . STW | Wool Railway Cottages SPS | 15 | 0.028846 | 46014.6008 | 1.1898 | 14.27 | 15.27 | 15.27 | 90 | 90 | 1.1898 | 16.4598 | 2.1898 | 1
15611 | Backwell Brook Farm SPS | 100 | 0.13889 | 5.8905 | - | 5.8905 | 453.006 | 0.1 | 0.7523 | Kingston Seymour Back Lane STW | Backwell Backwell Common SPS | 15 | 0.028846 | 57518.251 | 4.4226 | 14.17 | 14.2 | 14.21 | 452 | 454 | 4.4226 | 18.6326 | 4.4626 | 0.04
10193 | Burton The Green SPS | - | 0.13889 | - | - | - | 37.2399 | - | - | Christchurch Stoney Lane STW | Burton Stony Lane SPS | 15 | - | - | - | 8.01 | 8.72 | 8.72 | 38 | 38 | - | - | - | 0.71
19710 | Avonmouth Gloucester Road SPS | 100 | 0.13889 | 5.8905 | - | 5.8905 | 4.3676 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Victoria Road SPS | 15 | 0.028846 | 57518.251 | 0.04264 | 7.69 | 7.68 | 7.69 | 0 | 4 | 0.04264 | 7.7326 | 0.04264 | 0
17188 | Woolavington Reeds Drive SPS | 100 | 0.13889 | 5.8905 | - | 5.8905 | 15.3368 | 0.1 | 0.7523 | West Huntspill STW | West Huntspill STW | 15 | 0.028846 | 57518.251 | 0.14973 | 7.18 | 7.15 | 7.27 | 2 | 6 | 0.14973 | 7.4197 | 0.23973 | 0.09
14597 | Highbridge Lawrence Close Isleport Business Park SPS | 150 | 0.13889 | 13.2536 | - | 13.2536 | 334.4789 | 0.15 | 0.7523 | West Huntspill STW | Highbridge Tylers End SPS | 15 | 0.028846 | 86277.3765 | 1.9242 | 5.52 | 6.18 | 6.47 | 66 | 332 | 1.9242 | 8.3942 | 2.8742 | 0.95
15709 | Chickerell East Fleet Farm SPS | 100 | 0.13889 | 5.8905 | - | 5.8905 | 821.0009 | 0.1 | 0.7523 | Weymouth . STW | Weymouth Radipole SPS | 15 | 0.028846 | 57518.251 | 8.0152 | 4.05 | 34.14 | 34.5 | 800 | 822 | 8.0152 | 42.5152 | 38.4652 | 30.45
11353 | Sherston Field View SPS | 90 | 0.13889 | 4.7713 | - | 4.7713 | 51.3132 | 0.09 | 0.7523 | Sherston . STW | Sherston . STW | 15 | 0.028846 | 51766.4259 | 0.57551 | - | - | - | - | - | 0.57551 | - | - | -
15242 | Poole Merleys Way Merley SPS | - | 0.13889 | - | - | - | 0 | - | - | Wimborne Brook Road STW | Canford Magna Canford Main SPS | 15 | - | - | - | - | - | - | - | - | - | - | - | -
15116 | Coate Lodge SPS | 100 | 0.11574 | 5.8905 | - | 5.8905 | 295.8127 | 0.1 | 0.7523 | All Cannings Lower Mill Farm STW | Coate Spaniels Bridge SPS | 12 | 0.028846 | 57518.251 | 2.8879 | 121.35 | 123.74 | 123.79 | 294 | 296 | 2.8879 | 126.6779 | 5.3279 | 2.44
15105 | Bromham Westbrook Green SPS | 75 | 0.11574 | 3.3134 | - | 3.3134 | 19.2852 | 0.075 | 0.7523 | Rowde . STW | Bromham Loop Hill SPS | 12 | 0.028846 | 43138.6883 | 0.27536 | 109.14 | 109.59 | 109.6 | 18 | 20 | 0.27536 | 109.8754 | 0.73536 | 0.46
15287 | Yeovil Combe Street Lane SPS | 75 | 0.11574 | 3.3134 | - | 3.3134 | 91.6841 | 0.075 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Sherborne Road (Pen Mill) STW | 12 | 0.028846 | 43138.6883 | 1.3091 | 98.35 | 97.53 | 98.35 | 0 | 92 | 1.3091 | 99.6591 | 1.3091 | 0
19820 | Pitminster Queens Arms SPS | 100 | 0.11574 | 5.8905 | - | 5.8905 | 81.1407 | 0.1 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Pitminster Weir SPS | 12 | 0.028846 | 57518.251 | 0.79215 | 79.58 | 81.54 | 81.54 | 78 | 78 | 0.79215 | 82.3322 | 2.7522 | 1.96
15491 | Symondsbury Quarr Lane SPS | 100 | 0.11574 | 5.8905 | - | 5.8905 | 320.9311 | 0.1 | 0.7523 | Bridport Wych Farm STW | Symondsbury West Road Foundry SPS | 12 | 0.028846 | 57518.251 | 3.1332 | 76.57 | 90.61 | 93.99 | 246 | 320 | 3.1332 | 97.1232 | 20.5532 | 17.42
15789 | Gillingham Chantry Fields (Waitrose) SPS | 100 | 0.11574 | 5.8905 | - | 5.8905 | 79.0593 | 0.1 | 0.7523 | Gillingham Common Mead Lane STW | Gillingham Common Mead Lane STW | 12 | 0.028846 | 57518.251 | 0.77183 | 71.27 | 72.79 | 72.79 | - | 80 | 0.77183 | 73.5618 | 2.2918 | 1.52
15157 | Winterbourne Hicks Common Road SPS | 75 | 0.11574 | 3.3134 | - | 3.3134 | 12.5065 | 0.075 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 12 | 0.028846 | 43138.6883 | 0.17857 | 66.93 | 67.24 | 67.24 | 12 | 12 | 0.17857 | 67.4186 | 0.48857 | 0.31
17775 | Idmiston Hale Barn Court SPS | 100 | 0.11574 | 5.8905 | - | 5.8905 | 12.7425 | 0.1 | 0.7523 | Hurdcott . STW | Idmiston . SPS | 12 | 0.028846 | 57518.251 | 0.1244 | 66.5 | 66.3 | 66.5 | 0 | 12 | 0.1244 | 66.6244 | 0.1244 | 0
14343 | Great Wishford Cobbs Mill SPS | 100 | 0.11574 | 5.8905 | - | 5.8905 | 131.106 | 0.1 | 0.7523 | Wishford Wilton Road STW | Stoford . SPS | 12 | 0.028846 | 57518.251 | 1.28 | 58.36 | 62.19 | 62.19 | 130 | 130 | 1.28 | 63.47 | 5.11 | 3.83
17353 | Rode The Old Brewery SPS | 100 | 0.11574 | 5.8905 | - | 5.8905 | 30.9005 | 0.1 | 0.7523 | Rode . STW | Rode . STW | 12 | 0.028846 | 57518.251 | 0.30167 | 54.7 | 55.76 | 55.76 | 30 | 30 | 0.30167 | 56.0617 | 1.3617 | 1.06
19641 | Mudford Sock Council Houses Septic Tank SPS | 100 | 0.11574 | 5.8905 | - | 5.8905 | 261.917 | 0.1 | 0.7523 | Yeovil Without Off Stone Lane STW | Yeovil Mudford SPS | 12 | 0.028846 | 57518.251 | 2.557 | 46.84 | 49.77 | 51.1 | 176 | 262 | 2.557 | 53.657 | 6.817 | 4.26
14504 | Laverstock Milford Manor Gardens SPS | 150 | 0.11574 | 13.2536 | - | 13.2536 | 68.3643 | 0.15 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 12 | 0.028846 | 86277.3765 | 0.39328 | 46.09 | 45.45 | 46.37 | 12 | 68 | 0.39328 | 46.7633 | 0.67328 | 0.28
15451 | Bradford On Tone Three Bridges SPS | 75 | 0.11574 | 3.3134 | - | 3.3134 | 531.7523 | 0.075 | 0.7523 | Bradford On Tone . STW | Bradford On Tone . STW | 12 | 0.028846 | 43138.6883 | 7.5926 | 38.01 | 44.75 | 45.13 | 476 | 532 | 7.5926 | 52.7226 | 14.7126 | 7.12
14334 | Downton Avon Dyke SPS | 75 | 0.11574 | 3.3134 | - | 3.3134 | 74.663 | 0.075 | 0.7523 | Downton Moot Lane STW | Downton Moot Close/ Moot Gardens SPS | 12 | 0.028846 | 43138.6883 | 1.0661 | 36.21 | 40.03 | 40.03 | 74 | 74 | 1.0661 | 41.0961 | 4.8861 | 3.82
14579 | Corfe Mullen Mill Farm SPS | 110 | 0.11574 | 7.1275 | - | 7.1275 | 343.8896 | 0.11 | 0.7523 | Corfe Mullen Dorchester Road STW | Corfe Mullen Admiralty Source SPS | 12 | 0.028846 | 63270.0761 | 2.9627 | 22.11 | 23.2 | 23.29 | - | 344 | 2.9627 | 26.2527 | 4.1427 | 1.18
19836 | Bridgwater Meads Court SPS | - | 0.11574 | - | - | - | 92.227 | - | - | Chilton Trinity . STW | Bridgwater Taunton Road SPS | 12 | - | - | - | 9.47 | 14.04 | 14.04 | 92 | 92 | - | - | - | 4.57
19271 | Mark Grange Paddock SPS | 110 | 0.11574 | 7.1275 | - | 7.1275 | 178.5637 | 0.11 | 0.7523 | West Huntspill STW | Mark Queensway SPS | 12 | 0.028846 | 63270.0761 | 1.5384 | 6.23 | 8.18 | 8.18 | 178 | 178 | 1.5384 | 9.7184 | 3.4884 | 1.95
12694 | Hawkeridge Mill Lane SPS | 160 | 0.11574 | 15.0796 | - | 15.0796 | 1285.6965 | 0.16 | 0.7523 | Westbury STW | Westbury STW | 12 | 0.028846 | 92029.2016 | 6.8038 | - | - | - | - | - | 6.8038 | - | - | -
12458 | Wimborne Merley Gardens Foul SPS | 90 | 0.11574 | 4.7713 | - | 4.7713 | 71.5423 | 0.09 | 0.7523 | Wimborne Brook Road STW | Canford Magna Canford Main SPS | 12 | 0.028846 | 51766.4259 | 0.80239 | - | - | - | - | - | 0.80239 | - | - | -
11917 | Poole Faith Gardens SPS | 80 | 0.11574 | 3.7699 | - | 3.7699 | 13.5973 | 0.08 | 0.7523 | Poole Cabot Lane STW | Poole Recreation Road SPS | 12 | 0.028846 | 46014.6008 | 0.17821 | - | - | - | - | - | 0.17821 | - | - | -
14111 | Oakhill Ashwick Grove SPS | 75 | 0.092592 | 3.3134 | - | 3.3134 | 278.4182 | 0.075 | 0.7523 | Oakhill . STW | Oakhill . STW | 10 | 0.028846 | 43138.6883 | 3.9754 | 182.35 | 203.82 | 203.9 | - | 278 | 3.9754 | 207.8754 | 25.5254 | 21.55
14052 | Stanton St Bernard Canal Cottages SPS | 75 | 0.092592 | 3.3134 | - | 3.3134 | 218.6481 | 0.075 | 0.7523 | Stanton St Bernard . STW | Stanton St Bernard Church Farm SPS | 10 | 0.028846 | 43138.6883 | 3.1219 | 133.48 | 135.19 | 138.69 | 158 | 218 | 3.1219 | 141.8119 | 8.3319 | 5.21
10775 | Devizes Victoria Road Private SPS | 90 | 0.092592 | 4.7713 | - | 4.7713 | 15.5302 | 0.09 | 0.7523 | Devizes Webbs Lane STW | Devizes Webbs Lane STW | 10 | 0.028846 | 51766.4259 | 0.17418 | 130.5 | 130.62 | 130.62 | 16 | 16 | 0.17418 | 130.7942 | 0.29418 | 0.12
14636 | Lyneham Building 383 (C Site Ps 2) SPS | 225 | 0.092592 | 29.8206 | - | 29.8206 | 118.1466 | 0.225 | 0.7523 | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham B Site (Main Stw) Raf Lyneham STW | 10 | 0.028846 | 129416.0648 | 0.40341 | 126.27 | 126.45 | 126.59 | 112 | 118 | 0.40341 | 126.9934 | 0.72341 | 0.32
15508 | Wootton Courtenay . SPS | 75 | 0.092592 | 3.3134 | 0.7 | 0.7 | 67.5556 | 0.075 | 0.15893 | Minehead Headworks STW | Minehead Headworks STW | 10 | 0.0012874 | 9113.6281 | 0.04898 | 118.88 | 118.52 | 119.06 | - | 68 | 0.04898 | 119.109 | 0.22898 | 0.18
15291 | Odcombe No 2 SPS | 32 | 0.092592 | 0.60319 | - | 0.60319 | 90.3105 | 0.032 | 0.7523 | Yeovil Sherborne Road (Pen Mill) STW | Odcombe No 1 SPS | 10 | 0.028846 | 18405.8403 | 4.0888 | 101.59 | 108.77 | 108.77 | 90 | 90 | 4.0888 | 112.8588 | 11.2688 | 7.18
15623 | Leigh Dewlands Orchard SPS | 100 | 0.092592 | 5.8905 | - | 5.8905 | 57.2064 | 0.1 | 0.7523 | Thornford Bridge Halt STW | Leigh Frampton Farm SPS | 10 | 0.028846 | 57518.251 | 0.55849 | 77.48 | 80 | 80 | - | 58 | 0.55849 | 80.5585 | 3.0785 | 2.52
14297 | Chard Beechings Close SPS | 90 | 0.092592 | 4.7713 | - | 4.7713 | 15.2294 | 0.09 | 0.7523 | Chard Peasmarsh STW | Chard Peasmarsh STW | 10 | 0.028846 | 51766.4259 | 0.17081 | 75.88 | 75.86 | 75.94 | 12 | 16 | 0.17081 | 76.1108 | 0.23081 | 0.06
19254 | Poulshot Sillington Lane SPS | 100 | 0.092592 | 5.8905 | - | 5.8905 | 59.1237 | 0.1 | 0.7523 | Potterne . STW | Poulshot Townsend SPS | 10 | 0.028846 | 57518.251 | 0.57721 | 67.19 | 67.44 | 67.5 | 52 | 60 | 0.57721 | 68.0772 | 0.88721 | 0.31
15559 | Portland Pennsylvania Road SPS | 100 | 0.092592 | 5.8905 | 5 | 5 | 86.5945 | 0.1 | 0.63857 | Weymouth . STW | Portland Southwell SPS | 10 | 0.020783 | 48823.0078 | 0.61384 | 58.51 | 65.65 | 65.65 | 86 | 86 | 0.61384 | 66.2638 | 7.7538 | 7.14
19615 | North Curry Backham Cottages SPS | 90 | 0.092592 | 4.7713 | - | 4.7713 | 170.121 | 0.09 | 0.7523 | Stoke St Gregory . STW | North Curry Stoke Road SPS | 10 | 0.028846 | 51766.4259 | 1.908 | 52.55 | 56.24 | 56.26 | 162 | 170 | 1.908 | 58.168 | 5.618 | 3.71
19652 | Beercrocombe Broadbridge Road SPS | - | 0.092592 | - | - | - | 257.1458 | - | - | Fivehead . STW | Beercrocombe . SPS | 10 | - | - | - | 30.39 | 34.27 | 34.68 | 242 | 258 | - | - | - | 4.29
17044 | Bridport St Andrews Trading Estate SPS | 100 | 0.092592 | 5.8905 | - | 5.8905 | 117.1075 | 0.1 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 10 | 0.028846 | 57518.251 | 1.1433 | 13.66 | 16.25 | 16.25 | 118 | 118 | 1.1433 | 17.3933 | 3.7333 | 2.59
14123 | Charmouth Catherstone SPS | 100 | 0.092592 | 5.8905 | - | 5.8905 | 18.1926 | 0.1 | 0.7523 | Charmouth Headworks/Sea Outfall STW | Charmouth Headworks/Sea Outfall STW | 10 | 0.028846 | 57518.251 | 0.17761 | 7.99 | 9.17 | 9.17 | 20 | 20 | 0.17761 | 9.3476 | 1.3576 | 1.18
12283 | Berrow No 3 Manor Drive S105a SPS | - | 0.092592 | - | - | - | 83.9525 | - | - | West Huntspill STW | Berrow Meade Farm Coast Road SPS | 10 | - | - | - | 7.58 | 7.1 | 7.58 | 0 | 84 | - | - | - | 0
15610 | Kenn Moorside SPS | 75 | 0.092592 | 3.3134 | - | 3.3134 | 246.4956 | 0.075 | 0.7523 | Kingston Seymour Back Lane STW | Kingston Seymour Back Lane STW | 10 | 0.028846 | 43138.6883 | 3.5196 | 5.14 | 6.06 | 6.06 | 246 | 246 | 3.5196 | 9.5796 | 4.4396 | 0.92
15004 | Hengistbury Head Double Dykes SPS | 75 | 0.092592 | 3.3134 | - | 3.3134 | 606.3355 | 0.075 | 0.7523 | Holdenhurst Riverside Avenue STW | Southbourne Hengistbury Head SPS | 10 | 0.028846 | 43138.6883 | 8.6575 | 3.13 | 6.36 | 6.36 | 606 | 606 | 8.6575 | 15.0175 | 11.8875 | 3.23
17252 | Christchurch Wick Ferry SPS | 450 | 0.092592 | 119.2823 | - | 119.2823 | 172.1316 | 0.45 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Quomps No 2 SPS | 10 | 0.028846 | 258832.1296 | 0.24447 | - | 2.2 | 2.27 | 118 | 120 | 0.24447 | 2.5145 | - | -
10387 | Haselbury Plucknett Heathfield Row SPS | - | 0.092592 | - | - | - | 54.8966 | - | - | Haselbury Plucknett New Lane STW | Haselbury Plucknett New Lane STW | 10 | - | - | - | - | - | - | - | - | - | - | - | -
17477 | Wotton-Under-Edge Brookside SPS | - | 0.092592 | - | - | - | 0 | - | - | Wotton-Under-Edge Kingswood STW | Wotton-Under-Edge Kingswood STW | 10 | - | - | - | - | - | - | - | - | - | - | - | -
14637 | Lyneham Building 212 (D Site Ps 3) SPS | 125 | 0.069444 | 9.2039 | - | 9.2039 | 1179.4482 | 0.125 | 0.7523 | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham Building 383 (C Site Ps 2) SPS | 8 | 0.028846 | 71897.8138 | 8.5985 | 130.62 | 146.16 | 146.2 | - | 1180 | 8.5985 | 154.7985 | 24.1785 | 15.58
17202 | Temple Cloud Prospect House SPS | 100 | 0.069444 | 5.8905 | - | 5.8905 | 111.0688 | 0.1 | 0.7523 | Paulton . STW | Temple Cloud Temple Bridge SPS | 8 | 0.028846 | 57518.251 | 1.0843 | 127.01 | 129.06 | 129.06 | 112 | 112 | 1.0843 | 130.1443 | 3.1343 | 2.05
15816 | Winterbourne Dragon Road (Sandstone Rise) SPS | 100 | 0.069444 | 5.8905 | - | 5.8905 | 47.3435 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 8 | 0.028846 | 57518.251 | 0.4622 | 77.09 | 78.76 | 78.76 | 48 | 48 | 0.4622 | 79.2222 | 2.1322 | 1.67
14538 | Whitchurch The Witheys SPS | 50 | 0.069444 | 1.4726 | - | 1.4726 | 19.1103 | 0.05 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Dalby Ave SPS | 8 | 0.028846 | 28759.1255 | 0.46994 | 73.2 | 74.1 | 74.1 | 20 | 20 | 0.46994 | 74.5699 | 1.3699 | 0.9
15531 | Radstock Curtsons SPS | 80 | 0.069444 | 3.7699 | - | 3.7699 | 126.0865 | 0.08 | 0.7523 | Radstock Mill Lane STW | Radstock Mill Lane STW | 8 | 0.028846 | 46014.6008 | 1.6525 | 67.25 | 66.79 | 67.4 | 2 | 126 | 1.6525 | 69.0525 | 1.8025 | 0.15
15537 | Shoscombe Single Hill SPS | 100 | 0.069444 | 5.8905 | 2 | 2 | 15.4154 | 0.1 | 0.25543 | Shoscombe . STW | Shoscombe . STW | 8 | 0.0033254 | 19529.2031 | 0.018662 | 65.78 | 70.21 | 70.21 | 16 | 16 | 0.018662 | 70.2287 | 4.4487 | 4.43
15338 | Ash Ash School SPS | 75 | 0.069444 | 3.3134 | - | 3.3134 | 168.6659 | 0.075 | 0.7523 | Tintinhull Ash Bearley Lane STW | Tintinhull Ash Bearley Lane STW | 8 | 0.028846 | 43138.6883 | 2.4083 | 53.37 | 56.52 | 56.52 | 168 | 168 | 2.4083 | 58.9283 | 5.5583 | 3.15
15472 | Sherborne Lenthay Road SPS | 80 | 0.069444 | 3.7699 | - | 3.7699 | 95.9178 | 0.08 | 0.7523 | Sherborne West Mill Lane STW | Sherborne West Mill Lane STW | 8 | 0.028846 | 46014.6008 | 1.2571 | 51.5 | 54.05 | 54.05 | - | 96 | 1.2571 | 55.3071 | 3.8071 | 2.55
15807 | Wool Chalke Pit Lane SPS | - | 0.069444 | - | - | - | 86.7355 | - | - | Wool . STW | Wool . STW | 8 | - | - | - | 27.44 | 29.44 | 29.51 | 78 | 86 | - | - | - | 2.07
17982 | Monkton Combe Mill SPS | 90 | 0.069444 | 4.7713 | - | 4.7713 | 91.3801 | 0.09 | 0.7523 | Saltford Mead Lane STW | Monkton Combe Mill Lane SPS | 8 | 0.028846 | 51766.4259 | 1.0249 | 26.96 | 35.06 | 35.06 | 88 | 88 | 1.0249 | 36.0849 | 9.1249 | 8.1
14240 | Bovington Morris Road SPS | 100 | 0.069444 | 5.8905 | 2 | 2 | 293.4823 | 0.1 | 0.25543 | Wool . STW | Bovington Terminal SPS | 8 | 0.0033254 | 19529.2031 | 0.35528 | 25.65 | 32.74 | 32.74 | 294 | 294 | 0.35528 | 33.0953 | 7.4453 | 7.09
15061 | Shapwick Shapwick East SPS | 100 | 0.069444 | 5.8905 | - | 5.8905 | 106.4893 | 0.1 | 0.7523 | Tarrant Crawford . STW | Shapwick Stewards Lane SPS | 8 | 0.028846 | 57518.251 | 1.0396 | 25.33 | 25.03 | 25.33 | 0 | 106 | 1.0396 | 26.3696 | 1.0396 | 0
15861 | Keynsham The Brassmills Avon Mill Lane SPS | 100 | 0.069444 | 5.8905 | - | 5.8905 | 135.9401 | 0.1 | 0.7523 | Keynsham . STW | Keynsham Keynsham High Level SPS | 8 | 0.028846 | 57518.251 | 1.3271 | 12.68 | 19.73 | 19.73 | 136 | 136 | 1.3271 | 21.0571 | 8.3771 | 7.05
14519 | Somerton Barpool Lane SPS | 100 | 0.069444 | 5.8905 | - | 5.8905 | 1167.6293 | 0.1 | 0.7523 | Somerton Barpool Lane STW | Somerton Barpool Lane STW | 8 | 0.028846 | 57518.251 | 11.3992 | 9.28 | 21.03 | 21.03 | 1168 | 1168 | 11.3992 | 32.4292 | 23.1492 | 11.75
19698 | Bridgwater Ucb SPS | 100 | 0.069444 | 5.8905 | - | 5.8905 | 413.544 | 0.1 | 0.7523 | Chilton Trinity . STW | Bridgwater Bristol Road SPS | 8 | 0.028846 | 57518.251 | 4.0373 | 6.38 | 6.18 | 6.61 | 86 | 414 | 4.0373 | 10.6473 | 4.2673 | 0.23
17140 | Bridgwater Express Park SPS | 225 | 0.069444 | 29.8206 | - | 29.8206 | 1719.9794 | 0.225 | 0.7523 | Chilton Trinity . STW | Bridgwater Bristol Road SPS | 8 | 0.028846 | 129416.0648 | 5.8728 | 6.2 | 7.94 | 9.18 | 504 | 1524 | 5.8728 | 15.0528 | 8.8528 | 2.98
14631 | Mark Northwick Road SPS | 100 | 0.069444 | 5.8905 | - | 5.8905 | 387.2071 | 0.1 | 0.7523 | West Huntspill STW | Mark . SPS | 8 | 0.028846 | 57518.251 | 3.7802 | 5.26 | 5.62 | 5.79 | - | 352 | 3.7802 | 9.5702 | 4.3102 | 0.53
19677 | Mudeford Sandbank No.3 SPS | 125 | 0.069444 | 9.2039 | - | 9.2039 | 524.2344 | 0.125 | 0.7523 | Christchurch Stoney Lane STW | Mudeford Mudeford Quay SPS | 8 | 0.028846 | 71897.8138 | 3.8218 | 2.11 | 1.65 | 3.47 | 388 | 524 | 3.8218 | 7.2918 | 5.1818 | 1.36
15232 | Poole Salterns Way SPS | 120 | 0.069444 | 8.4823 | - | 8.4823 | 135.2984 | 0.12 | 0.7523 | Poole Cabot Lane STW | Poole Shore Road SPS | 8 | 0.028846 | 69021.9012 | 1.0403 | 1.85 | 3.24 | 3.24 | 136 | 136 | 1.0403 | 4.2803 | 2.4303 | 1.39
15250 | Poole Blandford Road Mini Roundabout SPS | 100 | 0.069444 | 5.8905 | - | 5.8905 | 29.4127 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Turlin Main Blandford Road Turlin Moor SPS | 8 | 0.028846 | 57518.251 | 0.28715 | 1.79 | 1.6 | 1.86 | - | 30 | 0.28715 | 2.1471 | 0.35715 | 0.07
17185 | Shepton Mallet Showground SPS | 100 | 0.069444 | 5.8905 | - | 5.8905 | 1688.5963 | 0.1 | 0.7523 | Evercreech . STW | Evercreech . STW | 8 | 0.028846 | 57518.251 | 16.4853 | - | 71.86 | 82.79 | - | 1664 | 16.4853 | 99.2753 | - | -
15642 | Poole Sterte F W Private SPS | 400 | 0.069444 | 94.2478 | - | 94.2478 | 2158.773 | 0.4 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 8 | 0.028846 | 230073.0041 | 3.5546 | - | - | - | - | - | 3.5546 | - | - | -
10271 | Swanage Bon Accord Road Private SPS | - | 0.069444 | - | - | - | 79.126 | - | - | Swanage Marine Parade STW | Swanage Marine Parade STW | 8 | - | - | - | - | - | - | - | - | - | - | - | -
12554 | Yeovil Cabot Road SPS | - | 0.069444 | - | - | - | 192.5088 | - | - | Yeovil Sherborne Road (Pen Mill) STW | Yeovil Sherborne Road (Pen Mill) STW | 8 | - | - | - | - | - | - | - | - | - | - | - | -
19299 | Coleford Church Lane SPS | 80 | 0.046296 | 3.7699 | - | 3.7699 | 38.1558 | 0.08 | 0.7523 | Coleford . STW | Coleford . STW | 5 | 0.028846 | 46014.6008 | 0.50007 | 135.35 | 142.1 | 142.1 | 38 | 38 | 0.50007 | 142.6001 | 7.2501 | 6.75
19635 | Cucklington Vale View SPS | 110 | 0.046296 | 7.1275 | - | 7.1275 | 321.2574 | 0.11 | 0.7523 | Cucklington Babwell Road Bioplant STW | Cucklington Babwell Road Bioplant STW | 5 | 0.028846 | 63270.0761 | 2.7677 | 85.26 | 110.25 | 110.27 | 320 | 324 | 2.7677 | 113.0377 | 27.7777 | 25.01
15143 | Patchway Highwood Trading Estate West SPS | 100 | 0.046296 | 5.8905 | - | 5.8905 | 62.3847 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Avonmouth Kingsweston Lane STW | 5 | 0.028846 | 57518.251 | 0.60904 | 81.44 | 81.41 | 81.44 | - | 62 | 0.60904 | 82.049 | 0.60904 | 0
15137 | Patchway Highwood Trading Estate East SPS | 125 | 0.046296 | 9.2039 | - | 9.2039 | 151.2192 | 0.125 | 0.7523 | Avonmouth Kingsweston Lane STW | Patchway Highwood Trading Estate West SPS | 5 | 0.028846 | 71897.8138 | 1.1024 | 81.34 | 81.44 | 81.46 | - | 152 | 1.1024 | 82.5624 | 1.2224 | 0.12
10438 | Salisbury Castlegate Business Park SPS | 150 | 0.046296 | 13.2536 | - | 13.2536 | 979.4509 | 0.15 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Old Sarum Airfield (Partridge Way) SPS | 5 | 0.028846 | 86277.3765 | 5.6345 | 78.09 | 75 | 81.76 | 328 | 980 | 5.6345 | 87.3945 | 9.3045 | 3.67
15305 | Yeovil Primrose Lane SPS | 80 | 0.046296 | 3.7699 | - | 3.7699 | 32.3981 | 0.08 | 0.7523 | Yeovil Without Off Stone Lane STW | Yeovil Without Off Stone Lane STW | 5 | 0.028846 | 46014.6008 | 0.42461 | 71.01 | 72.81 | 72.81 | 32 | 32 | 0.42461 | 73.2346 | 2.2246 | 1.8
19287 | Blandford St Mary Stour Park SPS | 100 | 0.046296 | 5.8905 | - | 5.8905 | 240.358 | 0.1 | 0.7523 | Tarrant Crawford . STW | Spetisbury No 3 SPS | 5 | 0.028846 | 57518.251 | 2.3465 | 33.39 | 40.54 | 40.54 | 240 | 240 | 2.3465 | 42.8865 | 9.4965 | 7.15
15049 | Wimborne Brook Road No 3 SPS | 100 | 0.046296 | 5.8905 | - | 5.8905 | 147.4283 | 0.1 | 0.7523 | Wimborne Brook Road STW | Wimborne Brook Road STW | 5 | 0.028846 | 57518.251 | 1.4393 | 17.37 | 17.22 | 17.43 | 142 | 148 | 1.4393 | 18.8693 | 1.4993 | 0.06
15597 | Portishead Golf Course SPS | 75 | 0.046296 | 3.3134 | - | 3.3134 | 172.3533 | 0.075 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Town Harbour Road SPS | 5 | 0.028846 | 43138.6883 | 2.4609 | 16.7 | 41.85 | 41.85 | 172 | 172 | 2.4609 | 44.3109 | 27.6109 | 25.15
15543 | Keynsham Bath Hill Chew Park SPS | 75 | 0.046296 | 3.3134 | - | 3.3134 | 5.3853 | 0.075 | 0.7523 | Keynsham . STW | Keynsham Keynsham High Level SPS | 5 | 0.028846 | 43138.6883 | 0.076893 | 13.68 | 14.96 | 14.96 | 6 | 6 | 0.076893 | 15.0369 | 1.3569 | 1.28
17060 | Easter Compton Firwood House SPS | 63 | 0.046296 | 2.3379 | - | 2.3379 | 77.7519 | 0.063 | 0.7523 | Avonmouth Kingsweston Lane STW | Easter Compton Pilning Road SPS | 5 | 0.028846 | 36236.4981 | 1.4009 | 6.74 | 6.57 | 6.79 | 2 | 78 | 1.4009 | 8.1909 | 1.4509 | 0.05
12246 | Burnham-On-Sea Shelley Close S105a SPS | - | 0.046296 | - | - | - | 19.0133 | - | - | West Huntspill STW | Burnham-On-Sea Rectory Drive SPS | 5 | - | - | - | 6.24 | 6.52 | 6.52 | - | 20 | - | - | - | 0.28
17620 | Minehead Queens Hall SPS | 100 | 0.046296 | 5.8905 | - | 5.8905 | 49.5822 | 0.1 | 0.7523 | Minehead Headworks STW | Minehead Mart Road SPS | 5 | 0.028846 | 57518.251 | 0.48406 | 5.75 | 7.55 | 7.55 | 50 | 50 | 0.48406 | 8.0341 | 2.2841 | 1.8
15675 | Bridport Wanderwell SPS | 100 | 0.046296 | 5.8905 | - | 5.8905 | 51.4668 | 0.1 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 5 | 0.028846 | 57518.251 | 0.50246 | 4.72 | 4.98 | 4.98 | 52 | 52 | 0.50246 | 5.4825 | 0.76246 | 0.26
15009 | Bournemouth Alum Chine SPS | 76 | 0.046296 | 3.4023 | - | 3.4023 | 139.634 | 0.076 | 0.7523 | Holdenhurst Riverside Avenue STW | Bournemouth No 1 SPS | 5 | 0.028846 | 43713.8708 | 1.959 | 2.96 | 6.42 | 6.42 | 140 | 140 | 1.959 | 8.379 | 5.419 | 3.46
14006 | Bath Bucklands Lodge SPS | 100 | 0.023148 | 5.8905 | - | 5.8905 | 20.9501 | 0.1 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 3 | 0.028846 | 57518.251 | 0.20453 | 189.38 | 192.82 | 192.82 | 20 | 20 | 0.20453 | 193.0245 | 3.6445 | 3.44
14332 | Wylye Corn Mill SPS | 80 | 0.023148 | 3.7699 | - | 3.7699 | 43.0375 | 0.08 | 0.7523 | Wishford Wilton Road STW | Wylye Chequers Cottages SPS | 3 | 0.028846 | 46014.6008 | 0.56405 | 72.3 | 73.14 | 73.51 | 18 | 28 | 0.56405 | 74.0741 | 1.7741 | 1.21
15640 | Dorchester South Station SPS | 80 | 0.023148 | 3.7699 | - | 3.7699 | 84.7827 | 0.08 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Dorchester Louds Mill St Georges Road STW | 3 | 0.028846 | 46014.6008 | 1.1112 | 69.92 | 71.41 | 71.48 | 74 | 84 | 1.1112 | 72.5912 | 2.6712 | 1.56
17269 | Wincanton Sports Ground SPS | 100 | 0.023148 | 5.8905 | - | 5.8905 | 896.0082 | 0.1 | 0.7523 | Wincanton . STW | Wincanton . STW | 3 | 0.028846 | 57518.251 | 8.7475 | 69.57 | 70.92 | 70.92 | 896 | 896 | 8.7475 | 79.6675 | 10.0975 | 1.35
17359 | Ansford Wayside Farm SPS | 110 | 0.023148 | 7.1275 | - | 7.1275 | 43.9802 | 0.11 | 0.7523 | Castle Cary Near Dimmer STW | Castle Cary Near Dimmer STW | 3 | 0.028846 | 63270.0761 | 0.37891 | 55.78 | 58.36 | 58.36 | 44 | 44 | 0.37891 | 58.7389 | 2.9589 | 2.58
15202 | Shroton The Glebe SPS | 75 | 0.023148 | 3.3134 | - | 3.3134 | 7.8017 | 0.075 | 0.7523 | Shroton . STW | Shroton . SPS | 3 | 0.028846 | 43138.6883 | 0.1114 | 55.26 | 55.24 | 55.26 | - | 8 | 0.1114 | 55.3714 | 0.1114 | 0
14695 | Castle Cary Warehouse Torbay Road Private SPS | 75 | 0.023148 | 3.3134 | - | 3.3134 | 141.9045 | 0.075 | 0.7523 | Castle Cary Near Dimmer STW | Castle Cary Near Dimmer STW | 3 | 0.028846 | 43138.6883 | 2.0262 | 50.02 | 54.38 | 54.38 | 142 | 142 | 2.0262 | 56.4062 | 6.3862 | 4.36
15727 | Crewkerne Blacknell Lane SPS | 100 | 0.023148 | 5.8905 | - | 5.8905 | 54.1595 | 0.1 | 0.7523 | Crewkerne Trading Estate Crewkerne East STW | Crewkerne Trading Estate Crewkerne East STW | 3 | 0.028846 | 57518.251 | 0.52874 | 49.78 | 50.9 | 50.9 | 54 | 54 | 0.52874 | 51.4287 | 1.6487 | 1.12
17488 | Castle Cary Crown Pet Foods SPS | 125 | 0.023148 | 9.2039 | - | 9.2039 | 504.5862 | 0.125 | 0.7523 | Castle Cary Near Dimmer STW | Castle Cary Near Dimmer STW | 3 | 0.028846 | 71897.8138 | 3.6786 | 44.52 | 54.94 | 54.94 | 504 | 504 | 3.6786 | 58.6186 | 14.0986 | 10.42
14278 | Bere Regis Rye Hill Close SPS | 100 | 0.023148 | 5.8905 | - | 5.8905 | 62.8274 | 0.1 | 0.7523 | Blackheath . STW | Bere Regis Court Farm Southbrook SPS | 3 | 0.028846 | 57518.251 | 0.61337 | 33.36 | 33.82 | 34.11 | 60 | 62 | 0.61337 | 34.7234 | 1.3634 | 0.75
15525 | Bathampton Mill Lane (Beafeater) SPS | 75 | 0.023148 | 3.3134 | - | 3.3134 | 93.7757 | 0.075 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 3 | 0.028846 | 43138.6883 | 1.339 | 20.09 | 24.69 | 24.69 | 94 | 94 | 1.339 | 26.029 | 5.939 | 4.6
15452 | Taunton Tangier SPS | 75 | 0.023148 | 3.3134 | - | 3.3134 | 3.4919 | 0.075 | 0.7523 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 3 | 0.028846 | 43138.6883 | 0.049859 | 16.21 | 16.28 | 16.28 | 4 | 4 | 0.049859 | 16.3299 | 0.11986 | 0.07
15005 | Southbourne Bedford Beach SPS | 100 | 0.023148 | 5.8905 | - | 5.8905 | 41.508 | 0.1 | 0.7523 | Holdenhurst Riverside Avenue STW | Southbourne Hengistbury Head SPS | 3 | 0.028846 | 57518.251 | 0.40523 | 5.43 | 16.67 | 16.67 | 42 | 42 | 0.40523 | 17.0752 | 11.6452 | 11.24
15016 | Southbourne Amenities SPS | 75 | 0.023148 | 3.3134 | - | 3.3134 | 56.8618 | 0.075 | 0.7523 | Holdenhurst Riverside Avenue STW | Southbourne Bedford Beach SPS | 3 | 0.028846 | 43138.6883 | 0.8119 | 4.14 | 5.68 | 5.88 | 54 | 56 | 0.8119 | 6.6919 | 2.5519 | 1.74
14282 | Studland Hardy Road SPS | 100 | 0.023148 | 5.8905 | - | 5.8905 | 474.1508 | 0.1 | 0.7523 | Studland Ferry Road STW | Studland Wadmore Lane SPS | 3 | 0.028846 | 57518.251 | 4.629 | 3.43 | 19.26 | 19.26 | 474 | 474 | 4.629 | 23.889 | 20.459 | 15.83
17253 | Portland Sailing Academy SPS | 80 | 0.023148 | 3.7699 | - | 3.7699 | 114.9759 | 0.08 | 0.7523 | Weymouth . STW | Portland Osprey Quay SPS | 3 | 0.028846 | 46014.6008 | 1.5069 | 3.18 | 3.75 | 3.79 | 112 | 114 | 1.5069 | 5.2969 | 2.1169 | 0.61
17564 | Poole Marshes End SPS | 125 | 0.023148 | 9.2039 | - | 9.2039 | 302.5977 | 0.125 | 0.7523 | Poole Cabot Lane STW | Poole Kennart Road SPS | 3 | 0.028846 | 71897.8138 | 2.206 | 2.86 | 2.8 | 2.88 | 2 | 300 | 2.206 | 5.086 | 2.226 | 0.02
15238 | Poole Hatch Pond Road SPS | 150 | 0.023148 | 13.2536 | - | 13.2536 | 156.8363 | 0.15 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane SPS | 3 | 0.028846 | 86277.3765 | 0.90223 | 2.78 | 5.76 | 5.97 | 142 | 156 | 0.90223 | 6.8722 | 4.0922 | 3.19
17769 | Highbridge Marconi Drive SPS | - | 0.023148 | - | - | - | 343.3189 | - | - | West Huntspill STW | Highbridge Newton SPS | 3 | - | - | - | - | - | - | - | - | - | - | - | -
14004 | Bath Van Diemens Lane SPS | 100 | 0 | 5.8905 | - | 5.8905 | 98.271 | 0.1 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 0 | 0.028846 | 57518.251 | 0.95939 | 182.39 | 185.74 | 185.74 | - | 98 | 0.95939 | 186.6994 | 4.3094 | 3.35
14008 | Bath Stonehouse Close SPS | 75 | 0 | 3.3134 | - | 3.3134 | 55.784 | 0.075 | 0.7523 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 0 | 0.028846 | 43138.6883 | 0.79651 | 161.87 | 163.06 | 163.06 | 56 | 56 | 0.79651 | 163.8565 | 1.9865 | 1.19
14638 | Lyneham Crash Bay (D Site Ps 4) SPS | - | 0 | - | - | - | 175.6141 | - | - | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham Building 212 (D Site Ps 3) SPS | 0 | - | - | - | 143.95 | 143.91 | 144.16 | 74 | 176 | - | - | - | 0.21
14635 | Lyneham A Site (Ps 1) SPS | 100 | 0 | 5.8905 | - | 5.8905 | 582.3717 | 0.1 | 0.7523 | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham Technical Site Dry Well (Ps 5) SPS | 0 | 0.028846 | 57518.251 | 5.6855 | 134.04 | 132.8 | 134.63 | 400 | 582 | 5.6855 | 140.3155 | 6.2755 | 0.59
14639 | Lyneham Technical Site Dry Well (Ps 5) SPS | 120 | 0 | 8.4823 | - | 8.4823 | 425.6664 | 0.12 | 0.7523 | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham B Site (Main Stw) Raf Lyneham STW | 0 | 0.028846 | 69021.9012 | 3.273 | 132.8 | 137.11 | 137.15 | - | 426 | 3.273 | 140.423 | 7.623 | 4.35
14644 | Lyneham Halifax Block (Ps 13) SPS | 75 | 0 | 3.3134 | - | 3.3134 | 17.8883 | 0.075 | 0.7523 | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham B Site (Main Stw) Raf Lyneham STW | 0 | 0.028846 | 43138.6883 | 0.25542 | 131.17 | 130.77 | 131.2 | 2 | 18 | 0.25542 | 131.4554 | 0.28542 | 0.03
14645 | Lyneham Building 380 (C Site Ps 14) SPS | 100 | 0 | 5.8905 | - | 5.8905 | 48.2625 | 0.1 | 0.7523 | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham Building 383 (C Site Ps 2) SPS | 0 | 0.028846 | 57518.251 | 0.47117 | 130.56 | 130.66 | 130.69 | 46 | 48 | 0.47117 | 131.1612 | 0.60117 | 0.13
14641 | Lyneham Domestic Site (Ps 9) SPS | - | 0 | - | - | - | 114.2536 | - | - | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham B Site (Main Stw) Raf Lyneham STW | 0 | - | - | - | 129.77 | 131.22 | 131.39 | 84 | 114 | - | - | - | 1.62
15168 | Great Badminton Badminton House SPS | 100 | 0 | 5.8905 | - | 5.8905 | 1215.1194 | 0.1 | 0.7523 | Great Badminton . STW | Great Badminton . STW | 0 | 0.028846 | 57518.251 | 11.8629 | 118.82 | 113.35 | 118.84 | 2 | 1216 | 11.8629 | 130.7029 | 11.8829 | 0.02
14578 | Kington St Michael Kyneton Way SPS | 75 | 0 | 3.3134 | - | 3.3134 | 77.3539 | 0.075 | 0.7523 | Sutton Benger . STW | Kington Langley . SPS | 0 | 0.028846 | 43138.6883 | 1.1045 | 97.35 | 99.21 | 99.21 | 78 | 78 | 1.1045 | 100.3145 | 2.9645 | 1.86
19790 | Upton Scudamore Wtw Sps SPS | - | 0 | - | - | - | 75.5554 | - | - | Dilton Marsh . STW | Upton Scudamore . SPS | 0 | - | - | - | 95.39 | 108.72 | 108.72 | - | 76 | - | - | - | 13.33
14532 | Midsomer Norton Rackvernal Court SPS | 70 | 0 | 2.8863 | - | 2.8863 | 39.5131 | 0.07 | 0.7523 | Radstock Mill Lane STW | Radstock Mill Lane STW | 0 | 0.028846 | 40262.7757 | 0.61845 | 82.05 | 84.93 | 84.93 | 40 | 40 | 0.61845 | 85.5484 | 3.4984 | 2.88
15279 | Horsington Horsington School SPS | 100 | 0 | 5.8905 | - | 5.8905 | 78.1863 | 0.1 | 0.7523 | Wincanton . STW | North Cheriton Grove Lane SPS | 0 | 0.028846 | 57518.251 | 0.76331 | 79.27 | 80.7 | 80.7 | - | 78 | 0.76331 | 81.4633 | 2.1933 | 1.43
17268 | Kingswood Station Road Storm Tank SPS | 150 | 0 | 13.2536 | 30 | 30 | 39.5658 | 0.15 | 1.7029 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 0 | 0.14779 | 195292.0313 | 1.1363 | 68.37 | 70.48 | 70.48 | 40 | 40 | 1.1363 | 71.6163 | 3.2463 | 2.11
14015 | Bristol Bedminster Down SPS | 100 | 0 | 5.8905 | - | 5.8905 | 98.1462 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 0 | 0.028846 | 57518.251 | 0.95817 | 61.59 | 66.29 | 66.29 | 98 | 98 | 0.95817 | 67.2482 | 5.6582 | 4.7
15256 | Poole ¦ Laural Drive SPS | 100 | 0 | 5.8905 | - | 5.8905 | 95.734 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 0 | 0.028846 | 57518.251 | 0.93462 | 58.74 | 71.58 | 71.58 | 96 | 96 | 0.93462 | 72.5146 | 13.7746 | 12.84
14356 | Wilton Bulbridge (Burcombe Road) SPS | 100 | 0 | 5.8905 | - | 5.8905 | 83.14 | 0.1 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 0 | 0.028846 | 57518.251 | 0.81167 | 58.03 | 60.02 | 60.05 | 82 | 84 | 0.81167 | 60.8617 | 2.8317 | 2.02
14344 | Netherhampton Waldrons Farm SPS | 32 | 0 | 0.60319 | - | 0.60319 | 38.2045 | 0.032 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Netherhampton Flowerland SPS | 0 | 0.028846 | 18405.8403 | 1.7297 | 48.83 | 49.22 | 49.51 | 28 | 38 | 1.7297 | 51.2397 | 2.4097 | 0.68
14218 | Bovington A T D U SPS | 100 | 0 | 5.8905 | - | 5.8905 | 60.0166 | 0.1 | 0.7523 | Wool . STW | Bovington Rhine Road SPS | 0 | 0.028846 | 57518.251 | 0.58593 | 47.52 | 51.26 | 51.26 | 60 | 60 | 0.58593 | 51.8459 | 4.3259 | 3.74
14350 | Laverstock Whitebridge Road SPS | 150 | 0 | 13.2536 | - | 13.2536 | 173.2478 | 0.15 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 0 | 0.028846 | 86277.3765 | 0.99664 | 47.45 | 46.94 | 47.47 | 2 | 174 | 0.99664 | 48.4666 | 1.0166 | 0.02
15775 | Broadstone Bryony Close SPS | 100 | 0 | 5.8905 | - | 5.8905 | 12.7201 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 0 | 0.028846 | 57518.251 | 0.12418 | 45.48 | 45.58 | 45.64 | 4 | 12 | 0.12418 | 45.7642 | 0.28418 | 0.16
15182 | Thornbury Orchard Avenue SPS | 150 | 0 | 13.2536 | - | 13.2536 | 117.2604 | 0.15 | 0.7523 | Thornbury . STW | Thornbury . STW | 0 | 0.028846 | 86277.3765 | 0.67457 | 44.76 | 47.79 | 47.79 | - | 118 | 0.67457 | 48.4646 | 3.7046 | 3.03
15711 | Eype Picnic Site SPS | 50 | 0 | 1.4726 | - | 1.4726 | 222.9006 | 0.05 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 0 | 0.028846 | 28759.1255 | 5.4813 | 44.26 | 48.7 | 48.7 | 222 | 222 | 5.4813 | 54.1813 | 9.9213 | 4.44
14215 | Bovington East Wing SPS | 100 | 0 | 5.8905 | - | 5.8905 | 74.9463 | 0.1 | 0.7523 | Wool . STW | Bovington Rhine Road SPS | 0 | 0.028846 | 57518.251 | 0.73168 | 43.66 | 44.59 | 44.59 | 74 | 74 | 0.73168 | 45.3217 | 1.6617 | 0.93
17357 | Haselbury Plucknett Petvins Court SPS | 60 | 0 | 2.1206 | - | 2.1206 | 176.4967 | 0.06 | 0.7523 | Haselbury Plucknett New Lane STW | Haselbury Plucknett New Lane STW | 0 | 0.028846 | 34510.9506 | 3.3949 | 42.94 | 42.73 | 43.8 | 72 | 176 | 3.3949 | 47.1949 | 4.2549 | 0.86
14331 | Salisbury Longford Castle SPS | 100 | 0 | 5.8905 | - | 5.8905 | 664.0104 | 0.1 | 0.7523 | Salisbury Petersfinger -Southampton Road STW | Alderbury Home Farm SPS | 0 | 0.028846 | 57518.251 | 6.4825 | 40.99 | 41.64 | 42.27 | 130 | 664 | 6.4825 | 48.7525 | 7.7625 | 1.28
10736 | Bryanston ¦ Bryanston School SPS | 125 | 0 | 9.2039 | - | 9.2039 | 1197.1384 | 0.125 | 0.7523 | Tarrant Crawford . STW | Blandford St Mary Bournemouth Road SPS | 0 | 0.028846 | 71897.8138 | 8.7275 | 40.61 | 70.99 | 71.57 | 1096 | 1198 | 8.7275 | 80.2975 | 39.6875 | 30.96
19776 | Warmwell Bourne Leisure SPS | 160 | 0 | 15.0796 | - | 15.0796 | 505.4834 | 0.16 | 0.7523 | Dorchester Louds Mill St Georges Road STW | Warmwell Crossways Of B3390 SPS | 0 | 0.028846 | 92029.2016 | 2.675 | 37.79 | 52.46 | 56.77 | 464 | 496 | 2.675 | 59.445 | 21.655 | 18.98
15172 | Bristol Newlands SPS | 100 | 0 | 5.8905 | - | 5.8905 | 89.0768 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 0 | 0.028846 | 57518.251 | 0.86963 | 34.61 | 43.13 | 43.13 | 90 | 90 | 0.86963 | 43.9996 | 9.3896 | 8.52
15018 | Bournemouth West Overcliff SPS | 100 | 0 | 5.8905 | - | 5.8905 | 115.5457 | 0.1 | 0.7523 | Holdenhurst Riverside Avenue STW | Bournemouth No 1 SPS | 0 | 0.028846 | 57518.251 | 1.128 | 33.4 | 36.49 | 36.53 | 126 | 128 | 1.128 | 37.658 | 4.258 | 3.13
15011 | Bournemouth St Ives Gardens SPS | 75 | 0 | 3.3134 | - | 3.3134 | 101.2869 | 0.075 | 0.7523 | Holdenhurst Riverside Avenue STW | Hengistbury Head Double Dykes SPS | 0 | 0.028846 | 43138.6883 | 1.4462 | 30.48 | 37.91 | 37.91 | 102 | 102 | 1.4462 | 39.3562 | 8.8762 | 7.43
15790 | West Parley Dunedin Drive SPS | 100 | 0 | 5.8905 | - | 5.8905 | 11.5025 | 0.1 | 0.7523 | Kinson New Road Northbourne STW | Ferndown Golf Links Road SPS | 0 | 0.028846 | 57518.251 | 0.1123 | 29.22 | 29.03 | 29.26 | 4 | 12 | 0.1123 | 29.3723 | 0.1523 | 0.04
15259 | Poole Coy Pond SPS | 32 | 0 | 0.60319 | - | 0.60319 | 146.3909 | 0.032 | 0.7523 | Holdenhurst Riverside Avenue STW | Poole Wilderton Road SPS | 0 | 0.028846 | 18405.8403 | 6.6279 | 28.32 | 28.78 | 29.64 | 56 | 146 | 6.6279 | 36.2679 | 7.9479 | 1.32
15492 | Symondsbury Miles Cross SPS | 40 | 0 | 0.94248 | - | 0.94248 | 213.8544 | 0.04 | 0.7523 | Bridport Wych Farm STW | Symondsbury West Road Foundry SPS | 0 | 0.028846 | 23007.3004 | 7.1236 | 27.51 | 38.9 | 38.94 | 210 | 214 | 7.1236 | 46.0636 | 18.5536 | 11.43
14402 | Osmington Pontins SPS | 170 | 0 | 17.0235 | 11 | 11 | 369.3506 | 0.17 | 0.48611 | Weymouth . STW | Weymouth Preston Fisherbridge Estate SPS | 0 | 0.012044 | 63182.716 | 0.77156 | 26.41 | 52.38 | 52.38 | 370 | 370 | 0.77156 | 53.1516 | 26.7416 | 25.97
15448 | Taunton Longacre Close SPS | 75 | 0 | 3.3134 | 7 | 7 | 55.8689 | 0.075 | 1.5893 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 0 | 0.12874 | 91136.2813 | 3.4711 | 26.11 | 28.87 | 28.87 | 56 | 56 | 3.4711 | 32.3411 | 6.2311 | 2.76
19905 | Winfrith Newburgh Technology Centre 1 SPS | 170 | 0 | 17.0235 | - | 17.0235 | 570.4994 | 0.17 | 0.7523 | Wool . STW | Wool . STW | 0 | 0.028846 | 97781.0267 | 2.7917 | 23.8 | 24.33 | 24.33 | 570 | 570 | 2.7917 | 27.1217 | 3.3217 | 0.53
14234 | Bovington Stanley Barracks SPS | 100 | 0 | 5.8905 | - | 5.8905 | 94.9687 | 0.1 | 0.7523 | Wool . STW | Bovington Terminal SPS | 0 | 0.028846 | 57518.251 | 0.92715 | 21.55 | 24.67 | 24.67 | 94 | 94 | 0.92715 | 25.5972 | 4.0472 | 3.12
19526 | Bridgwater Vickery Close SPS | - | 0 | - | - | - | 0 | - | - | Chilton Trinity . STW | Bridgwater West Quay Drawbridge SPS | 0 | - | - | - | 20.62 | 25.39 | 25.49 | - | 214 | - | - | - | 4.87
15620 | Ringwood Brook Close SPS | 150 | 0 | 13.2536 | - | 13.2536 | 116.8284 | 0.15 | 0.7523 | Ringwood Hampshire Hatches Lane STW | Ringwood Bickerley SPS | 0 | 0.028846 | 86277.3765 | 0.67208 | 19.92 | 20.4 | 20.5 | 110 | 116 | 0.67208 | 21.1721 | 1.2521 | 0.58
16057 | Bath Technology House SPS | 250 | 0 | 36.8155 | 11 | 11 | 79.5096 | 0.25 | 0.22478 | Saltford Mead Lane STW | Bath Midland Road Twerton SPS | 0 | 0.0025752 | 42964.2469 | 0.022964 | 18.22 | 19.07 | 19.3 | 72 | 80 | 0.022964 | 19.323 | 1.103 | 1.08
17142 | Bath Windsor Villas Pumping Station SPS | 250 | 0 | 36.8155 | - | 36.8155 | 50.1094 | 0.25 | 0.7523 | Saltford Mead Lane STW | Saltford Mead Lane STW | 0 | 0.028846 | 143795.6275 | 0.14957 | 18.14 | 18.25 | 18.32 | 40 | 50 | 0.14957 | 18.4696 | 0.32957 | 0.18
17195 | Locking Pine Tree Road SPS | 125 | 0 | 9.2039 | - | 9.2039 | 46.043 | 0.125 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Weston-Super-Mare Accommodation Road Bleadon STW | 0 | 0.028846 | 71897.8138 | 0.33567 | 15.27 | 15.92 | 15.97 | 44 | 46 | 0.33567 | 16.3057 | 1.0357 | 0.7
15701 | Wembdon Keltings SPS | 80 | 0 | 3.7699 | - | 3.7699 | 89.5269 | 0.08 | 0.7523 | Chilton Trinity . STW | Wembdon Common SPS | 0 | 0.028846 | 46014.6008 | 1.1734 | 14.71 | 21.37 | 21.37 | 90 | 90 | 1.1734 | 22.5434 | 7.8334 | 6.66
15343 | Puriton Downend SPS | 75 | 0 | 3.3134 | - | 3.3134 | 102.2283 | 0.075 | 0.7523 | West Huntspill STW | Puriton Rye SPS | 0 | 0.028846 | 43138.6883 | 1.4597 | 14.35 | 12.35 | 15.1 | 18 | 102 | 1.4597 | 16.5597 | 2.2097 | 0.75
15690 | Taunton Holway Barton SPS | - | 0 | - | - | - | 2.858 | - | - | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 0 | - | - | - | 13.25 | 13.28 | 13.28 | 2 | 2 | - | - | - | 0.03
14601 | Taunton Blackbrook Business Park SPS | - | 0 | - | - | - | 3.8299 | - | - | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 0 | - | - | - | 12.99 | 12.69 | 12.99 | 0 | 4 | - | - | - | 0
17237 | Bridport St. Cecilia'S Gardens SPS | 50 | 0 | 1.4726 | - | 1.4726 | 189.3132 | 0.05 | 0.7523 | Bridport Wych Farm STW | Bridport West Bay SPS | 0 | 0.028846 | 28759.1255 | 4.6554 | 11.51 | 11.7 | 11.82 | 138 | 190 | 4.6554 | 16.4754 | 4.9654 | 0.31
19036 | Bristol Penny Well Road Semi Syphons SPS | 100 | 0 | 5.8905 | - | 5.8905 | 3.0122 | 0.1 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Ashton Avenue SPS | 0 | 0.028846 | 57518.251 | 0.029407 | 10.38 | 10.39 | 10.41 | 2 | 4 | 0.029407 | 10.4394 | 0.059407 | 0.03
17129 | Bristol Clanage Flood Relief Pstn SPS | 250 | 0 | 36.8155 | - | 36.8155 | 90.7043 | 0.25 | 0.7523 | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 0 | 0.028846 | 143795.6275 | 0.27074 | 7.84 | 9.22 | 9.22 | 90 | 90 | 0.27074 | 9.4907 | 1.6507 | 1.38
15595 | Weston-Super-Mare Anchor Head SPS | 100 | 0 | 5.8905 | - | 5.8905 | 25.854 | 0.1 | 0.7523 | Weston-Super-Mare Accommodation Road Bleadon STW | Weston-Super-Mare Accommodation Road Bleadon STW | 0 | 0.028846 | 57518.251 | 0.25241 | 7.67 | 7.42 | 7.68 | - | 26 | 0.25241 | 7.9324 | 0.26241 | 0.01
15598 | Portishead Old Mill Lane SPS | 75 | 0 | 3.3134 | - | 3.3134 | 34.6325 | 0.075 | 0.7523 | Portbury Wharf The Drove Portbury STW | Portishead Poacher Hotel (Anchor Hotel) SPS | 0 | 0.028846 | 43138.6883 | 0.4945 | 7.18 | 7.6 | 7.81 | 4 | 34 | 0.4945 | 8.3045 | 1.1245 | 0.63
10594 | Berrow No 3 Manor Close SPS | - | 0 | - | - | - | 50.4834 | - | - | West Huntspill STW | Berrow Meade Farm Coast Road SPS | 0 | - | - | - | 6.82 | 6.96 | 7.19 | 12 | 50 | - | - | - | 0.37
12282 | Berrow No 4 Manor Close SPS | - | 0 | - | - | - | 40.9738 | - | - | West Huntspill STW | Berrow Meade Farm Coast Road SPS | 0 | - | - | - | 6.73 | 7.08 | 7.19 | 28 | 40 | - | - | - | 0.46
15801 | Poole Albany Park SPS | 200 | 0 | 23.5619 | - | 23.5619 | 157.3097 | 0.2 | 0.7523 | Poole Cabot Lane STW | Poole Cabot Lane STW | 0 | 0.028846 | 115036.502 | 0.62458 | 6.65 | 7.17 | 7.17 | 158 | 158 | 0.62458 | 7.7946 | 1.1446 | 0.52
15171 | Hallen Caravan Site SPS | 150 | 0 | 13.2536 | - | 13.2536 | 12.0208 | 0.15 | 0.7523 | Avonmouth Kingsweston Lane STW | Hallen Hallen Village SPS | 0 | 0.028846 | 86277.3765 | 0.069152 | 6.62 | 6.52 | 6.62 | 0 | 12 | 0.069152 | 6.6892 | 0.069152 | 0
17734 | Minehead Stephenson Road SPS | 150 | 0 | 13.2536 | - | 13.2536 | 110.738 | 0.15 | 0.7523 | Minehead Headworks STW | Minehead Mart Road SPS | 0 | 0.028846 | 86277.3765 | 0.63704 | 6.39 | 6.2 | 6.48 | 30 | 110 | 0.63704 | 7.117 | 0.72704 | 0.09
15380 | Bridgwater Crows Lane Surface Water SPS | - | 0 | - | - | - | 6.4856 | - | - | Chilton Trinity . STW | Bridgwater Bower Lane Bower Manor SPS | 0 | - | - | - | 6.34 | 6.26 | 6.34 | 0 | 6 | - | - | - | 0
15372 | Bridgwater Church Path SPS | 70 | 0 | 2.8863 | - | 2.8863 | 73.3399 | 0.07 | 0.7523 | Chilton Trinity . STW | Bridgwater Chilton Street Saltlands SPS | 0 | 0.028846 | 40262.7757 | 1.1479 | 6.3 | 9.11 | 9.11 | 74 | 74 | 1.1479 | 10.2579 | 3.9579 | 2.81
15029 | Christchurch Conifer Close SPS | 100 | 0 | 5.8905 | - | 5.8905 | 73.5699 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Lodge Road SPS | 0 | 0.028846 | 57518.251 | 0.71824 | 5.77 | 6.62 | 6.8 | 72 | 74 | 0.71824 | 7.5182 | 1.7482 | 1.03
14279 | Studland Beach Cafe SPS | 100 | 0 | 5.8905 | - | 5.8905 | 145.4424 | 0.1 | 0.7523 | Studland Ferry Road STW | Studland Coombe SPS | 0 | 0.028846 | 57518.251 | 1.4199 | 5.74 | 19.14 | 19.14 | 146 | 146 | 1.4199 | 20.5599 | 14.8199 | 13.4
15034 | Christchurch Endfield Road SPS | 100 | 0 | 5.8905 | - | 5.8905 | 40.8036 | 0.1 | 0.7523 | Christchurch Stoney Lane STW | Christchurch Lodge Road SPS | 0 | 0.028846 | 57518.251 | 0.39835 | 5.3 | 6.13 | 6.13 | 40 | 40 | 0.39835 | 6.5284 | 1.2284 | 0.83
15017 | Bournemouth Fishermans Walk SPS | 100 | 0 | 5.8905 | - | 5.8905 | 37.4924 | 0.1 | 0.7523 | Holdenhurst Riverside Avenue STW | Boscombe No 1 SPS | 0 | 0.028846 | 57518.251 | 0.36603 | 4.3 | 30.98 | 31.39 | 34 | 38 | 0.36603 | 31.756 | 27.456 | 27.09
14239 | Wareham Sandford Lane Industrial Estate SPS | 80 | 0 | 3.7699 | - | 3.7699 | 384.0718 | 0.08 | 0.7523 | Wareham Keysworth Drive STW | Wareham Bestwall SPS | 0 | 0.028846 | 46014.6008 | 5.0337 | 3.81 | 3.29 | 3.88 | 18 | 388 | 5.0337 | 8.9137 | 5.1037 | 0.07
15010 | Boscombe No 3 SPS | 150 | 0 | 13.2536 | - | 13.2536 | 6.352 | 0.15 | 0.7523 | Holdenhurst Riverside Avenue STW | Boscombe No 1 SPS | 0 | 0.028846 | 86277.3765 | 0.036541 | 3.77 | 3.97 | 3.97 | 6 | 6 | 0.036541 | 4.0065 | 0.23654 | 0.2
15800 | Poole Newfoundland Drive Opp 20 SPS | 780 | 0 | 358.3772 | - | 358.3772 | 366.4025 | 0.78 | 0.7523 | Poole Cabot Lane STW | Poole East Quay Perry Gardens SPS | 0 | 0.028846 | 448642.3579 | 0.26238 | 2.41 | -0.96 | 2.57 | 46 | 366 | 0.26238 | 2.8324 | 0.42238 | 0.16
19676 | Mudeford Sandbank No.2 SPS | 90 | 0 | 4.7713 | - | 4.7713 | 352.8135 | 0.09 | 0.7523 | Christchurch Stoney Lane STW | Mudeford Sandbank No.3 SPS | 0 | 0.028846 | 51766.4259 | 3.957 | 2.21 | 2.07 | 2.21 | 0 | 352 | 3.957 | 6.167 | 3.957 | 0
15245 | Poole Blue Lagoon Sandbanks Road SPS | 100 | 0 | 5.8905 | - | 5.8905 | 58.6002 | 0.1 | 0.7523 | Poole Cabot Lane STW | Poole 101 Lilliput Road PSP | 0 | 0.028846 | 57518.251 | 0.5721 | 2.02 | 3.24 | 3.24 | 58 | 58 | 0.5721 | 3.8121 | 1.7921 | 1.22
19675 | Mudeford Sandbank No.1 SPS | 90 | 0 | 4.7713 | - | 4.7713 | 184.7379 | 0.09 | 0.7523 | Christchurch Stoney Lane STW | Mudeford Sandbank No.2 SPS | 0 | 0.028846 | 51766.4259 | 2.072 | 2.01 | 2.07 | 2.07 | 184 | 184 | 2.072 | 4.142 | 2.132 | 0.06
19678 | Mudeford Sandbank No.4 SPS | 90 | 0 | 4.7713 | - | 4.7713 | 215.0802 | 0.09 | 0.7523 | Christchurch Stoney Lane STW | Mudeford Sandbank No.3 SPS | 0 | 0.028846 | 51766.4259 | 2.4123 | 1.98 | 2.11 | 2.46 | 82 | 216 | 2.4123 | 4.8723 | 2.8923 | 0.48
15261 | Poole Taverner Close SPS | 500 | 0 | 147.2622 | - | 147.2622 | 374.1396 | 0.5 | 0.7523 | Poole Cabot Lane STW | Poole East Quay Perry Gardens SPS | 0 | 0.028846 | 287591.2551 | 0.46572 | 1.85 | -0.76 | 3.29 | - | 374 | 0.46572 | 3.7557 | 1.9057 | 1.44
15014 | Hengistbury Head Wardens Cottage SPS | 32 | 0 | 0.60319 | - | 0.60319 | 89.6594 | 0.032 | 0.7523 | Holdenhurst Riverside Avenue STW | Hengistbury Head Double Dykes SPS | 0 | 0.028846 | 18405.8403 | 4.0594 | 1.6 | 2.52 | 2.52 | 90 | 90 | 4.0594 | 6.5794 | 4.9794 | 0.92
14389 | Taunton Priory Storm Tanks SPS | 700 | 0 | 288.6338 | 750 | 750 | 161.376 | 0.7 | 1.9548 | Taunton Ham Lane Creech St Michael Taunton STW | Taunton Ham Lane Creech St Michael Taunton STW | 0 | 0.19476 | 1046207.3105 | 0.86809 | - | 17.67 | 17.84 | 112 | 114 | 0.86809 | 18.7081 | - | -
14372 | West Huntspill Sloway Lane SPS | 475 | 0 | 132.9041 | 130 | 130 | 3064.583 | 0.475 | 0.73586 | West Huntspill STW | West Huntspill STW | 0 | 0.027599 | 267241.727 | 3.8952 | - | 5.34 | 8.2 | 110 | 3064 | 3.8952 | 12.0952 | - | -
15552 | Weymouth Knightsdale Newstead Road SPS | 900 | 0 | 477.1294 | 87 | 87 | 1023.5283 | 0.9 | 0.13717 | Weymouth . STW | Weymouth Radipole SPS | 0 | 0.00095906 | 94391.1485 | 0.023172 | - | 3.02 | 30.89 | 940 | 1110 | 0.023172 | 30.9132 | - | -
11571 | Frome Dragonfly Close SPS | 125 | 0 | 9.2039 | - | 9.2039 | 349.2782 | 0.125 | 0.7523 | Frome Welshmill Lane STW | Frome Welshmill Lane STW | 0 | 0.028846 | 71897.8138 | 2.5463 | - | - | - | - | - | 2.5463 | - | - | -
12706 | Radstock Nelson Ward Drive SPS | 80 | 0 | 3.7699 | - | 3.7699 | 155.5578 | 0.08 | 0.7523 | Radstock Mill Lane STW | Radstock Victoria Square SPS | 0 | 0.028846 | 46014.6008 | 2.0388 | - | - | - | - | - | 2.0388 | - | - | -
11570 | Weston-Super-Mare Haygrove SPS | 90 | 0 | 4.7713 | - | 4.7713 | 59.0485 | 0.09 | 0.7523 | Wick St Lawrence . STW | Worle North (Fw) SPS | 0 | 0.028846 | 51766.4259 | 0.66227 | - | - | - | - | - | 0.66227 | - | - | -
11642 | Martock Long Orchard Way SPS | 90 | 0 | 4.7713 | - | 4.7713 | 51.1443 | 0.09 | 0.7523 | Martock Hurst Bow STW | Martock Hurst Bow STW | 0 | 0.028846 | 51766.4259 | 0.57362 | - | - | - | - | - | 0.57362 | - | - | -
17807 | Burton Whitehayes Road SPS | - | 0 | - | - | - | 9.8655 | - | - | Christchurch Stoney Lane STW | Christchurch Stoney Lane STW | 0 | - | - | - | - | 3.94 | 3.95 | 0 | 4 | - | - | - | -
11591 | Weston-Super-Mare Tiger Moth Road SPS | - | 0 | - | - | - | 10.2197 | - | - | Wick St Lawrence . STW | Haywood Village Cobham Parade PPS | 0 | - | - | - | - | - | - | - | - | - | - | - | -
13523 | Lyneham D Site (Old Small Stw) SPS | - | 0 | - | - | - | 0 | - | - | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham Building 212 (D Site Ps 3) SPS | 0 | - | - | - | - | - | - | - | - | - | - | - | -
14019 | Bristol Rosery Close SPS | - | 0 | - | - | - | 0 | - | - | Avonmouth Kingsweston Lane STW | Bristol Saltmarsh Drive SPS | 0 | - | - | - | - | - | - | - | - | - | - | - | -
14640 | Lyneham Gymnasium (Ps 8) SPS | - | 0 | - | - | - | 0 | - | - | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham B Site (Main Stw) Raf Lyneham STW | 0 | - | - | - | - | - | - | - | - | - | - | - | -
15248 | Poole Quay Surface Water SPS | - | 0 | - | - | - | 0 | - | - | Poole Cabot Lane STW | Poole East Quay Perry Gardens SPS | 0 | - | - | - | - | - | - | - | - | - | - | - | -
15820 | Christchurch Fairfield Close SPS | - | 0 | - | - | - | 25.3322 | - | - | Christchurch Stoney Lane STW | Christchurch Beaconsfield Road SPS | 0 | - | - | - | - | - | - | - | - | - | - | - | -
17946 | Poole Crichel Mount Road SPS | - | 0 | - | - | - | 0 | - | - | Poole Cabot Lane STW | Poole Shore Road SPS | 0 | - | - | - | - | - | - | - | - | - | - | - | -
18728 | Lyneham Technical Site (Ps 18) SPS | - | 0 | - | - | - | 0 | - | - | Lyneham B Site (Main Stw) Raf Lyneham STW | Lyneham B Site (Main Stw) Raf Lyneham STW | 0 | - | - | - | - | - | - | - | - | - | - | - | -
19054 | Clevedon Pedder Road SPS | - | 0 | - | - | - | 0 | - | - | Kingston Seymour Back Lane STW | Clevedon Clevedon Main SPS | 0 | - | - | - | - | - | - | - | - | - | - | - | -
19107 | Old Sarum Castle Gate SPS | - | 0 | - | - | - | 0 | - | - | Salisbury Petersfinger -Southampton Road STW | Salisbury Petersfinger -Southampton Road STW | 0 | - | - | - | - | - | - | - | - | - | - | - | -
19990 | Chilton Trinity Western Way Surface Water SPS | - | 0 | - | - | - | 0 | - | - | Chilton Trinity . STW | Bridgwater Chilton Street Saltlands SPS | 0 | - | - | - | - | - | - | - | - | - | - | - | -
17454 | Bourton Bridge SPS | 125 | - | 9.2039 | - | 9.2039 | 271.9191 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 1.9824 | 103.59 | 102.24 | 103.59 | 0 | 136 | 1.9824 | 105.5724 | 1.9824 | 0
17975 | Leigh Woods North Road Private SPS | 75 | - | 3.3134 | - | 3.3134 | 284.8067 | 0.075 | 0.7523 | - | - | - | 0.028846 | 43138.6883 | 4.0666 | 97.92 | 104.9 | 106.93 | 234 | 284 | 4.0666 | 110.9966 | 13.0766 | 9.01
10298 | Blandford Sandbourne Avenue SPS | 100 | - | 5.8905 | - | 5.8905 | 26.0859 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 0.25467 | 83.68 | 85.03 | 85.79 | 6 | 26 | 0.25467 | 86.0447 | 2.3647 | 2.11
12266 | Evercreech Kingfisher Road SPS | 125 | - | 9.2039 | - | 9.2039 | 223.5401 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 1.6297 | 83.62 | 84.76 | 89.48 | 20 | 44 | 1.6297 | 91.1097 | 7.4897 | 5.86
12564 | Yate Hazel Close SPS | 180 | - | 19.0852 | - | 19.0852 | 377.7795 | 0.18 | 0.7523 | - | - | - | 0.028846 | 103532.8518 | 1.7174 | 79.99 | 79.78 | 80.91 | 62 | 88 | 1.7174 | 82.6274 | 2.6374 | 0.92
10066 | Castle Combe Near Preedy Cottage SPS | 80 | - | 3.7699 | - | 3.7699 | 14.9674 | 0.08 | 0.7523 | - | - | - | 0.028846 | 46014.6008 | 0.19616 | 76.25 | 76.33 | 76.33 | 14 | 14 | 0.19616 | 76.5262 | 0.27616 | 0.08
10434 | Salisbury Sassoon Close S105a SPS | - | - | - | - | - | 68.8926 | - | - | - | - | - | - | - | - | 73.02 | 79.96 | 79.96 | 68 | 68 | - | - | - | 6.94
17306 | Yate Station Yard Surface Water SPS | 100 | - | 5.8905 | - | 5.8905 | 30.5094 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 0.29786 | 69.67 | 69.96 | 69.96 | 14 | 14 | 0.29786 | 70.2579 | 0.58786 | 0.29
10777 | Radstock Fortescue Road Private SPS | 80 | - | 3.7699 | - | 3.7699 | 18.885 | 0.08 | 0.7523 | - | - | - | 0.028846 | 46014.6008 | 0.24751 | 69.37 | 69.27 | 69.37 | 0 | 16 | 0.24751 | 69.6175 | 0.24751 | 0
14165 | Malmesbury Cowbridge SPS | 100 | - | 5.8905 | - | 5.8905 | 3.1573 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 0.030824 | 67.82 | 67.83 | 67.83 | 4 | 4 | 0.030824 | 67.8608 | 0.040824 | 0.01
15479 | Dorchester Castle Park SPS | 150 | - | 13.2536 | - | 13.2536 | 554.4326 | 0.15 | 0.7523 | - | - | - | 0.028846 | 86277.3765 | 3.1895 | 60.81 | 67.24 | 68.32 | 290 | 554 | 3.1895 | 71.5095 | 10.6995 | 7.51
10864 | Bristol Bishopthorpe Road SPS | 160 | - | 15.0796 | - | 15.0796 | 21.1899 | 0.16 | 0.7523 | - | - | - | 0.028846 | 92029.2016 | 0.11213 | 58.53 | 58.13 | 58.53 | 0 | 22 | 0.11213 | 58.6421 | 0.11213 | 0
10053 | Chew Magna Limeburn Hill SPS | 100 | - | 5.8905 | - | 5.8905 | 33.7941 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 0.32992 | 57.91 | 58.36 | 58.51 | 10 | 16 | 0.32992 | 58.8399 | 0.92992 | 0.6
10825 | Bath Bailbrook Cottages SPS | 90 | - | 4.7713 | - | 4.7713 | 67.0181 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 0.75165 | 57.5 | 60.72 | 60.72 | 68 | 68 | 0.75165 | 61.4716 | 3.9716 | 3.22
17794 | Frampton Cotterell Beesmoor Road SPS | 80 | - | 3.7699 | - | 3.7699 | 15.0592 | 0.08 | 0.7523 | - | - | - | 0.028846 | 46014.6008 | 0.19737 | 56.77 | 56.76 | 56.77 | 0 | 8 | 0.19737 | 56.9674 | 0.19737 | 0
11921 | Bristol Hampton Road SPS | 200 | - | 23.5619 | - | 23.5619 | 27.42 | 0.2 | 0.7523 | - | - | - | 0.028846 | 115036.502 | 0.10887 | 54.79 | 54.92 | 54.92 | 14 | 14 | 0.10887 | 55.0289 | 0.23887 | 0.13
10510 | Bishops Lydeard Station Green SPS | 125 | - | 9.2039 | - | 9.2039 | 743.032 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 5.4169 | 52.28 | 59.23 | 59.96 | 670 | 742 | 5.4169 | 65.3769 | 13.0969 | 7.68
10312 | Iron Acton Hoovers Lane SPS | 180 | - | 19.0852 | 400 | 400 | 57.4173 | 0.18 | 15.7672 | - | - | - | 12.6709 | 2169911.4589 | 109.277 | 51.12 | 51.07 | 51.24 | - | 58 | 109.277 | 160.517 | 109.397 | 0.12
10516 | Melksham St. Andrews Road SPS | 32 | - | 0.60319 | - | 0.60319 | 42.8095 | 0.032 | 0.7523 | - | - | - | 0.028846 | 18405.8403 | 1.9382 | 47.07 | 47.15 | 47.21 | - | 42 | 1.9382 | 49.1482 | 2.0782 | 0.14
10508 | South Petherton Chapel Field Road SPS | 80 | - | 3.7699 | - | 3.7699 | 192.8756 | 0.08 | 0.7523 | - | - | - | 0.028846 | 46014.6008 | 2.5279 | 43.97 | 48.67 | 48.68 | 188 | 192 | 2.5279 | 51.2079 | 7.2379 | 4.71
10767 | Trowbridge Leisler Gardens SPS | 250 | - | 36.8155 | - | 36.8155 | 762.5802 | 0.25 | 0.7523 | - | - | - | 0.028846 | 143795.6275 | 2.2762 | 39.5 | 41.28 | 43.08 | 544 | 740 | 2.2762 | 45.3562 | 5.8562 | 3.58
10256 | Bishops Hull Milligan Sngle PrSPS | 90 | - | 4.7713 | - | 4.7713 | 64.3673 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 0.72192 | 34.18 | 35.09 | 35.09 | 64 | 64 | 0.72192 | 35.8119 | 1.6319 | 0.91
17651 | Norton Fitzwarren Great Western Way No. 2 SPS | 180 | - | 19.0852 | - | 19.0852 | 324.2083 | 0.18 | 0.7523 | - | - | - | 0.028846 | 103532.8518 | 1.4739 | 22.15 | 21.55 | 22.72 | 250 | 290 | 1.4739 | 24.1939 | 2.0439 | 0.57
10847 | Bath The Podium SPS | 90 | - | 4.7713 | - | 4.7713 | 93.7223 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 1.0512 | 21.63 | 28.96 | 28.99 | 90 | 94 | 1.0512 | 30.0412 | 8.4112 | 7.36
17568 | Cannington Blackmore Lane SPS | 160 | - | 15.0796 | - | 15.0796 | 1184.8398 | 0.16 | 0.7523 | - | - | - | 0.028846 | 92029.2016 | 6.2701 | 13.42 | 11.12 | 16.54 | 1022 | 1146 | 6.2701 | 22.8101 | 9.3901 | 3.12
15483 | Bradpole Fishweir Flood Surface Water SPS | 300 | - | 53.0144 | - | 53.0144 | 23.3961 | 0.3 | 0.7523 | - | - | - | 0.028846 | 172554.753 | 0.055392 | 13.24 | 13.86 | 13.86 | 24 | 24 | 0.055392 | 13.9154 | 0.67539 | 0.62
15570 | Clevedon Middle Yeo SPS | 610 | - | 219.185 | - | 219.185 | 116.1772 | 0.61 | 0.7523 | - | - | - | 0.028846 | 350861.3312 | 0.11285 | 9.63 | 5.67 | 9.63 | 0 | 68 | 0.11285 | 9.7429 | 0.11285 | 0
10302 | Minehead Blue Anchor Chalets SPS | - | - | - | - | - | 110.4313 | - | - | - | - | - | - | - | - | 7.64 | 10.1 | 10.1 | - | 110 | - | - | - | 2.46
17595 | Avonmouth Access 18 Kings Weston Lane Station 2 SPS | 129 | - | 9.8024 | - | 9.8024 | 843.6175 | 0.129 | 0.7523 | - | - | - | 0.028846 | 74198.5438 | 5.903 | 7.36 | 6.53 | 10.03 | 124 | 844 | 5.903 | 15.933 | 8.573 | 2.67
15453 | Burrowbridge School Lane SPS | 75 | - | 3.3134 | - | 3.3134 | 14.279 | 0.075 | 0.7523 | - | - | - | 0.028846 | 43138.6883 | 0.20388 | 6.89 | 4.86 | 7.64 | 8 | 14 | 0.20388 | 7.8439 | 0.95388 | 0.75
10368 | Glastonbury Sharpham Road No 1 Private SPS | 125 | - | 9.2039 | - | 9.2039 | 89.7139 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 0.65404 | 6.36 | 6.75 | 6.75 | 14 | 14 | 0.65404 | 7.404 | 1.044 | 0.39
10223 | Horsey Kings Road SPS | 180 | - | 19.0852 | - | 19.0852 | 189.9313 | 0.18 | 0.7523 | - | - | - | 0.028846 | 103532.8518 | 0.86344 | 6.34 | 5.89 | 6.42 | 54 | 190 | 0.86344 | 7.2834 | 0.94344 | 0.08
14373 | Dunball . SPS | 125 | - | 9.2039 | - | 9.2039 | 480.3662 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 3.502 | 6.18 | 4.01 | 8.92 | 406 | 430 | 3.502 | 12.422 | 6.242 | 2.74
10221 | Horsey Regal Walk SPS | 180 | - | 19.0852 | - | 19.0852 | 313.8916 | 0.18 | 0.7523 | - | - | - | 0.028846 | 103532.8518 | 1.427 | 6.13 | 5.89 | 6.26 | 110 | 314 | 1.427 | 7.687 | 1.557 | 0.13
17360 | Brean Pontins Surface Water SPS | 100 | - | 5.8905 | - | 5.8905 | 34.4112 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 0.33595 | 6.07 | 5.89 | 6.75 | 4 | 10 | 0.33595 | 7.0859 | 1.0159 | 0.68
10370 | Porlock Weir Quay SPS | - | - | - | - | - | 195.6441 | - | - | - | - | - | - | - | - | 6.02 | 6.56 | 6.56 | 196 | 196 | - | - | - | 0.54
10222 | Horsey Kings Down Main SPS | 280 | - | 46.1814 | - | 46.1814 | 401.2966 | 0.28 | 0.7523 | - | - | - | 0.028846 | 161051.1028 | 1.037 | 5.85 | 6.32 | 6.92 | 136 | 354 | 1.037 | 7.957 | 2.107 | 1.07
15520 | Minehead Vulcan Road SPS | 100 | - | 5.8905 | - | 5.8905 | 266.5544 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 2.6023 | 5.78 | 5.55 | 6.09 | 8 | 266 | 2.6023 | 8.6923 | 2.9123 | 0.31
12719 | Mark Poplar Lane SPS | 110 | - | 7.1275 | - | 7.1275 | 107.7678 | 0.11 | 0.7523 | - | - | - | 0.028846 | 63270.0761 | 0.92846 | 5.4 | 5.36 | 5.61 | 76 | 108 | 0.92846 | 6.5385 | 1.1385 | 0.21
10908 | Weston-Super-Mare Aisecome Way Surface Water SPS | 450 | - | 119.2823 | - | 119.2823 | 744.0685 | 0.45 | 0.7523 | - | - | - | 0.028846 | 258832.1296 | 1.0568 | 5.24 | 4.86 | 6.25 | 16 | 744 | 1.0568 | 7.3068 | 2.0668 | 1.01
10064 | East Huntspill Crown Inn Church Road SPS | 100 | - | 5.8905 | - | 5.8905 | 2.779 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 0.02713 | 4.91 | 4.96 | 4.96 | 2 | 2 | 0.02713 | 4.9871 | 0.07713 | 0.05
17999 | Wilstock Village Clover Way SPS | 280 | - | 46.1814 | - | 46.1814 | 1560.524 | 0.28 | 0.7523 | - | - | - | 0.028846 | 161051.1028 | 4.0326 | 4.8 | 5.6 | 6.79 | 74 | 1560 | 4.0326 | 10.8226 | 6.0226 | 1.99
10198 | Charmouth Seadown Holiday Park SPS | 160 | - | 15.0796 | - | 15.0796 | 446.3987 | 0.16 | 0.7523 | - | - | - | 0.028846 | 92029.2016 | 2.3623 | 4.64 | 9.54 | 9.54 | 338 | 338 | 2.3623 | 11.9023 | 7.2623 | 4.9
17250 | Poole Broomhill Way Surface SPS | 315 | - | 58.4483 | - | 58.4483 | 29.8786 | 0.315 | 0.7523 | - | - | - | 0.028846 | 181182.4907 | 0.066501 | 2.13 | 1.72 | 2.35 | 20 | 30 | 0.066501 | 2.4165 | 0.2865 | 0.22
15234 | Poole Turlin Moor Sw SPS | 900 | - | 477.1294 | - | 477.1294 | 18.0291 | 0.9 | 0.7523 | - | - | - | 0.028846 | 517664.2591 | 0.01082 | 1.81 | 1.74 | 2.13 | 10 | 18 | 0.01082 | 2.1408 | 0.33082 | 0.32
15249 | Poole Rnli Surface Water Slipway SPS | 850 | - | 425.5876 | - | 425.5876 | 50.5678 | 0.85 | 0.7523 | - | - | - | 0.028846 | 488905.1336 | 0.032564 | 1.74 | 1.09 | 2.08 | 30 | 50 | 0.032564 | 2.1126 | 0.37256 | 0.34
13340 | Weston-Super-Mare Black Rock Windwhistle Road SPS | 1800 | - | 1908.5175 | 3000 | 3000 | 1937.7201 | 1.8 | 1.1825 | - | - | - | 0.071274 | 1627433.5942 | 1.2118 | - | 1.46 | 14.92 | 774 | 1676 | 1.2118 | 16.1318 | - | -
19056 | Weymouth Castle Cove Old Castle Road Wyke Regis SPS | 225 | - | 29.8206 | 30 | 30 | 495.3412 | 0.225 | 0.75682 | - | - | - | 0.029194 | 130194.6875 | 1.7113 | - | 11.86 | 21.38 | 132 | 480 | 1.7113 | 23.0913 | - | -
13273 | Shipton Gorge Off Markets Lane SPS | 110 | - | 7.1275 | 6.3 | 6.3 | 866.0551 | 0.11 | 0.66496 | - | - | - | 0.022537 | 55924.5362 | 5.8627 | - | 60.18 | 60.18 | 864 | 864 | 5.8627 | 66.0427 | - | -
11492 | Berkeley Gloucestershire Science And Technology Park SPS | 160 | - | 15.0796 | - | 15.0796 | 3203.6707 | 0.16 | 0.7523 | - | - | - | 0.028846 | 92029.2016 | 16.9535 | - | - | - | - | - | 16.9535 | - | - | -
12498 | Brent Knoll Brent Knoll Primary School SPS | 225 | - | 29.8206 | - | 29.8206 | 2616.6943 | 0.225 | 0.7523 | - | - | - | 0.028846 | 129416.0648 | 8.9346 | - | - | - | - | - | 8.9346 | - | - | -
13645 | Larkhill The Packway SPS | 110 | - | 7.1275 | - | 7.1275 | 867.1587 | 0.11 | 0.7523 | - | - | - | 0.028846 | 63270.0761 | 7.4709 | - | - | - | - | - | 7.4709 | - | - | -
13586 | Warminster St Andrews Road SPS | 160 | - | 15.0796 | - | 15.0796 | 1404.2715 | 0.16 | 0.7523 | - | - | - | 0.028846 | 92029.2016 | 7.4313 | - | - | - | - | - | 7.4313 | - | - | -
11280 | Bridgwater Woodlands Court SPS | 125 | - | 9.2039 | - | 9.2039 | 992.0788 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 7.2326 | - | - | - | - | - | 7.2326 | - | - | -
10363 | Keynsham St Clements Road SPS | 160 | - | 15.0796 | - | 15.0796 | 917.4242 | 0.16 | 0.7523 | - | - | - | 0.028846 | 92029.2016 | 4.8549 | - | 40.35 | 40.45 | 448 | 460 | 4.8549 | 45.3049 | - | -
12155 | Chipping Sodbury Kingrove Lane SPS | 50 | - | 1.4726 | - | 1.4726 | 189.6727 | 0.05 | 0.7523 | - | - | - | 0.028846 | 28759.1255 | 4.6642 | - | - | - | - | - | 4.6642 | - | - | -
10567 | Weston-Super-Mare Weston Airfield Business Park S105a SPS | 180 | - | 19.0852 | - | 19.0852 | 905.7269 | 0.18 | 0.7523 | - | - | - | 0.028846 | 103532.8518 | 4.1175 | - | - | - | - | - | 4.1175 | - | - | -
13674 | Glastonbury ¦ Bligh Bund Road SPS | 125 | - | 9.2039 | - | 9.2039 | 527.5614 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 3.8461 | - | - | - | - | - | 3.8461 | - | - | -
13623 | Wimborne ¦ Parmiter Drive SPS | 80 | - | 3.7699 | - | 3.7699 | 273.3802 | 0.08 | 0.7523 | - | - | - | 0.028846 | 46014.6008 | 3.583 | - | - | - | - | - | 3.583 | - | - | -
12724 | Yeovil Lufton SPS | 225 | - | 29.8206 | - | 29.8206 | 935.1606 | 0.225 | 0.7523 | - | - | - | 0.028846 | 129416.0648 | 3.1931 | - | - | - | - | - | 3.1931 | - | - | -
11768 | Tetbury Cirencester Road 2 SPS | 150 | - | 13.2536 | - | 13.2536 | 508.8695 | 0.15 | 0.7523 | - | - | - | 0.028846 | 86277.3765 | 2.9274 | - | - | - | - | - | 2.9274 | - | - | -
13744 | Frome Lily Road SPS | 110 | - | 7.1275 | - | 7.1275 | 323.8841 | 0.11 | 0.7523 | - | - | - | 0.028846 | 63270.0761 | 2.7904 | - | - | - | - | - | 2.7904 | - | - | -
10243 | Cheddar Helliers Lane SPS | 100 | - | 5.8905 | - | 5.8905 | 253.5833 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 2.4757 | - | - | - | - | - | 2.4757 | - | - | -
13589 | Langford Muntjac Road Surface SPS | 180 | - | 19.0852 | - | 19.0852 | 533.347 | 0.18 | 0.7523 | - | - | - | 0.028846 | 103532.8518 | 2.4246 | - | - | - | - | - | 2.4246 | - | - | -
12367 | Bridgwater Haywater Avenue SPS | 125 | - | 9.2039 | - | 9.2039 | 326.041 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 2.3769 | - | - | - | - | - | 2.3769 | - | - | -
15560 | Weymouth Camp Road Wyke Regis SPS | 100 | - | 5.8905 | - | 5.8905 | 224.154 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 2.1884 | - | - | - | - | - | 2.1884 | - | - | -
12879 | Calne Beversbrook Road SPS | 110 | - | 7.1275 | - | 7.1275 | 233.4552 | 0.11 | 0.7523 | - | - | - | 0.028846 | 63270.0761 | 2.0113 | - | - | - | - | - | 2.0113 | - | - | -
12355 | Thornbury Otter Way SPS | 125 | - | 9.2039 | - | 9.2039 | 273.5475 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 1.9942 | - | - | - | - | - | 1.9942 | - | - | -
12324 | Maiden Newton Neils View Private SPS | 80 | - | 3.7699 | - | 3.7699 | 149.6706 | 0.08 | 0.7523 | - | - | - | 0.028846 | 46014.6008 | 1.9616 | - | - | - | - | - | 1.9616 | - | - | -
13574 | Wickwar Sodbury Road SPS | 125 | - | 9.2039 | - | 9.2039 | 265.8641 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 1.9382 | - | - | - | - | - | 1.9382 | - | - | -
12872 | Berkeley Canonbury Street SPS | 125 | - | 9.2039 | - | 9.2039 | 251.9735 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 1.837 | - | - | - | - | - | 1.837 | - | - | -
10523 | Midsomer Norton Withies Park SPS | 120 | - | 8.4823 | - | 8.4823 | 227.6281 | 0.12 | 0.7523 | - | - | - | 0.028846 | 69021.9012 | 1.7502 | - | - | - | - | - | 1.7502 | - | - | -
11559 | Taunton Mountfields Road SPS | 110 | - | 7.1275 | - | 7.1275 | 197.6156 | 0.11 | 0.7523 | - | - | - | 0.028846 | 63270.0761 | 1.7025 | - | - | - | - | - | 1.7025 | - | - | -
11707 | Calne Rookery Park SPS | 150 | - | 13.2536 | - | 13.2536 | 292.6492 | 0.15 | 0.7523 | - | - | - | 0.028846 | 86277.3765 | 1.6835 | - | - | - | - | - | 1.6835 | - | - | -
12886 | Keynsham The Chocolate Quarters SPS | 315 | - | 58.4483 | - | 58.4483 | 755.5452 | 0.315 | 0.7523 | - | - | - | 0.028846 | 181182.4907 | 1.6816 | - | - | - | - | - | 1.6816 | - | - | -
12173 | Evercreech Chestnut Lane SPS | 90 | - | 4.7713 | - | 4.7713 | 120.8709 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 1.3556 | - | - | - | - | - | 1.3556 | - | - | -
10692 | Blandford Forum ¦ Grange Care Home The Orchard SPS | 100 | - | 5.8905 | - | 5.8905 | 136.9578 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 1.3371 | - | - | - | - | - | 1.3371 | - | - | -
12369 | Horton Langworthy Orchard SPS | 80 | - | 3.7699 | - | 3.7699 | 91.8044 | 0.08 | 0.7523 | - | - | - | 0.028846 | 46014.6008 | 1.2032 | - | - | - | - | - | 1.2032 | - | - | -
12520 | Weymouth Curtis Way SPS | 450 | - | 119.2823 | - | 119.2823 | 772.4389 | 0.45 | 0.7523 | - | - | - | 0.028846 | 258832.1296 | 1.0971 | - | - | - | - | - | 1.0971 | - | - | -
12459 | Wimborne Merley Gardens Surface SPS | 90 | - | 4.7713 | - | 4.7713 | 94.0754 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 1.0551 | - | - | - | - | - | 1.0551 | - | - | -
10835 | Salwayash Ash Farm Private SPS | 90 | - | 4.7713 | - | 4.7713 | 93.3836 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 1.0474 | - | - | - | - | - | 1.0474 | - | - | -
10778 | Weston-Super-Mare Old Mill Way Private SPS | 100 | - | 5.8905 | - | 5.8905 | 105.3752 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 1.0287 | - | - | - | - | - | 1.0287 | - | - | -
13581 | Ansford ¦ Bartlett Square SPS | 90 | - | 4.7713 | - | 4.7713 | 82.554 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 0.92589 | - | - | - | - | - | 0.92589 | - | - | -
13694 | Bridgwater ¦ Campion Way SPS | 125 | - | 9.2039 | - | 9.2039 | 116.6505 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 0.85042 | - | - | - | - | - | 0.85042 | - | - | -
10785 | Weston-Super-Mare Spring Hill SPS | 180 | - | 19.0852 | - | 19.0852 | 184.4784 | 0.18 | 0.7523 | - | - | - | 0.028846 | 103532.8518 | 0.83865 | - | 39.44 | 39.56 | 170 | 176 | 0.83865 | 40.3987 | - | -
17719 | Frome Knights Maltings SPS | 100 | - | 5.8905 | - | 5.8905 | 83.2916 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 0.81315 | - | - | - | - | - | 0.81315 | - | - | -
12421 | Oakdale Dorchester Road Surface SPS | 90 | - | 4.7713 | - | 4.7713 | 70.4291 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 0.78991 | - | - | - | - | - | 0.78991 | - | - | -
13716 | Congresbury Furnace Way SPS | 125 | - | 9.2039 | - | 9.2039 | 97.1429 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 0.7082 | - | - | - | - | - | 0.7082 | - | - | -
12675 | Blandford Brewery SPS | 250 | - | 36.8155 | - | 36.8155 | 236.1678 | 0.25 | 0.7523 | - | - | - | 0.028846 | 143795.6275 | 0.70493 | - | - | - | - | - | 0.70493 | - | - | -
12169 | Tetbury Clothiers Close SPS | 110 | - | 7.1275 | - | 7.1275 | 69.4902 | 0.11 | 0.7523 | - | - | - | 0.028846 | 63270.0761 | 0.59868 | - | - | - | - | - | 0.59868 | - | - | -
12186 | Bridgwater Gateway SPS | 250 | - | 36.8155 | - | 36.8155 | 166.497 | 0.25 | 0.7523 | - | - | - | 0.028846 | 143795.6275 | 0.49697 | - | - | - | - | - | 0.49697 | - | - | -
17593 | Avonmouth Constellation Kings Weston Lane SPS | 100 | - | 5.8905 | - | 5.8905 | 44.8527 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 0.43788 | - | - | - | - | - | 0.43788 | - | - | -
12695 | Dunster Marsh Gardens Sewage SPS | 125 | - | 9.2039 | - | 9.2039 | 53.2303 | 0.125 | 0.7523 | - | - | - | 0.028846 | 71897.8138 | 0.38807 | - | - | - | - | - | 0.38807 | - | - | -
15608 | Worle Summer Lane SPS | 600 | - | 212.0575 | - | 212.0575 | 348.5533 | 0.6 | 0.7523 | - | - | - | 0.028846 | 345109.5061 | 0.34562 | - | 5.27 | 6.45 | - | 326 | 0.34562 | 6.7956 | - | -
14633 | Rooksbridge Gills Lane SPS | 100 | - | 5.8905 | - | 5.8905 | 32.3334 | 0.1 | 0.7523 | - | - | - | 0.028846 | 57518.251 | 0.31566 | - | - | - | - | - | 0.31566 | - | - | -
11928 | Bristol Rose Bush Gardens SPS | 90 | - | 4.7713 | - | 4.7713 | 21.3409 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 0.23935 | - | - | - | - | - | 0.23935 | - | - | -
11879 | Street Farm Lane SPS | 90 | - | 4.7713 | - | 4.7713 | 20.1384 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 0.22586 | - | - | - | - | - | 0.22586 | - | - | -
12888 | Somrerton Bancombe Road Surface Water SPS | 150 | - | 13.2536 | - | 13.2536 | 9.8697 | 0.15 | 0.7523 | - | - | - | 0.028846 | 86277.3765 | 0.056778 | - | - | - | - | - | 0.056778 | - | - | -
13732 | Monkton Heathfield Hartnells Farm SPS | 90 | - | 4.7713 | - | 4.7713 | 3.9312 | 0.09 | 0.7523 | - | - | - | 0.028846 | 51766.4259 | 0.04409 | - | - | - | - | - | 0.04409 | - | - | -
10216 | Horsey Little Sydenham Farm Temporary SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10303 | Christchurch Marina View S105a SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10354 | Horsey Kings Road Lift Station SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10355 | Horsey Regal Walk Lift Station SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10361 | Taunton Silkmills Mill Rise Private SPS | - | - | - | - | - | 267.5377 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10366 | Glastonbury Sharpham Road No 2 Private SPS | - | - | - | - | - | 120.8032 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10404 | Crewkerne Bradford Road Private SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10418 | Crewkerne Station Road Private SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10426 | Salisbury Lywood Close SPS | - | - | - | - | - | 232.3811 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10463 | Trowbridge Riverway Depot SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10495 | Amesbury Haragon Drive Private SPS | - | - | - | - | - | 179.0164 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10519 | Creech St Michael Laburnum Terrace SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10560 | Poole Foxgloves Close Private SPS | - | - | - | - | - | 72.2731 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10663 | Bristol Access 18 Private SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10748 | Highbridge Withycombe Meadow SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10762 | Highbridge Huntspill Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10768 | Sixpenny Handley Town Farm House SPS | - | - | - | - | - | 9.2861 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10786 | Weston-Super-Mare Duplicate Site SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10906 | Highbridge Oldway Place SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10954 | South Petherton Hele Cottages Private SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10960 | Weymouth Fairways Court Surface Water SPS | - | - | - | - | - | 35.9273 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
11528 | Wimborne Merley Lane SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
11722 | Trowbridge Castle Hedingham SPS | - | - | - | - | - | 170.8449 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12167 | Salisbury Rhodes Moorhouse Way SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12171 | Wimborne Wimborne Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12183 | Wick Kingsfield Close SPS | - | - | - | - | - | 65.3893 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12696 | Dunster Marsh Gardens SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12764 | Salisbury Long Hedge Farm SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12864 | Chickerell Oldridge Road SPS | - | - | - | - | - | 187.7224 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12865 | Bridgwater Old Taunton Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12878 | Paulton Bristol Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12894 | Charfield Kestrel Road SPS | - | - | - | - | - | 151.1616 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12897 | Studley Studley Gardens SPS | - | - | - | - | - | 99.8104 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
12900 | South Petherton Compton Durville SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13564 | Puriton Orchard Close SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13566 | Poole Whitecliff Road SPS | - | - | - | - | - | 3.2135 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13567 | Poole Whitecliff Road Surface SPS | - | - | - | - | - | 3.8569 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13587 | Highbridge Pepperall Roundabout Surface SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13606 | St Leonards Neptune Drive SPS | - | - | - | - | - | 387.6832 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13639 | Durleigh ¦ Enmore Road 1 SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13652 | Erlestoke ¦ Erlestoke House SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13668 | Dorchester Poundbury Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13693 | Thornbury ¦ Red Admiral Way SPS | - | - | - | - | - | 603.2362 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13718 | Westbury Sailing Club SPS | - | - | - | - | - | 220.5889 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
13722 | Corsham The Cleeve 1 SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14018 | Bristol Glen Avon Sludge Quay SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14037 | Christchurch Quomps No 1 SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14060 | Warmley Anchor Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14091 | Glastonbury Paradise SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14208 | Calne Lickhill Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14223 | Upton Palmerston Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14225 | Swanage Yacht Comminutor SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14231 | Upton Meadows Drive SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14233 | Swanage Pier Macerators SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14267 | Bovington Cologne Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14308 | Durrington Brigmerston Syphon SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14357 | Salisbury Milford Mill Gardens SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14418 | Minehead Blenheim Gardens SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14419 | Minehead Green Spot SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14465 | Melksham Snarlton Lane SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14471 | Melksham Hampton Meadows Bowerhill SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14472 | Melksham Awdry Avenue Depot SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14484 | Melksham Sandridge Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14494 | St Georges Trelawn Close No 2 SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14499 | Weston-Super-Mare Black Rock SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14516 | Portishead Brampton Court SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14541 | Clutton Maypole Farm SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14628 | Wiveliscombe Ford Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
14646 | Lyneham Ejector Station Preston Lane SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15199 | Shaftesbury Heathfields SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15224 | Fordingbridge Sandlecopse SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15255 | Poole East Quay Surface Water Slipway SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15263 | Poole Fleetsbridge Surface Water SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15296 | Kingsbury Episcopi Stembridge (Old) SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15329 | Yeovil Houndstone SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15346 | Bridgwater Wembdon Rise SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15404 | Bridgwater Blake Bridge Lime Kiln SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15407 | Dunwear Riverside SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15437 | Taunton New Road Trull SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15442 | Taunton Priorswood Refuse Tip SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15477 | Chickerell Budmouth School SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15509 | Horner . SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15512 | West Luccombe . SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15546 | Bathford Comminutor SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15563 | Weymouth Park Stanley Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15571 | Portishead Severn Heights SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15578 | Portishead Tower Farm SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15579 | Portishead Bristol Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15586 | Worle Madam Rhyne SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15590 | Clevedon Regents Park Surface SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15596 | Portishead Nautical School SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15604 | Locking Moor Lane SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15636 | Bridport Pymore Village SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15681 | Weston-Super-Mare Railway Triangle SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15696 | Weymouth Lodmoor No 2 SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15707 | Crossways Dick O'The Banks (Pauls Way) SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15730 | Poole Albany Park SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15780 | Radstock Springfield Place SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15788 | Watchet Wansborough Paper Mill SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15794 | Bournemouth Green Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15799 | Amesbury Inside Park SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
15802 | Bowerhill Lodge Farm SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17248 | Bridport Old Convent SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17594 | Avonmouth Access 18 Kings Weston Lane Station 1 SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17658 | Falfield Eastwood Park Hm Prison SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17841 | Charfield New Street SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17843 | Warmley Tower Road North SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17844 | Trowbridge Riverway SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17846 | Bristol Wootton Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17848 | Potterne Devizes Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17959 | Upton Beach Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
17961 | Poole Foxholes Road SPS | - | - | - | - | - | 35.4824 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
18724 | Minety Flisteridge Malmesbury SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19034 | Edington Broadmead Lane SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19072 | Lower Langford Blackmoor Road Lower Langford SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19079 | Swanage The Tunnel High St SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19088 | Bushy Coombe - Glastonbury Glastonbury - Bushy Coombe SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19089 | Street Houndswood Drove SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19090 | Godney Godney Mendip SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19105 | Pensford Pensford Bridge SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19131 | Bridgwater Wills Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19298 | Melksham Savernake Ave SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19470 | Bath Kensington Storage (Pumped) SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19722 | Crossways Woodsford Road SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
19833 | West Wick Business Park Surface Water SPS | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## 371 Consented Sites
SiteTypeAbbrev | siteId | SiteName | SiteDescription | cstNo | 1st permit discharge | 2nd permit discharge
SPS | 13074 | COMBWICH | QUAY ROAD | 103336 | EMERGENCY OVERFLOW | SETTLED STORM OVERFLOW
SPS | 14075 | GLASTONBURY | NORTH LOAD BRIDGE | 102496 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 14076 | EVERCREECH | STONEY STRATTON | 103622 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 14110 | STOKE ST MICHAEL | STOKE HILL | 102699 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 14142 | MINETY | STATION ROAD | CSSA.2213 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 14147 | CHIPPENHAM | WESTMEAD | 100823 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 14248 | EAST BURTON | CROSS ROADS | 401422 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 14255 | STOBOROUGH | RIDGE | 401423 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 14475 | BROUGHTON GIFFORD | THE GREEN | 100634 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 14621 | PORTISHEAD | TOWN HARBOUR ROAD | 070308 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 15273 | POOLE | TURLIN MAIN BLANDFORD ROAD TURLIN MOOR | 400793 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 15290 | HENSTRIDGE | MARSH LANE (HENSTRIDGE NO 2) | 050882 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 15389 | PAWLETT | MAIN ROAD | 102689 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 15449 | MEARE GREEN | WRANTAGE | 070796 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 15461 | STOKE ST GREGORY | WOODHILL | 103188 | EMERGENCY OVERFLOW | STORM OVERFLOW
SPS | 14374 | HIGHBRIDGE | NEWTON | 102480 | SETTLED STORM OVERFLOW | STORM/EMERGENCY
SPS | 14097 | BALTONSBOROUGH | BALTONSBOROUGH MAIN | 103055 | STORM OVERFLOW | STORM/EMERGENCY
SPS | 13014 | AXBRIDGE | OLD STW SITE | 103918 | STORM/EMERGENCY
SPS | 13093 | DONIFORD | . | 101941 | STORM/EMERGENCY
SPS | 13153 | HOLTON HEATH | HOLTON HEATH SEWAGE PUMPING STATION | 041577 | STORM/EMERGENCY
SPS | 13265 | SHAPWICK | SOMERSET | 072077 | STORM/EMERGENCY
SPS | 13273 | SHIPTON GORGE | OFF MARKETS LANE | NPSWQD008206 | STORM/EMERGENCY
SPS | 13283 | SPAXTON | . | 070975 | STORM/EMERGENCY
SPS | 13334 | BRIDPORT | WEST BAY | 400678 | STORM/EMERGENCY
SPS | 13337 | WEST LULWORTH | HAMBURY FARM | 401815 | STORM/EMERGENCY
SPS | 13373 | PORLOCK | PORLOCK WEIR | 100353 | STORM/EMERGENCY
SPS | 13389 | BOSSINGTON | . | 100138 | STORM/EMERGENCY
SPS | 14002 | BATH | MIDLAND ROAD TWERTON | 102287 | STORM/EMERGENCY
SPS | 14016 | BRISTOL | ASHTON AVENUE | 102970 | STORM/EMERGENCY
SPS | 14020 | LOWER STANTON DREW | . | 012370 | STORM/EMERGENCY
SPS | 14046 | PEWSEY | SWAN | 401642 | STORM/EMERGENCY
SPS | 14047 | COATE | SPANIELS BRIDGE | NPSWQD008925 | STORM/EMERGENCY
SPS | 14049 | PEWSEY | WILCOT LODGE | NPSWQD003670 | STORM/EMERGENCY
SPS | 14050 | COLLINGBOURNE DUCIS | . | 401764 | STORM/EMERGENCY
SPS | 14055 | MARDEN | HIGH STREET | 402523 | STORM/EMERGENCY
SPS | 14057 | GREAT CHEVERELL | CHEVERELL GREEN | 021366 | STORM/EMERGENCY
SPS | 14058 | HORTON | HORTON FARM | 401149 | STORM/EMERGENCY
SPS | 14059 | ROWDE | TOWER VIEW | 103621 | STORM/EMERGENCY
SPS | 14064 | KINGSWOOD | WILLSBRIDGE | NPSWQD001439 | STORM/EMERGENCY
SPS | 14067 | BITTON | . | 010665 | STORM/EMERGENCY
SPS | 14069 | STREET | HOUNDWOOD DROVE | 103572 | STORM/EMERGENCY
SPS | 14072 | BLEADNEY | BLEADNEY MILL | 102371 | STORM/EMERGENCY
SPS | 14074 | SHEPTON MALLET | FOSSE LANE CHARLTON | 103573 | STORM/EMERGENCY
SPS | 14082 | STREET | MAIN | 100740 | STORM/EMERGENCY
SPS | 14083 | WEST PENNARD | HAVYATT | 102369 | STORM/EMERGENCY
SPS | 14084 | GLASTONBURY | ACTIS | 102497 | STORM/EMERGENCY
SPS | 14085 | COXLEY | COXLEY RIPPLE | 102367 | STORM/EMERGENCY
SPS | 14092 | GLASTONBURY | WELLS ROAD | 102377 | STORM/EMERGENCY
SPS | 14093 | WEST PENNARD | PAGE LANE | 103782 | STORM/EMERGENCY
SPS | 14095 | GLASTONBURY | PORCHESTALL | 071825 | STORM/EMERGENCY
SPS | 14096 | COXLEY | MILL LANE | 102834 | STORM/EMERGENCY
SPS | 14099 | STREET | WALTON GLOBE | 103783 | STORM/EMERGENCY
SPS | 14102 | KILMERSDON | . | 102698 | STORM/EMERGENCY
SPS | 14107 | WITHAM FRIARY | . | 102695 | STORM/EMERGENCY
SPS | 14108 | MELLS | . | 102696 | STORM/EMERGENCY
SPS | 14112 | WANSTROW | . | 102697 | STORM/EMERGENCY
SPS | 14113 | TRUDOXHILL | . | 102700 | STORM/EMERGENCY
SPS | 14114 | GLASTONBURY | EDGARLEY MILLFIELD SCHOOL | 102378 | STORM/EMERGENCY
SPS | 14116 | GURNEY SLADE | . | 101865 | STORM/EMERGENCY
SPS | 14120 | STREET | MIDDLE BROOKS ROAD | 100744 | STORM/EMERGENCY
SPS | 14125 | GILLINGHAM | BUCKINGHAM ROAD | 042428 | STORM/EMERGENCY
SPS | 14126 | SHROTON | . | 402122 | STORM/EMERGENCY
SPS | 14127 | GILLINGHAM | BRICKYARD LANE | 401128 | STORM/EMERGENCY
SPS | 14139 | CHRISTIAN MALFORD | SWALLETTS GATE | NPSWQD004959 | STORM/EMERGENCY
SPS | 14145 | MALMESBURY | TANNERS BRIDGE | 103784 | STORM/EMERGENCY
SPS | 14151 | DAUNTSEY | THE GREEN | 102280 | STORM/EMERGENCY
SPS | 14152 | BROADS GREEN | . | 101985 | STORM/EMERGENCY
SPS | 14157 | CALNE | ROUGH LEAZE | 101356 | STORM/EMERGENCY
SPS | 14158 | HULLAVINGTON | RAF STATION | 101678 | STORM/EMERGENCY
SPS | 14161 | COMPTON BASSETT | THE POND | 103449 | STORM/EMERGENCY
SPS | 14162 | MALMESBURY | BURTON HILL | 103660 | STORM/EMERGENCY
SPS | 14174 | BOX | MILL LANE | 011833 | STORM/EMERGENCY
SPS | 14176 | KINGTON LANGLEY | . | 101694 | STORM/EMERGENCY
SPS | 14179 | BIDDESTONE | MANOR COTTAGES | 102548 | STORM/EMERGENCY
SPS | 14185 | MALMESBURY | ST JOHNS STREET | 012855 | STORM/EMERGENCY
SPS | 14188 | LOWER STANTON ST QUINTIN | . | EPRAB3098VQ | STORM/EMERGENCY
SPS | 14196 | MALMESBURY | NOAHS ARK | 101696 | STORM/EMERGENCY
SPS | 14199 | UPPER MINETY | FLISTERIDGE | 102549 | STORM/EMERGENCY
SPS | 14200 | LEA | LEA NORTH | 101677 | STORM/EMERGENCY
SPS | 14216 | STOBOROUGH | KINGS ARMS | 401198 | STORM/EMERGENCY
SPS | 14219 | UPTON | SANDY LANE | 402036 | STORM/EMERGENCY
SPS | 14220 | LYTCHETT MATRAVERS | BULBURY LANE | 401452 | STORM/EMERGENCY
SPS | 14222 | EAST KNIGHTON | BLACKNOLL | 401166 | STORM/EMERGENCY
SPS | 14226 | CHURCH KNOWLE | GLEBE FARM | 401417 | STORM/EMERGENCY
SPS | 14227 | STUDLAND | WADMORE LANE | 401418 | STORM/EMERGENCY
SPS | 14229 | WAREHAM | WEST MILL CRESCENT | 401202 | STORM/EMERGENCY
SPS | 14232 | CHURCH KNOWLE | ANIMAL SANCTUARY | 401419 | STORM/EMERGENCY
SPS | 14235 | BOVINGTON | DUNCAN CRESCENT | 401420 | STORM/EMERGENCY
SPS | 14240 | BOVINGTON | MORRIS ROAD | 401421 | STORM/EMERGENCY
SPS | 14243 | MORDEN | COCK AND BOTTLE | 401197 | STORM/EMERGENCY
SPS | 14244 | SWANAGE | DURLSTON ROAD | 402252 | STORM/EMERGENCY
SPS | 14252 | STUDLAND | COOMBE | 401199 | STORM/EMERGENCY
SPS | 14256 | AFFPUDDLE | . | 401424 | STORM/EMERGENCY
SPS | 14259 | WAREHAM | SOUTH EAST | 402472 | STORM/EMERGENCY
SPS | 14260 | LYTCHETT MATRAVERS | GLEBE ROAD | 041152 | STORM/EMERGENCY
SPS | 14261 | STUDLAND | WATERY LANE | 041159 | STORM/EMERGENCY
SPS | 14263 | CORFE CASTLE | RED LANE | 401200 | STORM/EMERGENCY
SPS | 14264 | EAST KNIGHTON | . | 401425 | STORM/EMERGENCY
SPS | 14265 | UPTON | MOORLANDS WAY | 401241 | STORM/EMERGENCY
SPS | 14266 | WAREHAM | SANDFORD LANE | 401201 | STORM/EMERGENCY
SPS | 14270 | BOVINGTON | TERMINAL | 401426 | STORM/EMERGENCY
SPS | 14272 | BRIANTSPUDDLE | . | 041980 | STORM/EMERGENCY
SPS | 14273 | WOOL | RAILWAY COTTAGES | 401164 | STORM/EMERGENCY
SPS | 14274 | EAST CHALDON | . | 401427 | STORM/EMERGENCY
SPS | 14275 | CORFE CASTLE | HALVES COTTAGES | 401428 | STORM/EMERGENCY
SPS | 14276 | CORFE CASTLE | STUDLAND ROAD | 401429 | STORM/EMERGENCY
SPS | 14283 | BARTON ST DAVID | . | EPRCB3399AC | STORM/EMERGENCY
SPS | 14285 | MISTERTON | . | 103598 | STORM/EMERGENCY
SPS | 14286 | LOPEN | . | NPSWQD004020 | STORM/EMERGENCY
SPS | 14287 | HINTON ST GEORGE | . | 102398 | STORM/EMERGENCY
SPS | 14288 | MARSTON MAGNA | CHURCH LANE | 101772 | STORM/EMERGENCY
SPS | 14289 | ILCHESTER | ILCHESTER MAIN | 012884 | STORM/EMERGENCY
SPS | 14291 | WEST CAMEL | . | 101764 | STORM/EMERGENCY
SPS | 14293 | QUEEN CAMEL | ENGLANDS MEAD GREEN LANE | 071692 | STORM/EMERGENCY
SPS | 14294 | DONYATT | . | 102568 | STORM/EMERGENCY
SPS | 14295 | YEOVILTON | WEIR | 101765 | STORM/EMERGENCY
SPS | 14301 | STALBRIDGE | . | 050979 | STORM/EMERGENCY
SPS | 14302 | IDMISTON | . | 401574 | STORM/EMERGENCY
SPS | 14304 | ALLINGTON | OLD INN | 401580 | STORM/EMERGENCY
SPS | 14311 | TILSHEAD | CAMP ROAD | 401790 | STORM/EMERGENCY
SPS | 14317 | HURDCOTT | . | 401575 | STORM/EMERGENCY
SPS | 14323 | AMESBURY | FLOWER LANE | 401046 | STORM/EMERGENCY
SPS | 14337 | ALDERBURY | HOME FARM | 041885 | STORM/EMERGENCY
SPS | 14346 | HINDON | THE DENE | 042095 | STORM/EMERGENCY
SPS | 14354 | BARFORD ST MARTIN | . | 050763 | STORM/EMERGENCY
SPS | 14362 | CHILMARK | . | 041188 | STORM/EMERGENCY
SPS | 14368 | MERE | EDGEBRIDGE | 401447 | STORM/EMERGENCY
SPS | 14371 | CHEDDAR | FROGLANDS | 101665 | STORM/EMERGENCY
SPS | 14372 | WEST HUNTSPILL | SLOWAY LANE | 100880 | STORM/EMERGENCY
SPS | 14375 | PEDWELL | . | 102298 | STORM/EMERGENCY
SPS | 14378 | BRIDGWATER | BLAKE GARDENS | 102691 | STORM/EMERGENCY
SPS | 14379 | FIDDINGTON | . | 102215 | STORM/EMERGENCY
SPS | 14380 | NORTH NEWTON | CHURCH ROAD | 101802 | STORM/EMERGENCY
SPS | 14384 | BRIDGWATER | CHILTON STREET SALTLANDS | 102690 | STORM/EMERGENCY
SPS | 14385 | BRIDGWATER | BRISTOL ROAD | 082162 | STORM/EMERGENCY
SPS | 14386 | GREINTON | MOOR DRIVE | 102299 | STORM/EMERGENCY
SPS | 14388 | BERKELEY | PARK VIEW ROAD | 103822 | STORM/EMERGENCY
SPS | 14391 | STOKE ST GREGORY | NO 1 LANE END | 101803 | STORM/EMERGENCY
SPS | 14392 | WEST BUCKLAND | . | 101804 | STORM/EMERGENCY
SPS | 14394 | WELLINGTON | MITCHELLS POOL | 100238 | STORM/EMERGENCY
SPS | 14395 | HATCH BEAUCHAMP | . | 070916 | STORM/EMERGENCY
SPS | 14397 | BEER HACKETT | . | NPSWQD008609 | STORM/EMERGENCY
SPS | 14402 | OSMINGTON | PONTINS | 051316 | STORM/EMERGENCY
SPS | 14404 | BEAMINSTER | SOUTHGATE | 401557 | STORM/EMERGENCY
SPS | 14405 | WEST STAFFORD | DORCHESTER ROAD | 401967 | STORM/EMERGENCY
SPS | 14410 | BURTON BRADSTOCK | BURTON SOUTHOVER | 401968 | STORM/EMERGENCY
SPS | 14411 | SYDLING ST NICHOLAS | . | 401196 | STORM/EMERGENCY
SPS | 14413 | CHIDEOCK | SEATOWN | 043190 | STORM/EMERGENCY
SPS | 14414 | CHARMINSTER | NORTH STREET | 402447 | STORM/EMERGENCY
SPS | 14415 | LITTON CHENEY | CHICKSBRIDGE | 401592 | STORM/EMERGENCY
SPS | 14420 | MINEHEAD | QUAY WEST | 101776 | STORM/EMERGENCY
SPS | 14423 | BLUE ANCHOR | PILL BRIDGE | 102437 | STORM/EMERGENCY
SPS | 14425 | CLUTTON | GREENBROOK | 102915 | STORM/EMERGENCY
SPS | 14426 | PAULTON | GOOSARD BRIDGE | 102216 | STORM/EMERGENCY
SPS | 14427 | HALLATROW | . | 101867 | STORM/EMERGENCY
SPS | 14428 | CORSTON | NEWTON ST LOE | 010300 | STORM/EMERGENCY
SPS | 14429 | CHEW STOKE | BILBIE ROAD | 021523 | STORM/EMERGENCY
SPS | 14430 | CHEW MAGNA | DUMPERS LANE | 102223 | STORM/EMERGENCY
SPS | 14431 | BISHOP SUTTON | . | EPRZP3821GK | STORM/EMERGENCY
SPS | 14432 | COMPTON DANDO | TURNBRIDGE | 103604 | STORM/EMERGENCY
SPS | 14439 | WARMINSTER | CALVESWATER | 401094 | STORM/EMERGENCY
SPS | 14440 | DILTON MARSH | PEN KNAPP | 103205 | STORM/EMERGENCY
SPS | 14444 | WINGFIELD | CHURCH LANE | 102026 | STORM/EMERGENCY
SPS | 14447 | KEEVIL | THE STREET | 011447 | STORM/EMERGENCY
SPS | 14450 | COULSTON | . | 103785 | STORM/EMERGENCY
SPS | 14452 | FRESHFORD | NEW INN | 103786 | STORM/EMERGENCY
SPS | 14456 | BRATTON | TROWBRIDGE ROAD | 103243 | STORM/EMERGENCY
SPS | 14457 | BULKINGTON | WICKLEAZE | 011485 | STORM/EMERGENCY
SPS | 14458 | NORTH BRADLEY | CHURCHLANDS | 103244 | STORM/EMERGENCY
SPS | 14459 | SOUTHWICK | CHANTRY GARDENS | 021630 | STORM/EMERGENCY
SPS | 14462 | BROUGHTON GIFFORD | CURTIS ORCHARD | 100633 | STORM/EMERGENCY
SPS | 14466 | SEMINGTON | SEMINGTON BROOK | 102810 | STORM/EMERGENCY
SPS | 14467 | HOLT | THE STAR | 101024 | STORM/EMERGENCY
SPS | 14468 | MELKSHAM | SEMINGTON ROAD | 100635 | STORM/EMERGENCY
SPS | 14469 | GREAT HINTON | . | NPSWQD008924 | STORM/EMERGENCY
SPS | 14474 | MELKSHAM | SEMINGTON ROUNDABOUT | 100632 | STORM/EMERGENCY
SPS | 14502 | BRISTOL | WHITBY ROAD B CO-OP DEPOT ARNOS VALE | 021674 | STORM/EMERGENCY
SPS | 14507 | SHIREHAMPTON | LAMPLIGHTERS | 011540 | STORM/EMERGENCY
SPS | 14528 | CARLINGCOTT | STONEAGE LANE | 013269 | STORM/EMERGENCY
SPS | 14542 | COAT | CRIPPLE STREET (OLD STW SITE) | 071742 | STORM/EMERGENCY
SPS | 14550 | LACOCK | NETHERCOTE HILL | 010701 | STORM/EMERGENCY
SPS | 14562 | GLASTONBURY | WIRRAL PARK | 103823 | STORM/EMERGENCY
SPS | 14563 | FROME | COURTS BARTON MARSTON LANE | 102701 | STORM/EMERGENCY
SPS | 14580 | BRISTOL | ULLSWATER CLOSE | 103824 | STORM/EMERGENCY
SPS | 14581 | BRISTOL | VICTORIA ROAD | 012020 | STORM/EMERGENCY
SPS | 14583 | BRISTOL | WEST TOWN ROAD | 102067 | STORM/EMERGENCY
SPS | 14585 | EDINGTON | BROADMEAD LANE (SOM) | NPSWQD006726 | STORM/EMERGENCY
SPS | 14588 | WEST LULWORTH | LULWORTH OUTFALL PS | 401864 | STORM/EMERGENCY
SPS | 14620 | PEWSEY | SALISBURY ROAD | 041656 | STORM/EMERGENCY
SPS | 14624 | SALTFORD | MEAD LANE | 011904 | STORM/EMERGENCY
SPS | 14632 | TAUNTON | MAIDENBROOK | 070804 | STORM/EMERGENCY
SPS | 14648 | CHILTON POLDEN | MAIN | 072076 | STORM/EMERGENCY
SPS | 15002 | BOSCOMBE | NO 1 | 400551 | STORM/EMERGENCY
SPS | 15007 | BOURNEMOUTH | IFORD LANE TUCKTON | 401244 | STORM/EMERGENCY
SPS | 15013 | SOUTHBOURNE | HENGISTBURY HEAD | 400550 | STORM/EMERGENCY
SPS | 15019 | BOURNEMOUTH | NO 1 | 400758 | STORM/EMERGENCY
SPS | 15042 | BURTON | STONY LANE | 402473 | STORM/EMERGENCY
SPS | 15043 | MUDEFORD | MUDEFORD GARDENS | 401748 | STORM/EMERGENCY
SPS | 15047 | FERNDOWN | REDWOOD DRIVE | 400647 | STORM/EMERGENCY
SPS | 15048 | VERWOOD | ACACIA AVENUE | 400642 | STORM/EMERGENCY
SPS | 15051 | CORFE MULLEN | RUSHCOMBE BOTTOM | 401393 | STORM/EMERGENCY
SPS | 15052 | VERWOOD | EBBLAKE | 400643 | STORM/EMERGENCY
SPS | 15053 | FERNDOWN | GOLF LINKS ROAD | 401404 | STORM/EMERGENCY
SPS | 15057 | FERNDOWN | THAMES CLOSE | 401154 | STORM/EMERGENCY
SPS | 15060 | WEST MOORS | PENNINGTON COPSE | 400645 | STORM/EMERGENCY
SPS | 15068 | ST LEONARDS | WAYSIDE ROAD NO 1 | 402453 | STORM/EMERGENCY
SPS | 15070 | WIMBORNE | HAYES LANE COLEHILL | 401780 | STORM/EMERGENCY
SPS | 15071 | ST LEONARDS | CRAIGSIDE ROAD | 401243 | STORM/EMERGENCY
SPS | 15072 | FERNDOWN | AMEYSFORD ROAD | 400646 | STORM/EMERGENCY
SPS | 15073 | WIMBORNE | PILFORD HEATH | 042514 | STORM/EMERGENCY
SPS | 15075 | CORFE MULLEN | PARDYS HILL | 401392 | STORM/EMERGENCY
SPS | 15078 | FERNDOWN | A31 TRICKETTS CROSS | 401156 | STORM/EMERGENCY
SPS | 15079 | WIMBORNE | POOLE ROAD | 401624 | STORM/EMERGENCY
SPS | 15080 | FERNDOWN | DUGDELL CLOSE | 400649 | STORM/EMERGENCY
SPS | 15082 | WIMBORNE | BROOK ROAD NO 1 | 401779 | STORM/EMERGENCY
SPS | 15083 | ST LEONARDS | FOREST EDGE DRIVE | 402454 | STORM/EMERGENCY
SPS | 15084 | VERWOOD | POTTERNE WAY | 401155 | STORM/EMERGENCY
SPS | 15090 | WEST PARLEY | CHURCH LANE | 401157 | STORM/EMERGENCY
SPS | 15091 | FERNDOWN | ALDRIDGE ROAD | 400641 | STORM/EMERGENCY
SPS | 15100 | NORTH NEWNTON | . | 402067 | STORM/EMERGENCY
SPS | 15101 | PATNEY | PATNEY WEIR | 401225 | STORM/EMERGENCY
SPS | 15106 | POULSHOT | TOWNSEND | 102478 | STORM/EMERGENCY
SPS | 15111 | ALL CANNINGS | . | 401226 | STORM/EMERGENCY
SPS | 15115 | CHIRTON | SMALL STREET | 401765 | STORM/EMERGENCY
SPS | 15117 | DEVIZES | DUNKIRK HILL | 101767 | STORM/EMERGENCY
SPS | 15123 | SEEND | BELL INN / BELL HILL | 102808 | STORM/EMERGENCY
SPS | 15125 | WORTON | MILL ROAD | 102479 | STORM/EMERGENCY
SPS | 15129 | POTTERNE | WICK | 101814 | STORM/EMERGENCY
SPS | 15139 | PILNING | SWANMOOR BRIDGE | 101958 | STORM/EMERGENCY
SPS | 15158 | OLVESTON | THE COMMON | 101837 | STORM/EMERGENCY
SPS | 15166 | RANGEWORTHY | BERROWS MEAD | 103233 | STORM/EMERGENCY
SPS | 15167 | CROMHALL | JUBILEE LANE | 103286 | STORM/EMERGENCY
SPS | 15188 | YATE | NORTH ROAD | 101589 | STORM/EMERGENCY
SPS | 15189 | AUST | VILLAGE | 010692 | STORM/EMERGENCY
SPS | 15190 | MILBORNE ST ANDREW | MANOR FARM | 042113 | STORM/EMERGENCY
SPS | 15193 | CHILD OKEFORD | GOLD HILL | 402218 | STORM/EMERGENCY
SPS | 15196 | STURMINSTER NEWTON | THE BRIDGE | 402224 | STORM/EMERGENCY
SPS | 15200 | MARNHULL | SODOM LANE | 402474 | STORM/EMERGENCY
SPS | 15201 | DURWESTON | WATER LANE | 402475 | STORM/EMERGENCY
SPS | 15203 | SHILLINGSTONE | HAYWARDS BRIDGE | 402500 | STORM/EMERGENCY
SPS | 15205 | BLANDFORD ST MARY | BOURNEMOUTH ROAD | 402254 | STORM/EMERGENCY
SPS | 15206 | BLANDFORD | LANGTON ROAD (BLANDFORD NO 1) | 401302 | STORM/EMERGENCY
SPS | 15207 | SHAFTESBURY | LONG CROSS | 401300 | STORM/EMERGENCY
SPS | 15209 | SPETISBURY | CRAWFORD BRIDGE | 402313 | STORM/EMERGENCY
SPS | 15230 | POOLE | KENNART ROAD | EPRQB3993NE | STORM/EMERGENCY
SPS | 15231 | POOLE | SANDBANKS PAVILION | 051303 | STORM/EMERGENCY
SPS | 15235 | POOLE | SHORE ROAD | 051290 | STORM/EMERGENCY
SPS | 15236 | POOLE | CANFORD HEATH ROAD | 401619 | STORM/EMERGENCY
SPS | 15237 | POOLE | MAGNA ROAD | 400714 | STORM/EMERGENCY
SPS | 15240 | POOLE | BRANKSOME CHINE | NPSWQD003865 | STORM/EMERGENCY
SPS | 15243 | BRIDGWATER | EAST QUAY | 071343 | STORM/EMERGENCY
SPS | 15246 | CANFORD MAGNA | CANFORD MAIN | 040821 | STORM/EMERGENCY
SPS | 15252 | POOLE | EGMONT ROAD | 402037 | STORM/EMERGENCY
SPS | 15253 | POOLE | FAIRVIEW ROAD | 401394 | STORM/EMERGENCY
SPS | 15257 | POOLE | POOLE BRIDGE POOLE QUAY | 400719 | STORM/EMERGENCY
SPS | 15270 | POOLE | CREEKMOOR LANE | 401047 | STORM/EMERGENCY
SPS | 15275 | POOLE | HEWITT ROAD | 402038 | STORM/EMERGENCY
SPS | 15277 | POOLE | WOOD LANE | 401257 | STORM/EMERGENCY
SPS | 15278 | LONG SUTTON | BENNETTS ORCHARD | 102399 | STORM/EMERGENCY
SPS | 15282 | BRADFORD ABBAS | MILL LANE | 101782 | STORM/EMERGENCY
SPS | 15283 | WINCANTON | BAYFORD | 402455 | STORM/EMERGENCY
SPS | 15284 | HUISH EPISCOPI | WAGG DROVE | 071164 | STORM/EMERGENCY
SPS | 15297 | DRAYTON | DUCKS LANE | 102400 | STORM/EMERGENCY
SPS | 15298 | LIMINGTON | MAIN | 102569 | STORM/EMERGENCY
SPS | 15299 | KINGSDON | . | 101845 | STORM/EMERGENCY
SPS | 15304 | WEST CHINNOCK | GARAGE | 103720 | STORM/EMERGENCY
SPS | 15306 | LOWER SOMERTON | . | 102063 | STORM/EMERGENCY
SPS | 15309 | CHARLTON MACKERELL | ROOKERY FARM | 102064 | STORM/EMERGENCY
SPS | 15310 | ALLER | . | 071143 | STORM/EMERGENCY
SPS | 15311 | YEOVIL | MUDFORD | NPSWQD003764 | STORM/EMERGENCY
SPS | 15313 | HUISH EPISCOPI | PIBSBURY | 071157 | STORM/EMERGENCY
SPS | 15314 | UPTON | NR LANGPORT | 102405 | STORM/EMERGENCY
SPS | 15315 | HUISH EPISCOPI | WAGG BRIDGE | 071163 | STORM/EMERGENCY
SPS | 15316 | BARTON ST DAVID | TOOTLE BRIDGE | 103177 | STORM/EMERGENCY
SPS | 15317 | NORTON SUB HAMDON | . | 103178 | STORM/EMERGENCY
SPS | 15320 | LONG SUTTON | KNOLE | 103179 | STORM/EMERGENCY
SPS | 15322 | PITNEY | . | 103180 | STORM/EMERGENCY
SPS | 15325 | KEINTON MANDEVILLE | . | 103181 | STORM/EMERGENCY
SPS | 15327 | ILMINSTER | LORD NELSON | 102397 | STORM/EMERGENCY
SPS | 15331 | SHEPTON BEAUCHAMP | . | 102005 | STORM/EMERGENCY
SPS | 15333 | PENSELWOOD | PENN MILL | 402000 | STORM/EMERGENCY
SPS | 15334 | CHARLTON ADAM | . | 101604 | STORM/EMERGENCY
SPS | 15339 | TEMPLECOMBE | SLADES HILL | 401653 | STORM/EMERGENCY
SPS | 15371 | CROSS | CROSS EAST | 101667 | STORM/EMERGENCY
SPS | 15378 | PAWLETT | VICARAGE LANE | 101710 | STORM/EMERGENCY
SPS | 15381 | WEMBDON | COMMON | 102688 | STORM/EMERGENCY
SPS | 15383 | POOLE | EAST QUAY PERRY GARDENS | NPSWQD007062 | STORM/EMERGENCY
SPS | 15388 | OTHERY | RYE LANE/ SUMMERHEDGE ROAD | 101715 | STORM/EMERGENCY
SPS | 15391 | WESTONZOYLAND | HAMROD LANE | 101712 | STORM/EMERGENCY
SPS | 15393 | BRIDGWATER | TAUNTON ROAD | 102692 | STORM/EMERGENCY
SPS | 15394 | SUTTON MALLET | . | 101687 | STORM/EMERGENCY
SPS | 15396 | WOOLAVINGTON | MEADOW FARM | 101713 | STORM/EMERGENCY
SPS | 15397 | STAWELL | FORD LANE | 101711 | STORM/EMERGENCY
SPS | 15400 | BRIDGWATER | WEST QUAY DRAWBRIDGE | 102693 | STORM/EMERGENCY
SPS | 15402 | MIDDLEZOY | NETHERMOOR ROAD | 101686 | STORM/EMERGENCY
SPS | 15414 | BRISTOL | CENTRAL TRADING ESTATE BATH ROAD | 021635 | STORM/EMERGENCY
SPS | 15415 | BRIDGWATER | COLLEY LANE | 071342 | STORM/EMERGENCY
SPS | 15435 | BATHPOOL | HYDE LANE | 103186 | STORM/EMERGENCY
SPS | 15436 | RUISHTON | BARTON LANE | NPSWQD001438 | STORM/EMERGENCY
SPS | 15439 | HENLADE | . | NPSWQD001440 | STORM/EMERGENCY
SPS | 15440 | NORTH CURRY | MAIN | 101806 | STORM/EMERGENCY
SPS | 15446 | HILLCOMMON | HILL COMMON | NPSWQD003671 | STORM/EMERGENCY
SPS | 15448 | TAUNTON | LONGACRE CLOSE | 103187 | STORM/EMERGENCY
SPS | 15450 | NORTON FITZWARREN | LANGFORD LANE | 101807 | STORM/EMERGENCY
SPS | 15454 | CREECH ST MICHAEL | NORTH END | 102019 | STORM/EMERGENCY
SPS | 15457 | WELLINGTON | WESTFORD | 100532/PC/01 | STORM/EMERGENCY
SPS | 15458 | STOKE ST GREGORY | CURLOAD | 102570 | STORM/EMERGENCY
SPS | 15459 | RUMWELL | . | 082085 | STORM/EMERGENCY
SPS | 15460 | MEARE GREEN | STOKE ST GREGORY | 070896 | STORM/EMERGENCY
SPS | 15463 | BRADFORD ON TONE | TONE GREEN | 103189 | STORM/EMERGENCY
SPS | 15465 | NORTH CURRY | STOKE ROAD | 103190 | STORM/EMERGENCY
SPS | 15467 | NAILSBOURNE | . | 103191 | STORM/EMERGENCY
SPS | 15468 | BRADFORD ON TONE | HOCKHOLLER A38 | 070798 | STORM/EMERGENCY
SPS | 15469 | LEIGH | FRAMPTON FARM | 102977 | STORM/EMERGENCY
SPS | 15481 | BRADPOLE | LEE LANE | 402029 | STORM/EMERGENCY
SPS | 15486 | WEST BEXINGTON | . | 041125 | STORM/EMERGENCY
SPS | 15494 | ABBOTSBURY | CHURCH STREET | 401866 | STORM/EMERGENCY
SPS | 15495 | NETHERBURY | BEAMINSTER | 402106 | STORM/EMERGENCY
SPS | 15496 | LEIGH | BRIDGE FARM | 102978 | STORM/EMERGENCY
SPS | 15500 | BRADPOLE | FISHWEIR FOUL | 402030 | STORM/EMERGENCY
SPS | 15505 | SYMONDSBURY | WEST ROAD FOUNDRY | 402031 | STORM/EMERGENCY
SPS | 15507 | BRIDPORT | WEST BAY SLUICES | 402047 | STORM/EMERGENCY
SPS | 15508 | WOOTTON COURTENAY | . | 102300 | STORM/EMERGENCY
SPS | 15511 | MONKSILVER | B3188 | 102301 | STORM/EMERGENCY
SPS | 15516 | BILBROOK | . | 101656 | STORM/EMERGENCY
SPS | 15519 | WATCHET | MARKET STREET (TUNNEL) | 101270 | STORM/EMERGENCY
SPS | 15523 | CAMERTON | SUNNYVALE | 021687 | STORM/EMERGENCY
SPS | 15527 | DUNKERTON | BROOKLANDS | 021688 | STORM/EMERGENCY
SPS | 15535 | PEASEDOWN ST JOHN | NEW BUILDINGS / WHITEBROOK LANE | 103600 | STORM/EMERGENCY
SPS | 15536 | WELLOW | MILL HILL | 103601 | STORM/EMERGENCY
SPS | 15537 | SHOSCOMBE | SINGLE HILL | 021446 | STORM/EMERGENCY
SPS | 15541 | KEYNSHAM | THE HAMS | 013093 | STORM/EMERGENCY
SPS | 15542 | KEYNSHAM | KEYNSHAM HIGH LEVEL | 102126 | STORM/EMERGENCY
SPS | 15548 | KEYNSHAM | KEYNSHAM LOW LEVEL | 102124 | STORM/EMERGENCY
SPS | 15552 | WEYMOUTH | KNIGHTSDALE NEWSTEAD ROAD | 400892 | STORM/EMERGENCY
SPS | 15555 | WYKE REGIS | HILLCREST ROAD | 402476 | STORM/EMERGENCY
SPS | 15556 | WEYMOUTH | RADIPOLE | 401048 | STORM/EMERGENCY
SPS | 15559 | PORTLAND | PENNSYLVANIA ROAD | 402253 | STORM/EMERGENCY
SPS | 15561 | WEYMOUTH | FERRYBRIDGE PORTLAND ROAD | 402477 | STORM/EMERGENCY
SPS | 15569 | PORTBURY | DROVE | 070828 | STORM/EMERGENCY
SPS | 15572 | LOCKING | LOCKING VILLAGE | 100524/PC/01 | STORM/EMERGENCY
SPS | 15573 | BLEADON | PURN | 101663 | STORM/EMERGENCY
SPS | 15574 | SANDFORD BATCH | . | 103602 | STORM/EMERGENCY
SPS | 15577 | SANDFORD | SANDMEAD LANE | 103173 | STORM/EMERGENCY
SPS | 15580 | LANGFORD | BLACKMOOR ROAD | 012883 | STORM/EMERGENCY
SPS | 15606 | CLEVEDON | THE BEACH | 100767 | STORM/EMERGENCY
SPS | 15621 | CLEVEDON | LADYE BAY | 102489 | STORM/EMERGENCY
SPS | 15622 | CLEVEDON | MARINE PARADE | 071176 | STORM/EMERGENCY
SPS | 15627 | ILTON | FROST LANE | 070693 | STORM/EMERGENCY
SPS | 15630 | CHICKERELL | LOWER WAY | EPRCB3990NR | STORM/EMERGENCY
SPS | 15644 | SUTTON WALDRON | . | 041782 | STORM/EMERGENCY
SPS | 15645 | PILL | AVON ROAD | 011673 | STORM/EMERGENCY
SPS | 15648 | PORTLAND | PORTLAND BILL | 402219 | STORM/EMERGENCY
SPS | 15673 | PORTLAND | SOUTHWELL | 040686 | STORM/EMERGENCY
SPS | 15680 | PORTISHEAD | BLACK NORE (NAUTICAL SCHOOL) | 071587 | STORM/EMERGENCY
SPS | 15715 | BRIDGWATER | HORSEY BATH ROAD | 101841 | STORM/EMERGENCY
SPS | 15718 | BISHOPS HULL | SHUTEMEAD | EPR/JB3795EQ | STORM/EMERGENCY
SPS | 15723 | TETBURY | SPRINGFIELDS | 103899 | STORM/EMERGENCY
SPS | 15726 | PORTISHEAD | LAKE GROUNDS | 101909 | STORM/EMERGENCY
SPS | 15772 | PEASEDOWN ST JOHN | WELLOW LANE | 103787 | STORM/EMERGENCY
SPS | 17027 | SOUTH CADBURY | . | 102161 | STORM/EMERGENCY
SPS | 17175 | PURITON | DOWNEND TERRACE | 102773 | STORM/EMERGENCY
SPS | 18718 | CHAPMANSLADE | DIVERS BRIDGE | 010613 | STORM/EMERGENCY
SPS | 19035 | KINGSBURY EPISCOPI | . | 013464 | STORM/EMERGENCY
SPS | 19056 | WEYMOUTH | CASTLE COVE OLD CASTLE ROAD WYKE REGIS | EPRAP3923KW | STORM/EMERGENCY
SPS | 19699 | BOVINGTON | LYTCHETT LANE | 401064 | STORM/EMERGENCY
SPS | 19731 | HARMANS CROSS | TRANSFER STATION | 401237 | STORM/EMERGENCY
SPS | 19787 | STOUR ROW | . | 401115 | STORM/EMERGENCY
SPS | 19817 | SANDFORD ORCAS | . | 102522 | STORM/EMERGENCY
SPS | 19978 | ROOKSBRIDGE | BRISTOL ROAD | 101956 | STORM/EMERGENCY

## Flow_4
Site ID | tmp | Treatment / SPS owned site | Division | Pass forward monitor sites (Flow4) | Regulatory completion date | 2014 Survey results (l/s) | Consented PFF (l/s) | PFF (Pre-July 19) (l/s) | Jul 19 - PFF (l/s) | Date | Sept 19 - PFF (l/s) | Date2 | Dec 19 - PFF (l/s) | Date3 | Jan / Feb 20 PFF (l/s) | Date of last site maintenance (WAM) | Any history of changing pumps or impellers in reactive history (WAM)? | Any history of changing pumps or impellers in reactive history (WAM)? SPECIFICALLY TO ASSSET - DWF PUMPS | Date of last AV maintenance (WAM) | AV maintenance comments (WAM) | Date of pump install (Site Info File) | Actions (Set on: 10/12/19)
14413 | 14413 | SPS | S | Chideock Seatown | 2020-03-31 | 7 | 9 | 5 | 5.96l/s. But it reguarly peaks at about 8l/s. | 4371700% | 8 | 4382000% | 7 | 4386300% | 6.9 | 4352300% | N/A | N/A | 4280800% | No Comments (930957) Tim Whitehead | WET WELL 1,2; 1997. | Find pump curves. RG to ask for 1 minute data, check contractor maintenance feedback from Feb-19, request maintenance - lift pumps, update asset data, check NRVs, Fred to speak to Nigel about pump/impellor change
14252 | 14252 | SPS | S | Coombe PS, Studland | 2020-03-31 | 5 – 8 | 16 | 8 | unsure | 4373700% | 9 | 4381400% | 9 | 4384400% | 9 | 4362100% | NEW IMPELLER IS REQUIRED (22/07/2019) | N/A | N/A | No sched. Set up In Hansen | WET WELL 1; 1998. WET WELL 2; 2011. | Data looks like pumpd block. New impellers were required. P2 particularly poor performance - new pump fitted 08/08/19?? NO ASSET DATA. Check maintenance/if impellers were changed. Check if changed to N type. Carry out wet well clean, followed by mainteance and check pumps/impellers/NRVs, update asset details. NR spoke to Fred, getting quote from Flygts
15257 | 15257 | SPS | S | Poole Bridge Pumping Station | 2017-05-01 | 12 | 15 | 12 | unsure | 4373700% | 11 | 4380000% | 14.6 | 4385200% | 14 | 4330400% | N/A | N/A | N/A | No sched. Set up In Hansen | SUBMERSIBLE PUMP 1,2; 2012 | NR request outstanding planned maintenance is completed (this is being done 13/12/19) - lift pumps, check impellers etc.
14216 | 14216 | SPS | S | Stoborough Kings Arms | 2017-05-01 | 12 | 15 | 13 | 0 l/s (trend - 0 - 15l/s steady) | 4373700% | 15 | 4382000% | 14 | 4384600% | 14.7 | 4324400% | 27/06/2019 (1467509) - Fitted 2 x n pump kits and 2 x lifting handles 29th May, Fitted 2 x lifting chains 27th June. - RAISED TO SITE | N/A | 4312200% | 22/01/2018 - (1140107) JOB WAS MARKED AS COMPLETE WITH THE COMMENTS "Unable to find Valve. Found burst riser" | WET WELL SUBMERSIBLE 1,2; 1990 | OK no action
14420 | 14420 | SPS | W | Quay West, Minehead PS | 2020-03-31 | 15 | 14 | 7 (did not spill) | ERROR MESSAGE ('sorry, could not find mimic WASTE MINEHEAD QUAY WEST SPS') | 4371700% | 15 |  |  |  |  | 4355800% | fit new guide rails and imepllers now all okay 03/04/2019 (1389424) attend site to complete maint p1 blocked l/s and pump came away from guide rails as rotton impellor very worn will order replacement impellor and S/S guide rails for both pumps check both nrvs all ok update asset info 23/02/2017 (930917) P1 needs new impellers and N type kat p2 means new 7 meter lifting chain will raise job for three man entry. Unable to input meter reading which is. 94184 v0340 i02d02573 () fit new guide rails and imepllers now all okay | N/A | N/A | N/A - no sched. Set up In Hansen | WET WELL 1; 2013. WET WELL 2; 2014. | OK no action
15393 | 15393 | SPS | W | Bridgwater Taunton Road | 2017-03-31 | 50 | 70 | 62 – 70 | 19.55l/s. Peaks never go above 60l/s. In stormy conditions reach approx. 61l/s. | 4373700% | 59 | 4384000% | 67 | 4387000% | 66 | 4351000% | (16/03/2018 - 1185344) Collect hire pump with trailer from Chilton and install at site (09/05/2018 - 1215637) lifted and unblocked p2 storm pump. rag removed. mixer p1 lifted and impellor was off. replaced bolt, however still tripping. found windings imbalanced removed for repair. | N/A | N/A | No sched. Set up In Hansen | BOOSTER PUMP 1 1992 Estimated, DRY WELL STORM PUMP 1 1971, DRY WELL STORM PUMP 2 1971, DRY WELL STORM PUMP 3 1971, SUMP PUMP 1 1981 Estimated. | Capital maintenance (AMP6) - Planned Project takeover 1/10/19 C9924 - tasked with achieving the 70 l/s consent Investigate possible scale-up of impeller size
14372 | 14372 | SPS | W | Sloway Lane SPS, Huntspill | 2017-03-31 | 102-110 | 130 | 110 | 0.28 l/s. Usually peaks at 80l/s, but occasionally 98l/s. Weekly trend suggests it is not affected by stormy conditions. | 4362300% | 90 | 4383900% | 100 | 09/01/2020 (STW side) | 114 | 4350300% | 17/10/2017 (1086948) Install repaired p2 as per Apratt | 17/10/2017 (1086948) Install repaired p2 as per Apratt | n/a - no schedule in Hansen | No sched. Set up In Hansen | DRY WELL PUMP 1 ¦ SUBMERSIBLE 1, 2, 3; 2000. STORM PUMP ¦ DRY WELL 1, 2, 3; 2000. | Nominated scheme C9988 - due to start on site in 2020. Mark Chalk speaking to David Martin 13/12/19 about whether we can change pumps/NRVs earlier. NR - increased top wet well clean to 1 monthly frequency. Looking to increase the stop levels by 200mm to reduce air locking.
15400 | 15400 | SPS | W | Bridgwater, West Quay SPS | 2018-05-01 | 186 | 206 | 90 | 0.56l/s 30/07/19 reached 220l/s, in the week it is consistantly under 100l/s | 4373700% | 165 | 4381400% | 190 | 4383900% | 198 | 4330700% | 17/02/2017 (928890) l/s/u p3 and fit new impellers to p1 and 2 test all ok unable to fit new inserts unable to remove old ones | N/A | 4362100% | serviced air valves at site and emailed ashley and richard | DRY WELL PUMP 1,2,3,; 2013. STORM RETURN; 2014. STORM TANK MIXER 1,2; 2018. SUMP 1990. BOOSTER 1992. | Impellers changed, now achieving PFF
14374 | 14374 | Treatment | W | Highbridge SPS SSO (CSO) | 2016-03-31 | 254 | 300 | 310 | 100.92l/s. Pattern is constantly between 175l/s-40l/s. In stormy conditions the peaks reached 310l/s. | 4373700% | 300 |  |  |  |  | 27/07/2017 - 02/11/2018 WEEKLY MAINTENANCE | N/A | N/A | N/A | No sched. Set up In Hansen | BOXED SPARE PUMP, SUMP PUMP 1, TIDAL PUMP; 2016 | OK no action
14416 | 14416 | Treatment | W | Mart Road PS, Minehead | 2020-03-31 | n/a | 236 | 400 | unsure | 4373700% | 450 |  |  |  |  | 31/07/2019 Site Maintenance-Weekly-W 09/07/2019 Site Maintenance-Monthly | 17/04/2019 (1423611) pump removed and sent to workshop for repair 15/08/2014 (539523) installed refurbed dwf pump 17/09/2013 (422021) sump pump u/s removed and order replacement. follow on 422087 04/07/2013 (363738)Storm pump removed for delivery to Avonmouth for repair. Asset condition grade >= 3 comments: Mechanical seal leaking, removed to Avonmouth for repair 26/11/2012 (308095) Pump returnrd to Avonmouth for repair 06/04/2010 (16474)Replaced DWF pump 1 overload | 17/07/2019 (1464027 - Storm Pump / DRY WELL) storm pump, ok showing sign of life. known upgrade happening soon. 09/07/2018 (1251273 - storm/ dry well) Replaced dwf pump with repair from workshop. 01/06/2018 (1231906- DWF FOUL P1) Tested and checked operation of pump. Job requested by Jae Stone. 26/11/2012 (308095 - storm pump - dry well) Pump to be removed for refurb. Pump returnrd to Avonmouth for repair. 22/02/2012 (205304) 06/04/2010 (16474) Repaired pump fitted and tested ok. Replaced DWF pump 1 overload | N/A | No sched. Set up In Hansen | DWF FOUL PUMP 1,2; 2003. | OK no action
15553 | 15553 | Treatment | S | Victoria Square PS | 2020-03-31 | 442 | 480 | 480 | 0.0l/s. peaks regularly at 353l/s. stormy weather it peaked at 340l/s. | 4373700% | 460 | 4380800% | 430 |  |  | 06/08/2019 - 15553-Site Maintenance-Weekly-T | N/A | N/A | 4356000% | Air valve in good working order (1075300) | CONDITIONING PUMP, STORM PUMP, WASHWATER; 2007. NITRATE DOSING 1,2; 2005. STORM WATER 1,2;1986. | Pump is capable of delivering PFF but turned Variable speed drives 14 April 2019 - telemetry changed from 1 min to 5 min archiving Plans to safely remove pumps from well + refurbishment plans. Pass to Treatment RG: Email Bill for query
15244 | 15244 | SPS | S | Elgin Road PS overflow | 2017-05-01 | 604 | 850 | 600 | 242.00 l/s. Normally peaks approx. 310l/s, and in stormy conditions it did not go above 390l/s. | 4362300% | 570 | 4381100% | 600 |  |  | 2019-02-27 | 02/07/2019 (1467553) pump 1 installed and tested ok. (1394775) 27/02/2019 Flygt temporary pump installed. 20/01/2019 (1373855) All works completed, Pump 4 needs to be removed for repair. 27/12/2018 (1350222) pump is out ready for collection. 15/06/2018 (1231929) pump replaced. 30/08/2016 (854043) new pump installed and run up. 04/02/2019 (1382536) trimmed p2 impeller, p3 jacking bolt seized, 31/05/2018 (1173327) Lifted and checked impellor and wear plate. | 02/07/2019 (1467553) pump 1 installed and tested ok. 27/02/2019 (1394778)Temporary Flygt installed/Pump is awaiting repair. 04/07/2017 (937932) Sump pump replaced and pump adjusted. 05/07/2017 (937929) Replaced all ok - DRY WELL PUMP NO 1. 30/08/2016 (854043) new pump installed and run up - DRY WELL PUMP NO 2 | N/A | NSD 28/12/19 in Hansen | DRY WELL PUMP 1,2,3,4,N/A. SUMP PUMP;2004. NITRATE PUMP 2011. | Re-doing pump station CM338 Maintenance or Replacement of Existing Non-Infrastructure assets Mark Harris + Cliff to confirm surge vessel and scheme approval
15556 | 15556 | Treatment | S | Radipole Lake PS, Weymouth | 2020-03-31 | n/a | 2200 | 450 + 1700= 2150 | 290l/s peaks, storm weather raising to 470l/s ish + 1100l/s consistant peaks. | 4362300% | 1870 | 4381400% | 2080 |  |  | 15556-Site Maintenance-Weekly-Th - 01/08/2019 | N/A | N/A | 4362800% | Not a SPS assett. (1034921) - Tim Whitehead {SCHEDULE STILL SET UP IN HANSEN} | DWF 1,2;2003. Grit pump, WASHWATER; 2003. dosing 1,2;2012. Storm 1, 3, sump;2003. Storm2;1998. | Pump's currently being maintained? K Grit Clean Out starting on 13/1/20 Pass to Treatment
14219 | 14219 | SPS | S | Upton – Sandy Lane SPS | 2017-05-01 | 7 | 6 | 8 | 0.0l/s reaches peak 8.5 l/s in trend, other peaks only 7.5 l/s - Commonly goes over 8l/s | 4366700% | 9 | 4381900% | 8.3 |  |  | 2018-08-24 | N/A | N/A | N/A | No sched. Set up In Hansen | WET WELL SUBMERSIBLE 1,2; 1992 | OK no action
15507 | 15507 | SPS | S | West Bay Sluices PS, Bridport | 2020-03-31 | 2019-10-06 | 9 | 12 | 0.01l/s. It regualary peaks 10-11.5l/s. 30/07/19 a single peaked reached 15.5l/s, and another peak 13l/s. The rest were not above consent. | 4371700% | 18 | 4382500% | 15 |  |  | 4353100% | (1457075) 29/05/2019- Impellor, wear plate, guide rails fitted for pump 1 on 21.05.19, Impellor, wear plate, guide rails fitted for pump 2 on 29.05.19, (943305) 23/03/2017 fit new impella and valute to stom pump | N/A | N/A | No sched. Set up In Hansen | STORM RETURN, 2006. WET WELL PUMP 1; 2013. | OK no action
14423 | 14423 | SPS | W | Blue Anchor PS | 2020-03-31 | 28 | 18 | 30 | 0.01 l/s. - in the weekly trend 16.5l/s- 23l/s | 4371700% | 21 | 4381700% | 27 |  |  | 4358100% | 10/07/2019 (1469977) - fitted new impeller and insert to pump 1 tested | 10/07/2019 - (1469977) fitted new impeller and insert to pump 1 tested | 4302400% | maintenance complete (926188) | NO DATES LISTED | OK no action
15007 | 15007 | SPS | S | Iford Lane Tuckton | 2020-03-31 | 45 | 65 | 60 | 48.38l/s. Peaked at 56l/s consistently (in the weekly trend, incuding during the stormy conditions 30/07/19) | 4373700% | 70 | 4382500% | 70 |  |  | 18/03/2019 -'completed by contrators last month' | 06/06/2017 (980079) replace impellors and wear rings on p1 and p2 | 10/08/2017 (1042124 -Dry Well P2) replaced pump with new temp now out and Fred has off hired it. 06/06/2017 (980079) replace impellors and wear rings on p1 and p2 | N/A | No sched. Set up In Hansen | DRY WELL 1,2;2002. STORM PUMP 1; 1995. | Run-stops not working, job raised for Kieran 16/12/19. Also, wet well clean is overdue, requested from Celvac (Rescue team needed) 1min Archiving request for flow, pressure and well level
15551 | 15551 | SPS | S | Fisherbridge PS, Weymouth | 2020-03-31 | 115 | n/a | 118 | 0.08l/s. During stormy conditions on 30/07/19 it peaked at 110l/s. weekly trend shows normal peaks between 60-70l/s | 4373700% | 112 | 4381400% | 122 |  |  | 4363000% | 11/07/2019 (1466348) earth fault pump removed hire to be ordered fred liam dealing with. 28/03/2017 (951807)remove hire install new pump broke down await for aa | N/A | NONE | THERE IS A SCHEDULE SET UP IN HANSEN NSD 27/01/2020 BUT NO RECOR | DRY WELL PUMP 1,2,3; 2003. WET WELL PUMP 1,2,3;2002. | No PFF requirement - assessment of DWF into station: 1025 m3/day versus consent of less than 1728 m3/day Currently being investigated by Dave Searby within CM308 Project 1 Spill in 2 years
15270 | 15270 | SPS | S | Creekmore Lane, Poole | 2020-03-31 | n/a | 120 | 120 (did not spill) | 6.08l/s. peaks roughly 120l/s. (Never over 120.75l/s). Does not seem to be affected by stormy conditions. | 4366900% | 120 | 4417400% | 125 |  |  | 4337700% | 25/10/2016 (879722) have taken delivery of hire pump, have stored it in the RSPS cage at Poole StwAsset condition grade >= 3 comments: pump 1 is faulty, hire pump is now ready for it. p1 is being taken out on thursday and sent to flygts axminster for repair, and temporarily replaced with hire pump (WET WELL) | N/A | N/A | No sched. Set up In Hansen | WET WELL PUMP 1,2; 2003 | Request flow signal to 1min archiving
15383 | 15383 | SPS | S | East Quay SPS, Perry Gardens, Poole | 2020-03-31 | n/a | 202 | 160 (did not spill) | 0.18l/s. Trendview - peaks reach 120-130l/s, including in stormy weather. | 4373700% | 130 | 4383900% | 210 |  |  | 2019-06-03 | 21/09/2017 (1061006) replaced new sump pump will need new hose tail as leaking will ask Fred for new. 17/03/2016 (788533) pump out dry well install mtor on pump 2 cntactors us change them for pump3 as the mech seal gone on that pumpAsset condition grade >= 3 comments: site in oor state due for update. 16/06/2016 (824292) refitted pp1. Install pump 1 and test T Crayton Fred Hill Simon Gibbs | 16/06/2016 (824292) refitted pp1. Install pump 1 and test T Crayton Fred Hill Simon Gibbs | N/A | Sched. Is set up in Hansen, NSD 23/12/19 | DRY WELL 1,2,3;2018. STORM RETURN PUMP 2008. | Pressure + Rising Main flow available to make system curve Request 1-min archiving for flow at discharge end
15415 | 15415 | SPS | W | Bridgwater, Colley Lane SPS | 2018-05-01 | 103 | 123 | 120-130 | 0.0l/s on the trend, 30/7/19 reach 133 l/s in a peak, when looking at the week peaks are normally consistantly 103l/s | 4373700% | 130 | 4381900% | 150 |  |  | 4352900% | 05/03/2019 (1377120) -Maintenance carried out to the best ability.Pump is currently been removed for repair by Allan Ray. Have given visual inspection of pipework, guide rails etc. Can not inspect footstall without obtaining a 3 man entry and sump to be empty.There is no Emergency stop buttons on panel nor out where the pump is situated. This job was completed 01-3-19. 16/08/2018 (1277741) Please remove storm p2 for repair with electric hoist | 22/05/2018 (1153180 - DWF2) Pumping station being updated. | N/A | No sched. Set up In Hansen | DWF 1,2; 1991. BOOSTER&STORM 1,2,3 1991, STORAGE TANK MIXER/RETURN 1,2&STORM WET WELL; 2018. | OK no action
14378 | 14378 | SPS | W | Bridgwater, Blake Gardens SPS | 2017-03-31 | 116 | 140 | 160 | 0.0 l/s. Peaks reach 150l/s. In stormy conditions the trend shows one peak got to approx 160-162l/s. | 4373700% | 150 | 4381800% | 167 |  |  | 4352900% | N/A | N/A | N/A | n/a but schedule is set up for date dec 2019. | PUMP 1 ¦ DRY WELL 22777, PUMP 2 ¦ DRY WELL 22776 NO DATE, SUMP PUMP 1 1976, WET WELL PUMP ¦ SUBMERSIBLE - WITH TIDAL FLAP VALVES 1 & 2, 2007 | OK no action
14385 | 14385 | SPS | W | Bridgwater, Bristol Road SPS | 2017-05-01 | 90 | 160 | 175 | 0.0 l/s. Normally hits a peak of about 80l/s. occasionly as high as 129l/s. In stormy conditions reach 157l/s. | 4373700% | 165 | 4381800% | 165 |  |  | no PPM schedule for site (only air valve and inspection) | (04/11/2017 - 1099279) Found P2 had blown 332A Fuse rreplaced and try again blown 2nd Fuse - lift Pump no Blockage - IR and Continuity Tests on Windings showed negative result - try again with Pump on Surface making nosie discovered Impellor had dropped -reposition Impell and all ok | 1462177 (26/06/2019) attend site and cleared p3 and replaced 6 amp fuse pump runs but shows as unavailable on hmi screen commincation failure to this device tried to reset but unable to informed AP who is going to try and get henry to dial in | 4359800% | (1374353) - we found it does not look like the two air valves are working in chamber I have not raised a job for this as Sam mentioned that there might be a small schemes job raised for this, I have sent a email to Ashley to say, if it is something that we would have to do from the position of the air valve if we could get to the gantry in the chamber it might possibly work. Chamber cover size 1.2m X 0.900 with a pipe running through the centre of it giving a opening of 0.500 X 0.900 we have tested isolation valves on both and both are working it has a 80mm gate valve on from the base to the top of the gate valve is 1.87m.completed airvlave maintance tested valves and all okay small scemes for ones nr river | DRY WEATHER FLOW FOUL PUMP 1, 2, 3; 2017 | OK no action
14384 | 14384 | SPS | W | Bridgwater, Chilton St SPS | 2016-03-31 | 234 – 256 | 242 | 250 | 192l/s. peaks anywhere between 150 - 225l/s, including in stormy conditions. | 4373700% | 250 | 4383300% | 250 |  |  | 23/05/2019 - PUMP - DRY WELL (SPS) - 1Y | (18/07/19-1459221) installed and tested pump, seems to be panel fault with pump as is staying on even when selector switch turned off. email will be sent to ashley about this. (23/04/19-1425379) new pump. DWF 3. (03/12/2018 - 1344107) fitted new sump pump when on site. (07/02/2018 -1152963) Reinstalled storage tankker mixer pump. 01/11/2018 (1326136) new pump installed and test ran (17/11/2017 - 1107541) install replacement dwf pump to p1 | 23/04/2019 (1425379) install and test new pump back to site all ok. 21/03/2019 (1408395) Installed new junction box at the bottom of the dry well. Removed pump3 and found pump1 isolation valve half closed. Ops to install pump when repaired. 01/11/2018 (1326136) new pump installed and test ran | 4360700% | cut back and checked | DWF 1,2,3; 2008 | OK no action
15555 | 15555 | SPS | S | Hillcrest Road PS, Wyke, Weymouth | 2020-03-31 | 174 | 150 | No data | 96.88l/s. Storm 30/07/19 250l/s one peak. In the week it was consistently peaking at 135l/s. | 4371700% | 263.98 | 4381800% | 245 |  |  | n/a each site maintenance has been cancelled. | 21/01/2019 (1367273) pump 1 now replaced with new pump and working on new panel 13/08/2018 (1265495) Please fit newly delivered pump. 23/07/2018 (1261292) installed new pump fitted old lifting chain wich is in goog condiction. pulled cables throu nrv chamber and up in to the control room. did nick didnt conect cables because panels are being worked on and tecs said thay will concet it at a later date. but pump is ready to go outher than that. | N/A | N/A | No sched. Set up In Hansen | WASH PUMP; 1992. WET WELL PUMP 1,2,3; 1992. | OK no action
14495 | 14495 | SPS | W | Clevedon Main PS | 2020-03-31 | 150 | 335 | 380-400 | unsure | 4373700% | 400 | 4381800% | 400 |  |  | 4355300% | N/A | N/A | 2018-11-01 | located all air valves and test isolation valves and strip and check all valves test all ok | DWF 1,2,3; 2016. SPILLAGE PUMP; 2016. | OK no action
15273 | 15273 | SPS | S | Turlin Main CSO | 2017-05-01 | 234-259 | 345 | 400-430 | Shows a reading of 24l/s - BUT no trend, in the last week (NO SIGNAL) Last reading shown dates back to 16/07/19 5:15 40l/s (But previous peaks do reach consent amount - 410l/s). | 4373700% | 500 | 4382000% | 500 |  |  | 4334200% | "Fitted new pump and wear plate and impeller" - 13/04/2016 (798240) | 27/04/2016 (804003- Pump 3) Fitted new wear ring and impellor test run with no faults. 20/04/2016 (799214- Pump 2) Fitted new impellor and wear plate test run with no faults. 13/04/2016 (798240 - Pump 1) Fitted new pump and wear plate and impellor | 4334200% | "visually checked air valves all look ok" | DRY WELL 1,2,3 AND SUMP PUMP 2009. STORM PUMP 2014. | OK no action
15243 | 15243 | SPS | W | Bridgwater, East Quay SPS | 1 May 2018 | 172 -180 | 179 | 180 | unsure | 4373600% | 165 - 190 | 4382500% | 188 | 4384500% | 197 | 4337400% | 13/12/2018 (1346394) installed new pump but isolator faulty so ash ordering a new one. 21/02/2015 (629707) lifted pump-no blockage. pump pulling 20a over FLC. slightly noisy suspected bearings starting to fail. notified control that pump station guys need to remove pump and send for repair once theyre no.1 pump is back. got pump back running and drained down sump all okay | 13/12/2018 (1346394 - DWF 2) installed new pump but isolator faulty so ash ordering a new one. | N/A | n/a - job in Hansen NSD 16/12/2019 | DRY WELL PUMP 1;1991. DRY WELL SUMP PUMP; 2014. WASHWATER PUMP 1 1987. | OK no action
13016 | #N/A | Treatment | N | Saltford – Mead Lane STW SSO | 2016-03-31 | n/a | 580 | 530 | 441.51 l/s. Fluctuates between 0 - 510l/s. 30/07/19 showed that in stormy conditions it can reach 600l/s. | [6 empty] | 4336200% | (13/01/2019 - 1370227) attend site and fit 2 new pumps to site and test and found rising main in sump leaking very bad causing both pumps to run on this is what caused both pumps to run on and fail i have pumped sump down and will raise job for sump to be pumped down tomorrow and will speak to AP /GT | N/A | 12/04/2019 JOB MARKED AS COMPLETE BUT… | 12/04/2019 JOB MARKED AS COMPLETE BUT…DDixon advised job for M&E as on STW | stw - no pump details | 2 signals available, not sure which is the right one. Pass to Andy Cotterell
Note on L2: Sagar Rana: Regurlarly flows at 7.6 otherwise
Note on L4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 11.25 l/s during 2019 largest storm in 23/07
Note on N6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No significant sump fill past 3 months
Note on L7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2019 biggest storm only measured 61 l/s on 7/6
Note on L10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Down from 315 l/s during the biggest 2019 storm on 6/6
Note on H11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FFT at #16895 - Green Spot CSO
Note on L12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hits about 460 in recent storms
Note on L16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Peaks at 18 during a storm then regurlarly fuluctuates between 10 and 14 l/s
Note on L18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Peaks around 57 but averaging at about 50 Was hitting about 59 earlier in April
Note on H19: Sagar Rana: Emergency Only permit
Note on L21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Deteriorating from averaging 135 l/s to a range of 132 to 125 during storm
Note on H23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Used to be 90 l/s
Note on L28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 460 l/s during biggest storm in 2019

## Flowmeter Signals Nov22
Site Id | Site Area | Site Description | Site Name | DB_ADDR | DB_NAME | UNIT | Server | Include PFF | SignalLink | BD lookup
15070 | WIMBORNE | HAYES LANE COLEHILL | WIMBORNE HAYES LANE COLEHILL | E35523 |  | l/s | WASTE | Y | WASTE:E35523
15680 | PORTISHEAD | BLACK NORE (NAUTICAL SCHOOL) | PORTISHEAD BLACK NORE (NAUTICAL SCHOOL) | E22302 |  | l/s | WASTE | Y | WASTE:E22302
14222 | EAST KNIGHTON | BLACKNOLL | EAST KNIGHTON BLACKNOLL | E14126 | 142222EA448 MCERTS FPF FLOW | l/s | WASTE | Y | WASTE:E14126
13334 | BRIDPORT | WEST BAY | BRIDPORT WEST BAY | E12595 | 195390STORM TRANSFER FLOW | l/s | WASTE | Y-Treatment | WASTE:E12595
13334 | BRIDPORT | WEST BAY | BRIDPORT WEST BAY | E12596 | 195390TRANSFER PUMPS LEVEL | l/s | WASTE | Y-Treatment | WASTE:E12596
15519 | WATCHET | MARKET STREET (TUNNEL) | WATCHET MARKET STREET (TUNNEL) | E35890 | 155190SPS OUTLET FLOW ANG | l/s | WASTE | Y-Treatment | WASTE:E35890
15553 | PORTLAND | VICTORIA SQUARE | PORTLAND VICTORIA SQUARE | E12512 | 155531FLOW TO TREATMENT | l/s | WASTE | Y - Treatment | WASTE:E12512
15556 | WEYMOUTH | RADIPOLE | WEYMOUTH RADIPOLE | E17548 | 155562STORM FLOW | l/s | WASTE | Y - Treatment | WASTE:E17548
15556 | WEYMOUTH | RADIPOLE | WEYMOUTH RADIPOLE | E17549 | 155562DRY WEATHER FLOW | l/s | WASTE | Y - Treatment | WASTE:E17549
15556 | WEYMOUTH | RADIPOLE | WEYMOUTH RADIPOLE | E17547 | 155562EMERGENCY PMP 1 FLW | l/s | WASTE | Y - Treatment | WASTE:E17547
15556 | WEYMOUTH | RADIPOLE | WEYMOUTH RADIPOLE | E17548 | 155562STORM FLOW | l/s | WASTE | Y - Treatment | WASTE:E17548
15556 | WEYMOUTH | RADIPOLE | WEYMOUTH RADIPOLE | E17549 | 155562DRY WEATHER FLOW | l/s | WASTE | Y - Treatment | WASTE:E17549
15556 | WEYMOUTH | RADIPOLE | WEYMOUTH RADIPOLE | E17550 | 155562EMERGENCY PMP 2 FLW | l/s | WASTE | Y - Treatment | WASTE:E17550
15063 | STURMINSTER MARSHALL | NEWTON ROAD | STURMINSTER MARSHALL NEWTON ROAD | E33937 | 150631INCOMING FLOW ANG | l/s | WASTE | Y | WASTE:E33937
15299 | KINGSDON | . | KINGSDON . | E37331 | 152990RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E37331
11591 | WESTON-SUPER-MARE | TIGER MOTH ROAD | WESTON-SUPER-MARE TIGER MOTH ROAD | E54561 | 115910RISING MAIN FLOWMETER ANG | l/s | WASTE | Y | WASTE:E54561
11891 | HAYWOOD VILLAGE | COBHAM PARADE | HAYWOOD VILLAGE COBHAM PARADE | E52052 | 118910RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E52052
12254 | CONGRESBURY | CONGRESBURY SERVICE STATION | CONGRESBURY CONGRESBURY SERVICE STATION | E54490 | 122540RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E54490
12498 | BRENT KNOLL | BRENT KNOLL PRIMARY SCHOOL | BRENT KNOLL BRENT KNOLL PRIMARY SCHOOL | E52507 | 124981RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E52507
12520 | WEYMOUTH | CURTIS WAY | WEYMOUTH CURTIS WAY | E55373 | 125200DWF DELIVERY FLOW ANG | l/s | WASTE | Y | WASTE:E55373
12686 | WESTON SUPER MARE | HERCULES ROAD | WESTON SUPER MARE HERCULES ROAD | E54552 | 126860RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E54552
12719 | MARK | POPLAR LANE | MARK POPLAR LANE | E39643 | 127190RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E39643
13014 | AXBRIDGE | OLD STW SITE | AXBRIDGE OLD STW SITE | E4578 | 130140RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E4578
13033 | BRADFORD PEVERELL | GILES CROSS | BRADFORD PEVERELL GILES CROSS | E31386 | 130332RISING MAIN FLOW ANG | l/s | WASTE | N | WASTE:E31386
13093 | DONIFORD | . | DONIFORD . | E14298 | 130931FLOW TO WATCHET | l/s | WASTE | Y | WASTE:E14298
13197 | MARK | . | MARK . | E4364 | 131970RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E4364
13265 | SHAPWICK | SOMERSET | SHAPWICK SOMERSET | E11975 | 132651RISING MAIN FLOW METER | l/s | WASTE | Y | WASTE:E11975
13284 | ST GEORGES | NO 1 | ST GEORGES NO 1 | E11866 | 132841RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E11866
13375 | LYNEHAM | PRESTON LANE | LYNEHAM PRESTON LANE | E3095 | 133751PASS FWD FLW ANLG | l/s | WASTE | Y | WASTE:E3095
14002 | BATH | MIDLAND ROAD TWERTON | BATH MIDLAND ROAD TWERTON | E23612 | 140021WINDSOR VILLAS RISING MAIN FLOW AN | l/s | WASTE | Y | WASTE:E23612
14002 | BATH | MIDLAND ROAD TWERTON | BATH MIDLAND ROAD TWERTON | E6612 | 14002AOLD RISING MAIN FLOW ANG | l/s | WASTE2 | Y | WASTE2:E6612
14002 | BATH | MIDLAND ROAD TWERTON | BATH MIDLAND ROAD TWERTON | E6614 | 14002ANEW RISING MAIN FLOW ANG | l/s | WASTE2 | Y | WASTE2:E6614
14016 | BRISTOL | ASHTON AVENUE | BRISTOL ASHTON AVENUE | E11469 | 140161DWF FLOW TOTAL | l/s | WASTE | Y | WASTE:E11469
14016 | BRISTOL | ASHTON AVENUE | BRISTOL ASHTON AVENUE | E11475 | 140161DWF P1 FLOW ANLG | l/s | WASTE | Y | WASTE:E11475
14016 | BRISTOL | ASHTON AVENUE | BRISTOL ASHTON AVENUE | E11476 | 140161DWF P2 FLOW ANLG | l/s | WASTE | Y | WASTE:E11476
14016 | BRISTOL | ASHTON AVENUE | BRISTOL ASHTON AVENUE | E11477 | 140161DWF P3 FLOW ANLG | l/s | WASTE | Y | WASTE:E11477
14016 | BRISTOL | ASHTON AVENUE | BRISTOL ASHTON AVENUE | E11478 | 140161DWF P4 FLOW ANLG | l/s | WASTE | Y | WASTE:E11478
14016 | BRISTOL | ASHTON AVENUE | BRISTOL ASHTON AVENUE | E11479 | 140161DWF P5 FLOW ANLG | l/s | WASTE | Y | WASTE:E11479
14033 | CHRISTCHURCH | PUREWELL | CHRISTCHURCH PUREWELL | E15825 | 140331RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E15825
14035 | CHRISTCHURCH | SOMERFORD BRIDGE | CHRISTCHURCH SOMERFORD BRIDGE | E50018 | 140352RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E50018
14050 | COLLINGBOURNE DUCIS | . | COLLINGBOURNE DUCIS . | E23794 | 140502RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E23794
14054 | PEWSEY | JUBILEE | PEWSEY JUBILEE | E24022 | 140540RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E24022
14057 | GREAT CHEVERELL | CHEVERELL GREEN | GREAT CHEVERELL CHEVERELL GREEN | E5098 | 140571RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E5098
14067 | BITTON | . | BITTON . | E3094 | 129290RISING MAIN FLOWMETER | l/s | WASTE2 | Y | WASTE2:E3094
14070 | GODNEY | . | GODNEY . | E5622 | 140700RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E5622
14082 | STREET | MAIN | STREET MAIN | E39931 | 140821FLOWMETER AI | l/s | WASTE | Y | WASTE:E39931
14083 | WEST PENNARD | HAVYATT | WEST PENNARD HAVYATT | E85110 | 140831LEAK DETECTION FLOW METER | l/s | WASTE | Y | WASTE:E85110
14087 | WEST LYDFORD | . | WEST LYDFORD . | E5623 | 140870RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E5623
14090 | BUTLEIGH WOOTTON | . | BUTLEIGH WOOTTON . | E5338 | 140900RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E5338
14095 | GLASTONBURY | PORCHESTALL | GLASTONBURY PORCHESTALL | E3218 | 140950RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E3218
14096 | COXLEY | MILL LANE | COXLEY MILL LANE | E3547 | 140961RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E3547
14097 | BALTONSBOROUGH | BALTONSBOROUGH MAIN | BALTONSBOROUGH BALTONSBOROUGH MAIN | E5624 | 140970RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E5624
14108 | MELLS | . | MELLS . | E4153 | 141081RISING MAIN FLOWMETER ANLG | l/s | WASTE | Y | WASTE:E4153
14112 | WANSTROW | . | WANSTROW . | E22392 | 141122EA270MCERT FLOW METER | l/s | WASTE | Y | WASTE:E22392
14113 | TRUDOXHILL | . | TRUDOXHILL . | E33202 | 141131FLOW MONITOR | l/s | WASTE | Y | WASTE:E33202
14116 | GURNEY SLADE | . | GURNEY SLADE . | E4132 | 141160FLOW | l/s | WASTE | Y | WASTE:E4132
14122 | SPETISBURY | NO 3 | SPETISBURY NO 3 | E11155 | 141221RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E11155
14128 | BURLEY | ESDAILE LANE | BURLEY ESDAILE LANE | E15396 | 141281RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E15396
14131 | RINGWOOD | MOORTOWN | RINGWOOD MOORTOWN | E16488 | 141311PUMP 1 FLOW | l/s | WASTE | Y | WASTE:E16488
14131 | RINGWOOD | MOORTOWN | RINGWOOD MOORTOWN | E16489 | 141311PUMP 2 FLOW | l/s | WASTE | Y | WASTE:E16489
14133 | RINGWOOD | BICKERLEY | RINGWOOD BICKERLEY | E50045 | 141331RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E50045
14145 | MALMESBURY | TANNERS BRIDGE | MALMESBURY TANNERS BRIDGE | E11911 | 141451RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E11911
14147 | CHIPPENHAM | WESTMEAD | CHIPPENHAM WESTMEAD | E21141 | 141471FLOWMETER | l/s | WASTE | Y | WASTE:E21141
14175 | EASTCOURT | OATRIDGE FARM | EASTCOURT OATRIDGE FARM | E21184 | 141751RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E21184
14179 | BIDDESTONE | MANOR COTTAGES | BIDDESTONE MANOR COTTAGES | E21054 | 141791OUTLET FLOW | l/s | WASTE | Y | WASTE:E21054
14185 | MALMESBURY | ST JOHNS STREET | MALMESBURY ST JOHNS STREET | E35359 | 141852RISING MAIN 1 FLOW ANG | l/s | WASTE | Y | WASTE:E35359
14185 | MALMESBURY | ST JOHNS STREET | MALMESBURY ST JOHNS STREET | E35360 | 141852RISING MAIN 2 FLOW ANG | l/s | WASTE | Y | WASTE:E35360
14188 | LOWER STANTON ST QUINTIN | . | LOWER STANTON ST QUINTIN . | E38002 | 141881EA287DWF OUTFLOW FLOW | l/s | WASTE | Y | WASTE:E38002
14196 | MALMESBURY | NOAHS ARK | MALMESBURY NOAHS ARK | E7198 | 14196AINLET FLOWMETER AI | l/s | WASTE2 | Y | WASTE2:E7198
14197 | MALMESBURY | CORSTON | MALMESBURY CORSTON | E21378 | 141971RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E21378
14202 | HANKERTON | HANKERTON BRIDGE | HANKERTON HANKERTON BRIDGE | E21249 | 142021RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E21249
14216 | STOBOROUGH | KINGS ARMS | STOBOROUGH KINGS ARMS | E17983 | 142161DWF FLOW | l/s | WASTE | Y | WASTE:E17983
14219 | UPTON | SANDY LANE | UPTON SANDY LANE | E18411 | 142191DWF FLOW | l/s | WASTE | Y | WASTE:E18411
14220 | LYTCHETT MATRAVERS | BULBURY LANE | LYTCHETT MATRAVERS BULBURY LANE | E11314 | 142201FLW FROM SITE | l/s | WASTE | Y | WASTE:E11314
14227 | STUDLAND | WADMORE LANE | STUDLAND WADMORE LANE | E18164 | 142271RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E18164
14249 | BLOXWORTH | FOX POUND | BLOXWORTH FOX POUND | E56124 | 142492RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E56124
14252 | STUDLAND | COOMBE | STUDLAND COOMBE | E30089 | 142521PASS FWD FLOW ANLG | l/s | WASTE | Y | WASTE:E30089
14255 | STOBOROUGH | RIDGE | STOBOROUGH RIDGE | E17995 | 142551RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E17995
14259 | WAREHAM | SOUTH EAST | WAREHAM SOUTH EAST | E18502 | 142591RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E18502
14259 | WAREHAM | SOUTH EAST | WAREHAM SOUTH EAST | E18503 | 142591INCOMING FLOW FROM STOBOROUGH SPS | l/s | WASTE | Y | WASTE:E18503
14261 | STUDLAND | WATERY LANE | STUDLAND WATERY LANE | E18177 | 142611RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E18177
14265 | UPTON | MOORLANDS WAY | UPTON MOORLANDS WAY | E12797 | 142651DWF FLOW | l/s | WASTE | Y | WASTE:E12797
14266 | WAREHAM | SANDFORD LANE | WAREHAM SANDFORD LANE | E13967 | 142661RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E13967
14276 | CORFE CASTLE | STUDLAND ROAD | CORFE CASTLE STUDLAND ROAD | E15956 | 142761RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E15956
14283 | BARTON ST DAVID | . | BARTON ST DAVID . | E5307 | 142830FLOW METER | l/s | WASTE | Y | WASTE:E5307
14295 | YEOVILTON | WEIR | YEOVILTON WEIR | E13706 | 142952DWF FLOW | l/s | WASTE | Y | WASTE:E13706
14311 | TILSHEAD | CAMP ROAD | TILSHEAD CAMP ROAD | E18308 | 143111RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E18308
14312 | SHREWTON | HOMANTON | SHREWTON HOMANTON | E17852 | 143121STORM MAIN FLOWMETER | l/s | WASTE | Y | WASTE:E17852
14312 | SHREWTON | HOMANTON | SHREWTON HOMANTON | E31576 | 143121FFT PUMPING STATION FLOW | l/s | WASTE | Y | WASTE:E31576
14313 | STAPLEFORD | OVERSTREET | STAPLEFORD OVERSTREET | E17957 | 143132FLOW | l/s | WASTE | Y | WASTE:E17957
14320 | STAPLEFORD | PELICAN INN | STAPLEFORD PELICAN INN | E17969 | 143201RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E17969
14322 | DINTON | BRATCH LANE | DINTON BRATCH LANE | E16072 | 143221RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E16072
14328 | HANGING LANGFORD | . | HANGING LANGFORD . | E16514 | 143281RISING MAIN PUMP 1 FLOW | l/s | WASTE | Y | WASTE:E16514
14328 | HANGING LANGFORD | . | HANGING LANGFORD . | E16515 | 143281RISING MAIN PUMP 2 FLOW | l/s | WASTE | Y | WASTE:E16515
14329 | SALISBURY | PETERSFINGER | SALISBURY PETERSFINGER | E17735 | 143291RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E17735
14329 | SALISBURY | PETERSFINGER | SALISBURY PETERSFINGER | E17737 | 143291RISING MAIN PETERSFINGER SPS FLOW | l/s | WASTE | Y | WASTE:E17737
14330 | LITTLE LANGFORD | . | LITTLE LANGFORD . | E16735 | 143302RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E16735
14333 | EAST KNOYLE | SHAFTESBURY ROAD | EAST KNOYLE SHAFTESBURY ROAD | E51331 | 143332RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E51331
14337 | ALDERBURY | HOME FARM | ALDERBURY HOME FARM | E14733 | 143371RISING MAIN FLOW 1 ANLG | l/s | WASTE | Y | WASTE:E14733
14337 | ALDERBURY | HOME FARM | ALDERBURY HOME FARM | E14735 | 143371RISING MAIN FLOW 2 ANLG | l/s | WASTE | Y | WASTE:E14735
14338 | NETHERAVON | CAMP ROAD | NETHERAVON CAMP ROAD | E17060 | 143381RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E17060
14342 | TEFFONT EVIAS | . | TEFFONT EVIAS . | E18281 | 143421PUMPED FLOW | l/s | WASTE | Y | WASTE:E18281
14346 | HINDON | THE DENE | HINDON THE DENE | E16553 | 14346INFLOW | l/s | WASTE | Y | WASTE:E16553
14358 | SOUTH NEWTON | BELL INN | SOUTH NEWTON BELL INN | E51247 | 143583RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E51247
14359 | NEWTON TONEY | VILLAGE HALL CAR PARK | NEWTON TONEY VILLAGE HALL CAR PARK | E17138 | 143591RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E17138
14362 | CHILMARK | . | CHILMARK . | E15591 | 143621FLOW | l/s | WASTE | Y | WASTE:E15591
14371 | CHEDDAR | FROGLANDS | CHEDDAR FROGLANDS | E4766 | 143712RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E4766
14372 | WEST HUNTSPILL | SLOWAY LANE | WEST HUNTSPILL SLOWAY LANE | E56406 | 14372ADWF FLOWMETER AI | l/s | WASTE | Y | WASTE:E56406
14372 | WEST HUNTSPILL | SLOWAY LANE | WEST HUNTSPILL SLOWAY LANE | E56412 | 14372AFLOW FROM WOOLAVINGTON CAUSEWAY SPS AI | l/s | WASTE | Y | WASTE:E56412
14372 | WEST HUNTSPILL | SLOWAY LANE | WEST HUNTSPILL SLOWAY LANE | E56413 | 14372AFLOW FROM WEST HUNTSPILL SPS SITES AI | l/s | WASTE | Y | WASTE:E56413
14374 | HIGHBRIDGE | NEWTON | HIGHBRIDGE NEWTON | E21853 | 143740FLOW TO TREATMENT | l/s | WASTE | Y - Treatment | WASTE:E21853
14376 | MOORLINCH | RIGHT DROVE | MOORLINCH RIGHT DROVE | E13661 | 143761RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E13661
14378 | BRIDGWATER | BLAKE GARDENS | BRIDGWATER BLAKE GARDENS | E24698 | 143781DWF FLOW | l/s | WASTE | Y | WASTE:E24698
14379 | FIDDINGTON | . | FIDDINGTON . | E4592 | 143790 RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E4592
14381 | WESTONZOYLAND | . | WESTONZOYLAND . | E4994 | 143810RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E4994
14381 | WESTONZOYLAND | . | WESTONZOYLAND . | E4995 | 143810INCOMING RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E4995
14382 | BAWDRIP | . | BAWDRIP . | E4403 | 143821COSSINGTON PRIVATE SEWER FLOW | l/s | WASTE | Y | WASTE:E4403
14384 | BRIDGWATER | CHILTON STREET SALTLANDS | BRIDGWATER CHILTON STREET SALTLANDS | E31276 | 143841FLOW TO CHILTON TRINITY | l/s | WASTE | Y | WASTE:E31276
14385 | BRIDGWATER | BRISTOL ROAD | BRIDGWATER BRISTOL ROAD | E9640 | 13034BRISTOL ROAD FLOWMETER | l/s | WASTE | Y | WASTE:E9640
14386 | GREINTON | MOOR DRIVE | GREINTON MOOR DRIVE | E4613 | 143860RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E4613
14393 | HILLFARRANCE | . | HILLFARRANCE . | E13775 | 143931RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E13775
14397 | BEER HACKETT | . | BEER HACKETT . | E2351 | 143970RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E2351
14404 | BEAMINSTER | SOUTHGATE | BEAMINSTER SOUTHGATE | E21991 | 144042RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E21991
14407 | STRATTON | STRATTON BRIDGE | STRATTON STRATTON BRIDGE | E18086 | 144071RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E18086
14408 | BRADFORD PEVERELL | MR SOFTIES | BRADFORD PEVERELL MR SOFTIES | E15253 | 144081RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E15253
14413 | CHIDEOCK | SEATOWN | CHIDEOCK SEATOWN | E9603 | 130601CHIDEOCK PASS FWD FLOW FROM SEATOWN | l/s | WASTE | Y | WASTE:E9603
14423 | BLUE ANCHOR | PILL BRIDGE | BLUE ANCHOR PILL BRIDGE | E1574 | 144231DWF PASS FORWARD FLOW | l/s | WASTE | Y | WASTE:E1574
14426 | PAULTON | GOOSARD BRIDGE | PAULTON GOOSARD BRIDGE | E1697 | 144260RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E1697
14431 | BISHOP SUTTON | . | BISHOP SUTTON . | E1620 | 144310RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E1620
14437 | WARMINSTER | PORTWAY | WARMINSTER PORTWAY | E33172 | 144371RISING MAIN FLOW AI | l/s | WASTE | Y | WASTE:E33172
14475 | BROUGHTON GIFFORD | THE GREEN | BROUGHTON GIFFORD THE GREEN | E12895 | 144750RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E12895
14495 | CLEVEDON | CLEVEDON MAIN | CLEVEDON CLEVEDON MAIN | E50935 | 144950DWF FLOW | l/s | WASTE | Y | WASTE:E50935
14496 | CONGRESBURY | SOUTH | CONGRESBURY SOUTH | E3537 | 144960RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E3537
14497 | KEWSTOKE | SAND ROAD | KEWSTOKE SAND ROAD | E2757 | 144970RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E2757
14498 | UPHILL | . | UPHILL . | E10059 | 144980RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E10059
14510 | TROWBRIDGE | TERMINAL AT BRADFORD ROAD | TROWBRIDGE TERMINAL AT BRADFORD ROAD | E3937 | 145100MAIN NO 1 FLOW METER | l/s | WASTE | Y | WASTE:E3937
14510 | TROWBRIDGE | TERMINAL AT BRADFORD ROAD | TROWBRIDGE TERMINAL AT BRADFORD ROAD | E3938 | 145100MAIN NO2 FLOW METER | l/s | WASTE | Y | WASTE:E3938
14510 | TROWBRIDGE | TERMINAL AT BRADFORD ROAD | TROWBRIDGE TERMINAL AT BRADFORD ROAD | E52946 | 145100EA340 MCERT MAINS 1 FLOW AI | l/s | WASTE | Y | WASTE:E52946
14510 | TROWBRIDGE | TERMINAL AT BRADFORD ROAD | TROWBRIDGE TERMINAL AT BRADFORD ROAD | E52947 | 145100EA341 MCERT MAINS 2 FLOW AI | l/s | WASTE | Y | WASTE:E52947
14519 | SOMERTON | BARPOOL LANE | SOMERTON BARPOOL LANE | E19227 | 145191RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E19227
14521 | EAST LAMBROOK | . | EAST LAMBROOK . | E3411 | 145210PUMPED FLOW | l/s | WASTE | Y | WASTE:E3411
14523 | LOW HAM | MORETONS LANE | LOW HAM MORETONS LANE | E19123 | 145231RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E19123
14528 | CARLINGCOTT | STONEAGE LANE | CARLINGCOTT STONEAGE LANE | E19878 | 145281FLOW ANG | l/s | WASTE | Y | WASTE:E19878
14551 | BRIDGWATER | BRADNEY BRIDGE | BRIDGWATER BRADNEY BRIDGE | E1776 | 145510OUTLET RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E1776
14551 | BRIDGWATER | BRADNEY BRIDGE | BRIDGWATER BRADNEY BRIDGE | E1777 | 145510FLOW FROM WESTONZOYLAND SPS | l/s | WASTE | Y | WASTE:E1777
14551 | BRIDGWATER | BRADNEY BRIDGE | BRIDGWATER BRADNEY BRIDGE | E1778 | 145510FLOW FROM GREINTON SPS | l/s | WASTE | Y | WASTE:E1778
14555 | ISLE ABBOTTS | TWO BRIDGES | ISLE ABBOTTS TWO BRIDGES | E11965 | 145551RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E11965
14574 | HEWISH | PALMERS ELM | HEWISH PALMERS ELM | E22638 | 145741RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E22638
14598 | LOWER WEARE | . | LOWER WEARE . | E39282 | 145981RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E39282
14621 | PORTISHEAD | TOWN HARBOUR ROAD | PORTISHEAD TOWN HARBOUR ROAD | E11503 | 146210PHEAD SPS FOUL RIS FLOW | l/s | WASTE | Y | WASTE:E11503
14648 | CHILTON POLDEN | MAIN | CHILTON POLDEN MAIN | E18981 | 146481EDINGTON FLOW | l/s | WASTE | Y | WASTE:E18981
14648 | CHILTON POLDEN | MAIN | CHILTON POLDEN MAIN | E18987 | 146481RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E18987
14723 | WESTON-SUPER-MARE | FIELD NEAR FULL QUART | WESTON-SUPER-MARE FIELD NEAR FULL QUART | E6000 | 147231RISING MAIN FLOWMETER ANLG | l/s | WASTE2 | Y | WASTE2:E6000
14724 | CHILTON POLDEN | DRAINAGE POND SEDGEMOOR COUNCIL | CHILTON POLDEN DRAINAGE POND SEDGEMOOR COUNCIL | E56269 | 147240RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E56269
15002 | BOSCOMBE | NO 1 | BOSCOMBE NO 1 | E9422 | 150020PUMP 1 FLOW | l/s | WASTE | Y | WASTE:E9422
15002 | BOSCOMBE | NO 1 | BOSCOMBE NO 1 | E9423 | 150020PUMP 2 FLOW | l/s | WASTE | Y | WASTE:E9423
15007 | BOURNEMOUTH | IFORD LANE TUCKTON | BOURNEMOUTH IFORD LANE TUCKTON | E13880 | 150071PUMP MAIN FLOW | l/s | WASTE | Y | WASTE:E13880
15013 | SOUTHBOURNE | HENGISTBURY HEAD | SOUTHBOURNE HENGISTBURY HEAD | E9494 | 150130FLOW | l/s | WASTE | Y | WASTE:E9494
15019 | BOURNEMOUTH | NO 1 | BOURNEMOUTH NO 1 | E29653 | 150190FOUL PUMPED FLOW | l/s | WASTE | Y | WASTE:E29653
15037 | CHRISTCHURCH | QUOMPS NO 2 | CHRISTCHURCH QUOMPS NO 2 | E4208 | 150371RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E4208
15038 | CHRISTCHURCH | AVON MILL LANE | CHRISTCHURCH AVON MILL LANE | E15669 | 150381RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E15669
15063 | STURMINSTER MARSHALL | NEWTON ROAD | STURMINSTER MARSHALL NEWTON ROAD | E33935 | 150631RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E33935
15064 | SHAPWICK | STEWARDS LANE | SHAPWICK STEWARDS LANE | E7901 | 150640RISING MAIN FLOW ANG | l/s | WASTE | N | WASTE:E7901
15068 | ST LEONARDS | WAYSIDE ROAD NO 1 | ST LEONARDS WAYSIDE ROAD NO 1 | E7943 | 150680RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E7943
15075 | CORFE MULLEN | PARDYS HILL | CORFE MULLEN PARDYS HILL | E51205 | 150751FLOW METER ANG | l/s | WASTE | Y | WASTE:E51205
15078 | FERNDOWN | A31 TRICKETTS CROSS | FERNDOWN A31 TRICKETTS CROSS | E8017 | 150780RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E8017
15081 | STONEY DOWN | CRUMPET FARM ROAD | STONEY DOWN CRUMPET FARM ROAD | E36474 | 150811RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E36474
15084 | VERWOOD | POTTERNE WAY | VERWOOD POTTERNE WAY | E7339 | 150840PASS FORWARD FLOW ANG | l/s | WASTE | Y | WASTE:E7339
15100 | NORTH NEWNTON | . | NORTH NEWNTON . | E7614 | 151000RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E7614
15111 | ALL CANNINGS | . | ALL CANNINGS . | E13722 | 151111RISING MAIN FLOWMETER | l/s | WASTE | Y | WASTE:E13722
15134 | SEVERN BEACH | . | SEVERN BEACH . | E22366 | 151341RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E22366
15149 | HAWKESBURY UPTON | BRITAIN BOTTOM | HAWKESBURY UPTON BRITAIN BOTTOM | E23360 | 151491RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E23360
15158 | OLVESTON | THE COMMON | OLVESTON THE COMMON | E23065 | 151581RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E23065
15183 | BAGSTONE | . | BAGSTONE . | E12544 | 151831OUTLET FLOW | l/s | WASTE | Y | WASTE:E12544
15185 | LITTLE BADMINTON | WELL LANE | LITTLE BADMINTON WELL LANE | E23854 | 151851RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E23854
15190 | MILBORNE ST ANDREW | MANOR FARM | MILBORNE ST ANDREW MANOR FARM | E5464 | 151900RISING MAIN DWF FLOW | l/s | WASTE | Y | WASTE:E5464
15190 | MILBORNE ST ANDREW | MANOR FARM | MILBORNE ST ANDREW MANOR FARM | E5465 | 151900RISING MAIN STORM FLOW | l/s | WASTE | Y | WASTE:E5465
15207 | SHAFTESBURY | LONG CROSS | SHAFTESBURY LONG CROSS | E36699 | 152071PUMPED FLOW | l/s | WASTE | Y | WASTE:E36699
15207 | SHAFTESBURY | LONG CROSS | SHAFTESBURY LONG CROSS | E50016 | 152071RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E50016
15218 | BURLEY | MILL LAWN | BURLEY MILL LAWN | E5768 | 152180RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E5768
15233 | POOLE | WILDERTON ROAD | POOLE WILDERTON ROAD | E28790 | 152331PUMPED FLOW | l/s | WASTE | Y | WASTE:E28790
15235 | POOLE | SHORE ROAD | POOLE SHORE ROAD | E9763 | 152350FLOW TO TREATMENT | l/s | WASTE | Y | WASTE:E9763
15239 | POOLE | POOLE PARK | POOLE POOLE PARK | E1709 | 152390ELGIN RD SPS FLW | l/s | WASTE | Y | WASTE:E1709
15243 | BRIDGWATER | EAST QUAY | BRIDGWATER EAST QUAY | E9644 | 130340EAST QUAY FLOWMETER | l/s | WASTE | Y | WASTE:E9644
15244 | POOLE | ELGIN ROAD | POOLE ELGIN ROAD | E28744 | 152440SHORE ROAD SPS FLOW | l/s | WASTE | Y | WASTE:E28744
15244 | POOLE | ELGIN ROAD | POOLE ELGIN ROAD | E28747 | 152440OUTPUT FLOW | l/s | WASTE | Y | WASTE:E28747
15246 | CANFORD MAGNA | CANFORD MAIN | CANFORD MAGNA CANFORD MAIN | E58488 | 152461COMBINED PUMPED FLOW | l/s | WASTE | Y | WASTE:E58488
15257 | POOLE | POOLE BRIDGE POOLE QUAY | POOLE POOLE BRIDGE POOLE QUAY | E35313 | 152571DWF FLOW | l/s | WASTE | Y | WASTE:E35313
15270 | POOLE | CREEKMOOR LANE | POOLE CREEKMOOR LANE | E2442 | 152701RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E2442
15273 | POOLE | TURLIN MAIN BLANDFORD ROAD TURLIN MOOR | POOLE TURLIN MAIN BLANDFORD ROAD TURLIN MOOR | E11883 | 152731DWF FLOW | l/s | WASTE | Y | WASTE:E11883
15278 | LONG SUTTON | BENNETTS ORCHARD | LONG SUTTON BENNETTS ORCHARD | E20032 | 152781RM FLOW | l/s | WASTE | Y | WASTE:E20032
15284 | HUISH EPISCOPI | WAGG DROVE | HUISH EPISCOPI WAGG DROVE | E19046 | 152841RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E19046
15304 | WEST CHINNOCK | GARAGE | WEST CHINNOCK GARAGE | E19458 | 153041RISING MAIN FLOW AN | l/s | WASTE | Y | WASTE:E19458
15306 | LOWER SOMERTON | . | LOWER SOMERTON . | E19358 | 153061RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E19358
15309 | CHARLTON MACKERELL | ROOKERY FARM | CHARLTON MACKERELL ROOKERY FARM | E19214 | 153091FLOW METER | l/s | WASTE | Y | WASTE:E19214
15309 | CHARLTON MACKERELL | ROOKERY FARM | CHARLTON MACKERELL ROOKERY FARM | E19216 | 153091KINGSDON SPS RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E19216
15311 | YEOVIL | MUDFORD | YEOVIL MUDFORD | E36393 | 153112 FLOW MONITOR | l/s | WASTE | Y | WASTE:E36393
15313 | HUISH EPISCOPI | PIBSBURY | HUISH EPISCOPI PIBSBURY | E19306 | 153131RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E19306
15314 | UPTON | NR LANGPORT | UPTON NR LANGPORT | E20072 | 153141RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E20072
15315 | HUISH EPISCOPI | WAGG BRIDGE | HUISH EPISCOPI WAGG BRIDGE | E19040 | 153151RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E19040
15316 | BARTON ST DAVID | TOOTAL BRIDGE | BARTON ST DAVID TOOTAL BRIDGE | E19604 | 153161FLOW METRE | l/s | WASTE | Y | WASTE:E19604
15317 | NORTON SUB HAMDON | . | NORTON SUB HAMDON . | E3185 | 153171RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E3185
15318 | STOFORD | HILLSIDE MAIN | STOFORD HILLSIDE MAIN | E3528 | 153181RISING MAIN FLOW METER | l/s | WASTE | Y | WASTE:E3528
15320 | LONG SUTTON | KNOLE | LONG SUTTON KNOLE | E19344 | 153201RISING MAIN FLOWMETER | l/s | WASTE | Y | WASTE:E19344
15322 | PITNEY | . | PITNEY . | E10795 | 153221PASS FORWARD FLOW ANLG | l/s | WASTE | Y | WASTE:E10795
15334 | CHARLTON ADAM | . | CHARLTON ADAM . | E12428 | 153341RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E12428
15342 | BRENT KNOLL | FORGE HOUSE BRENT STREET | BRENT KNOLL FORGE HOUSE BRENT STREET | E52485 | 153421DWF FLOW ANG | l/s | WASTE | Y | WASTE:E52485
15347 | WOOLAVINGTON | CAUSEWAY | WOOLAVINGTON CAUSEWAY | E3039 | 153472RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E3039
15347 | WOOLAVINGTON | CAUSEWAY | WOOLAVINGTON CAUSEWAY | E3040 | 153472CHILTON POLDEN RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E3040
15353 | BURNHAM-ON-SEA | QUANTOCK CLOSE | BURNHAM-ON-SEA QUANTOCK CLOSE | E6383 | 153530RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E6383
15356 | ROOKSBRIDGE | MENDIP ROAD (FACTORY ROAD) EDINGWORTH | ROOKSBRIDGE MENDIP ROAD (FACTORY ROAD) EDINGWORTH | E6711 | 153560RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E6711
15361 | WEST HUNTSPILL | CROSSWAYS WITHY ROAD | WEST HUNTSPILL CROSSWAYS WITHY ROAD | E6444 | 153610RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E6444
15379 | HIGHBRIDGE | PADDOCK DRIVE | HIGHBRIDGE PADDOCK DRIVE | E6530 | 153790RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E6530
15383 | POOLE | EAST QUAY PERRY GARDENS | POOLE EAST QUAY PERRY GARDENS | E53515 | 153830RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E53515
15385 | BREAN | MERRY BEE SOUTH ROAD | BREAN MERRY BEE SOUTH ROAD | E6552 | 153850PASS FWD FLW TO WSM ANLG | l/s | WASTE | Y | WASTE:E6552
15388 | OTHERY | RYE LANE/ SUMMERHEDGE ROAD | OTHERY RYE LANE/ SUMMERHEDGE ROAD | E13676 | 153882RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E13676
15389 | PAWLETT | MAIN ROAD | PAWLETT MAIN ROAD | E6582 | 153890RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E6582
15392 | CHEDZOY | WARD LANE | CHEDZOY WARD LANE | E4489 | 153920RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E4489
15393 | BRIDGWATER | TAUNTON ROAD | BRIDGWATER TAUNTON ROAD | E24604 | 153930RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E24604
15394 | SUTTON MALLET | . | SUTTON MALLET . | E13652 | 153941RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E13652
15397 | STAWELL | FORD LANE | STAWELL FORD LANE | E4281 | 153970RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E4281
15399 | PURITON | RYE | PURITON RYE | E6642 | 153991RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E6642
15400 | BRIDGWATER | WEST QUAY DRAWBRIDGE | BRIDGWATER WEST QUAY DRAWBRIDGE | E35851 | 154002DWF FLOW | l/s | WASTE | Y | WASTE:E35851
15402 | MIDDLEZOY | NETHERMOOR ROAD | MIDDLEZOY NETHERMOOR ROAD | E55926 | 154022RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E55926
15412 | EAST HUNTSPILL | WITHY ROAD | EAST HUNTSPILL WITHY ROAD | E6725 | 154120RISING MAIN FLOW FROM PUMP 1 | l/s | WASTE | Y | WASTE:E6725
15412 | EAST HUNTSPILL | WITHY ROAD | EAST HUNTSPILL WITHY ROAD | E6726 | 154120RISING MAIN FLOW FROM PUMP 2 | l/s | WASTE | Y | WASTE:E6726
15415 | BRIDGWATER | COLLEY LANE | BRIDGWATER COLLEY LANE | E11634 | 154151DWF FLOW | l/s | WASTE | Y | WASTE:E11634
15421 | STONE | OLD MILL | STONE OLD MILL | E7336 | 154210RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E7336
15426 | NEWPORT | SOUTH | NEWPORT SOUTH | E7284 | 154260RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E7284
15434 | NEWPORT | NORTH | NEWPORT NORTH | E35567 | 154341RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E35567
15441 | CHEDDON FITZPAINE | CHEDDON FARM | CHEDDON FITZPAINE CHEDDON FARM | E6919 | 154410FLOW MONITOR | l/s | WASTE | Y | WASTE:E6919
15449 | MEARE GREEN | WRANTAGE | MEARE GREEN WRANTAGE | E6968 | 154490RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E6968
15450 | NORTON FITZWARREN | LANGFORD LANE | NORTON FITZWARREN LANGFORD LANE | E4856 | 154500FLOW METER | l/s | WASTE | Y | WASTE:E4856
15454 | CREECH ST MICHAEL | NORTH END | CREECH ST MICHAEL NORTH END | E7996 | 154540RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E7996
15468 | BRADFORD ON TONE | HOCKHOLLER A38 | BRADFORD ON TONE HOCKHOLLER A38 | E7083 | 154680RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E7083
15495 | NETHERBURY | BEAMINSTER | NETHERBURY BEAMINSTER | E35719 | 154952RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E35719
15497 | MARTINSTOWN | B3159 | MARTINSTOWN B3159 | E20558 | 154972UNCALIBRATED FORWARD FLOW | l/s | WASTE | Y | WASTE:E20558
15505 | SYMONDSBURY | WEST ROAD FOUNDRY | SYMONDSBURY WEST ROAD FOUNDRY | E18268 | 155051RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E18268
15507 | BRIDPORT | WEST BAY SLUICES | BRIDPORT WEST BAY SLUICES | E18516 | 155071WEST BAY SLUICES PASS FWD FLOW | l/s | WASTE | Y | WASTE:E18516
15511 | MONKSILVER | B3188 | MONKSILVER B3188 | E9773 | 155110PASS FORWARD FLOW ANLG | l/s | WASTE | Y | WASTE:E9773
15516 | BILBROOK | . | BILBROOK . | E55929 | 155160RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E55929
15544 | TEMPLE CLOUD | TEMPLE BRIDGE | TEMPLE CLOUD TEMPLE BRIDGE | E19749 | 155441RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E19749
15555 | WYKE REGIS | HILLCREST ROAD | WYKE REGIS HILLCREST ROAD | E52261 | 155551OUTLET FLOW ANG | l/s | WASTE | Y | WASTE:E52261
15572 | LOCKING | LOCKING VILLAGE | LOCKING LOCKING VILLAGE | E22743 | 155721PUMP 1 RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E22743
15572 | LOCKING | LOCKING VILLAGE | LOCKING LOCKING VILLAGE | E22750 | 155721PUMP 2 RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E22750
15572 | LOCKING | LOCKING VILLAGE | LOCKING LOCKING VILLAGE | E5411 | 155721LOCKING SPS FLOW | l/s | WASTE2 | Y | WASTE2:E5411
15573 | BLEADON | PURN | BLEADON PURN | E13827 | 155731PUMP 1 RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E13827
15573 | BLEADON | PURN | BLEADON PURN | E13828 | 155731PUMP 2 RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E13828
15576 | CONGRESBURY | NORTH | CONGRESBURY NORTH | E22237 | 155761RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E22237
15577 | SANDFORD | SANDMEAD LANE | SANDFORD SANDMEAD LANE | E23919 | 155771RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E23919
15582 | BANWELL | RIVERSIDE | BANWELL RIVERSIDE | E13822 | 155821RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E13822
15582 | BANWELL | RIVERSIDE | BANWELL RIVERSIDE | E13823 | 155821INCOMING RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E13823
15588 | WORLE | NORTH (FW) | WORLE NORTH (FW) | E51164 | 155880RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E51164
15593 | TICKENHAM | EAST | TICKENHAM EAST | E8566 | 155930RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E8566
15602 | KEWSTOKE | CROOKS LANE | KEWSTOKE CROOKS LANE | E22650 | 156021PASS FOWARD FLOW ANLG | l/s | WASTE | Y | WASTE:E22650
15621 | CLEVEDON | LADYE BAY | CLEVEDON LADYE BAY | E50151 | 156212PASS FORWARD FLOW | l/s | WASTE | Y | WASTE:E50151
15642 | POOLE | STERTE F W | POOLE STERTE F W | E50201 | 156420RISING MAIN FLOW AI | l/s | WASTE | Y | WASTE:E50201
15645 | PILL | AVON ROAD | PILL AVON ROAD | E22290 | 156452RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E22290
15649 | WEST HUNTSPILL | ROSE FARM | WEST HUNTSPILL ROSE FARM | E6713 | 156490RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E6713
15654 | ILMINSTER | WESTPORT | ILMINSTER WESTPORT | E19189 | 156541FLOW ANG | l/s | WASTE | Y | WASTE:E19189
15657 | WEST HUNTSPILL | WHITE COTTAGE | WEST HUNTSPILL WHITE COTTAGE | E6714 | 156570RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E6714
15686 | COMPTON DUNDON | HAM LANE | COMPTON DUNDON HAM LANE | E19240 | 156861RISING MAIN FLOWMETER ANLG | l/s | WASTE | Y | WASTE:E19240
15715 | BRIDGWATER | HORSEY BATH ROAD | BRIDGWATER HORSEY BATH ROAD | E19514 | 157151RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E19514
15726 | PORTISHEAD | LAKE GROUNDS | PORTISHEAD LAKE GROUNDS | E13756 | 157262RISING MAIN FLOW METER | l/s | WASTE | Y | WASTE:E13756
15805 | BRIDGWATER | SHOWGROUND NO1 | BRIDGWATER SHOWGROUND NO1 | E11347 | 158051RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E11347
15810 | MELKSHAM | PRIMROSE DRIVE | MELKSHAM PRIMROSE DRIVE | E7283 | 158100RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E7283
16050 | BATH | EA DEPOT | BATH EA DEPOT | E23548 | 160500RISING MAIN FLOW AN | l/s | WASTE | Y | WASTE:E23548
16057 | BATH | TECHNOLOGY HOUSE | BATH TECHNOLOGY HOUSE | E23517 | 160570RISING MAIN FLOW AN | l/s | WASTE | Y | WASTE:E23517
16920 | BRADFORD-ON-AVON | BARTON FARM TERMINAL P STN | BRADFORD-ON-AVON BARTON FARM TERMINAL P STN | E53552 | 169201SUMMATED DWF FLOW AI | l/s | WASTE | Y | WASTE:E53552
16920 | BRADFORD-ON-AVON | BARTON FARM TERMINAL P STN | BRADFORD-ON-AVON BARTON FARM TERMINAL P STN | E53553 | 169201SUMMATED STORM FLOW AI | l/s | WASTE | Y | WASTE:E53553
17034 | LYMPSHAM | INNSBRUCK | LYMPSHAM INNSBRUCK | E20491 | 170340RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E20491
17093 | LOCKING | WOOLVERS WAY | LOCKING WOOLVERS WAY | E21916 | 170930RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E21916
17122 | WAYTOWN | SLAPE MILL PARK | WAYTOWN SLAPE MILL PARK | E26783 | 171220RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E26783
17140 | BRIDGWATER | EXPRESS PARK | BRIDGWATER EXPRESS PARK | E24980 | 171400EFF FLOW RATE LS | l/s | WASTE | Y | WASTE:E24980
17185 | SHEPTON MALLET | SHOWGROUND | SHEPTON MALLET SHOWGROUND | E24514 | 171851PUMP FLOW TO EVERCREECH | l/s | WASTE | Y | WASTE:E24514
17213 | WESTON-SUPER-MARE | MOOR LANE AREA 22 | WESTON-SUPER-MARE MOOR LANE AREA 22 | E25432 | 172130RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E25432
17323 | LOCKING | FIR TREE AVENUE | LOCKING FIR TREE AVENUE | E28021 | 173230RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E28021
17498 | HUISH EPISCOPI | THE HILL STORM STORAGE TANK (PUMPED) | HUISH EPISCOPI THE HILL STORM STORAGE TANK (PUMPED) | E31010 | 174980RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E31010
17585 | PYMORE | THREAD MILL LANE | PYMORE THREAD MILL LANE | E31228 | 175850RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E31228
17588 | WEST WICK | WOLVERS HILL ROAD | WEST WICK WOLVERS HILL ROAD | E33307 | 175880RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E33307
17613 | MALMESBURY | COWBRIDGE NEW | MALMESBURY COWBRIDGE NEW | E30138 | 176130RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E30138
18710 | BRISTOL | ROYAL EDWARD DOCK ST ANDREWS ROAD | BRISTOL ROYAL EDWARD DOCK ST ANDREWS ROAD | E26344 | 187100RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E26344
19106 | CONGRESBURY | STATION CLOSE WESTON ROAD | CONGRESBURY STATION CLOSE WESTON ROAD | E9326 | 191060RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E9326
19129 | WESTON-SUPER-MARE | DIAMOND BATCH | WESTON-SUPER-MARE DIAMOND BATCH | E20004 | 191291RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E20004
19296 | CLEVEDON | KENN ROAD | CLEVEDON KENN ROAD | E12500 | 192960RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E12500
19300 | STAWELL | MOOR LANE | STAWELL MOOR LANE | E10143 | 193000RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E10143
19453 | WESTON-SUPER-MARE | EBDON GROUNDS | WESTON-SUPER-MARE EBDON GROUNDS | E12126 | 194530RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E12126
19505 | LOCKING | RAF | LOCKING RAF | E11726 | 195050RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E11726
19542 | AVONMOUTH | CABOT PARK NO.1 | AVONMOUTH CABOT PARK NO.1 | E12284 | 195420RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E12284
19712 | LITTON | . | LITTON . | E13467 | 197120FLOWMETER | l/s | WASTE | Y | WASTE:E13467
19827 | ST GEORGES | BRIMBLEWORTH FARM | ST GEORGES BRIMBLEWORTH FARM | E8674 | 198270SPS FLOW | l/s | WASTE | Y | WASTE:E8674
19829 | ST GEORGES | WILLOW CLOSE | ST GEORGES WILLOW CLOSE | E7816 | 198290RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E7816
19830 | WORLE | MOOR LANE | WORLE MOOR LANE | E4908 | 198300RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E4908
19978 | ROOKSBRIDGE | BRISTOL ROAD | ROOKSBRIDGE BRISTOL ROAD | E17075 | 199780RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E17075
15468 | BRADFORD ON TONE | HOCKHOLLER A38 | BRADFORD ON TONE HOCKHOLLER A38 | E7456 | 15468ARISING MAIN FLOW AI | l/s | WASTE2 | Y | WASTE2:E7456
15366 | BERROW | BARTON ROAD IN BETWEEN 60 BARTON ROAD & BONER COTTAGE | BERROW BARTON ROAD IN BETWEEN 60 BARTON ROAD & BONER COTTAGE | E7335 | 153660RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E7335
15439 | HENLADE | . | HENLADE . | E38432 | 154391RISING MAIN FLOWMETER ANLG | l/s | WASTE | Y | WASTE:E38432
15551 | WEYMOUTH | PRESTON FISHERBRIDGE ESTATE | WEYMOUTH PRESTON FISHERBRIDGE ESTATE | E34649 | 155541PASS FWD FLW TO FISHER BRG SPS | l/s | WASTE | Y | WASTE:E34649
13273 | SHIPTON GORGE | OFF MARKETS LANE | SHIPTON GORGE OFF MARKETS LANE | E32021 | 156831SHIPTON GORGE RISING MAIN FLOWMETER | l/s | WASTE | Y | WASTE:E32021
15722 | WELLINGTON | POOLE BRICKYARD | WELLINGTON POOLE BRICKYARD | E7340 | 157220RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E7340
17034 | LYMPSHAM | INNSBRUCK | LYMPSHAM INNSBRUCK | E20491 | 170340RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E20491
19129 | WESTON-SUPER-MARE | DIAMOND BATCH | WESTON-SUPER-MARE DIAMOND BATCH | E20004 | 191291RISING MAIN FLOW ANLG | l/s | WASTE | Y | WASTE:E20004
10312 | IRON ACTON | HOOVERS LANE | IRON ACTON HOOVERS LANE | E53854 | 103120HOOVERS LANE FLOWMETER ANG | l/s | WASTE | Y | WASTE:E53854
13074 | COMBWICH | QUAY ROAD | COMBWICH QUAY ROAD | E53482 | 130744FLOWMETER ANG | l/s | WASTE | Y | WASTE:E53482
13093 | DONIFORD | . | DONIFORD . | E14297 | 130931FLOW TO OUTFALL | l/s | WASTE | Y | WASTE:E14297
13093 | DONIFORD | . | DONIFORD . | E14298 | 130931FLOW TO WATCHET | l/s | WASTE | Y | WASTE:E14298
13138 | GRITTLETON | WOODMANS LODGE | GRITTLETON WOODMANS LODGE | E52821 | 131381DWF FLOW ANG | l/s | WASTE | Y | WASTE:E52821
13153 | HOLTON HEATH | HOLTON HEATH SEWAGE PUMPING STATION | HOLTON HEATH HOLTON HEATH SEWAGE PUMPING STATION | E35512 | 131532OUTFLOW METER AN | l/s | WASTE | Y | WASTE:E35512
13375 | LYNEHAM | PRESTON LANE | LYNEHAM PRESTON LANE | E3095 | 133751PASS FWD FLW ANLG | l/s | WASTE | Y | WASTE:E3095
13668 | DORCHESTER | POUNDBURY ROAD | DORCHESTER POUNDBURY ROAD | E6136 | 13668ARISING MAIN FLOW AI | l/s | WASTE2 | Y | WASTE2:E6136
14002 | BATH | MIDLAND ROAD TWERTON | BATH MIDLAND ROAD TWERTON | E6616 | 14002ATOTAL PUMPING FLOW ANG | l/s | WASTE2 | Y | WASTE2:E6616
14041 | SIXPENNY HANDLEY | . | SIXPENNY HANDLEY . | E17891 | 140411EA189STW FINAL EFF FLOW | l/s | WASTE | Y | WASTE:E17891
14042 | CRANBORNE | ALDERHOLT RD HIGHER HOLWELL | CRANBORNE ALDERHOLT RD HIGHER HOLWELL | E32131 | 140421FFT FLOW METER ANG | l/s | WASTE | Y | WASTE:E32131
14110 | STOKE ST MICHAEL | STOKE HILL | STOKE ST MICHAEL STOKE HILL | E4248 | 141100RISING MAIN FLOWMETER ANLG | l/s | WASTE | Y | WASTE:E4248
14114 | GLASTONBURY | EDGARLEY MILLFIELD SCHOOL | GLASTONBURY EDGARLEY MILLFIELD SCHOOL | E59956 | 141141FLOWMETER | l/s | WASTE | Y | WASTE:E59956
14227 | STUDLAND | WADMORE LANE | STUDLAND WADMORE LANE | E18164 | 142271RISING MAIN FLOW ANG | l/s | WASTE | Y | WASTE:E18164
14248 | EAST BURTON | CROSS ROADS | EAST BURTON CROSS ROADS | E29298 | 133591EAST BURTON FLOW | l/s | WASTE | Y | WASTE:E29298
14289 | ILCHESTER | ILCHESTER MAIN | ILCHESTER ILCHESTER MAIN | E25349 | 142893RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E25349
14309 | DONHEAD ST ANDREW | . | DONHEAD ST ANDREW . | E13313AINLET FLOWMETER | 143091RISING MAIN FLOW | l/s | WASTE | Y | WASTE:E13313AINLET FLOWMETER
14353 | DOWNTON | SOUTH LANE | DOWNTON SOUTH LANE | E51290 | 143532FLOW METER | l/s | WASTE | Y | WASTE:E51290
14370 | MAIDEN BRADLEY | FROME ROAD | MAIDEN BRADLEY FROME ROAD | E16866 | 143701FLOW | l/s | WASTE | Y | WASTE:E16866
14374 | HIGHBRIDGE | NEWTON | HIGHBRIDGE NEWTON | E21853 | 143740FLOW TO TREATMENT | l/s | WASTE | Y - Treatment | WASTE:E21853
14391 | STOKE ST GREGORY | NO 1 LANE END | STOKE ST GREGORY NO 1 LANE END | E13802 | 143911FLOW TO WORKS | l/s | WASTE | Y | WASTE:E13802
14414 | CHARMINSTER | NORTH STREET | CHARMINSTER NORTH STREET | E31413 | 144142OUTFLOW | l/s | WASTE | Y | WASTE:E31413
14415 | LITTON CHENEY | CHICKSBRIDGE | LITTON CHENEY CHICKSBRIDGE | E16749 | 144152OUTLET FLOW | l/s | WASTE | Y | WASTE:E16749
14420 | MINEHEAD | QUAY WEST | MINEHEAD QUAY WEST | E52171 | 144200PASS FWD FLOW ANLG | l/s | WASTE | Y | WASTE:E52171
14493 | KINGSTON | BRIDGE | KINGSTON BRIDGE | E55944 | 144930DISCHARGE FLOW ANG | l/s | WASTE | Y | WASTE:E55944
14510 | TROWBRIDGE | TERMINAL AT BRADFORD ROAD | TROWBRIDGE TERMINAL AT BRADFORD ROAD | E52946 | 145100EA340 MCERT MAINS 1 FLOW AI | l/s | WASTE | Y | WASTE:E52946
14510 | TROWBRIDGE | TERMINAL AT BRADFORD ROAD | TROWBRIDGE TERMINAL AT BRADFORD ROAD | E52947 | 145100EA341 MCERT MAINS 2 FLOW AI | l/s | WASTE | Y | WASTE:E52947
14542 | COAT | CRIPPLE STREET (OLD STW SITE) | COAT CRIPPLE STREET (OLD STW SITE) | E3401 | 145420PUMPED FLOW | l/s | WASTE | Y | WASTE:E3401
14621 | PORTISHEAD | TOWN HARBOUR ROAD | PORTISHEAD TOWN HARBOUR ROAD | E11502 | 146210PHEAD SPS STM SCRN FLOW | l/s | WASTE | Y | WASTE:E11502
14621 | PORTISHEAD | TOWN HARBOUR ROAD | PORTISHEAD TOWN HARBOUR ROAD | E11503 | 146210PHEAD SPS FOUL RIS FLOW | l/s | WASTE | Y | WASTE:E11503
15074 | WEST MOORS | THE FOREST | WEST MOORS THE FOREST | E7994 | 150741PUMP 1 FLOW | l/s | WASTE | Y | WASTE:E7994
15074 | WEST MOORS | THE FOREST | WEST MOORS THE FOREST | E7995 | 150741PUMP 2 FLOW | l/s | WASTE | Y | WASTE:E7995
15190 | MILBORNE ST ANDREW | MANOR FARM | MILBORNE ST ANDREW MANOR FARM | E5464 | 151900RISING MAIN DWF FLOW | l/s | WASTE | Y | WASTE:E5464
15190 | MILBORNE ST ANDREW | MANOR FARM | MILBORNE ST ANDREW MANOR FARM | E5465 | 151900RISING MAIN STORM FLOW | l/s | WASTE | Y | WASTE:E5465
15439 | HENLADE | . | HENLADE . | E38432 | 154391RISING MAIN FLOWMETER ANLG | l/s | WASTE | Y | WASTE:E38432
15484 | CHARMOUTH | LOWER SEA LANE | CHARMOUTH LOWER SEA LANE | E15513 | 154841OUTLET FLOW | l/s | WASTE | Y | WASTE:E15513
15520 | MINEHEAD | VULCAN ROAD | MINEHEAD VULCAN ROAD | E32836 | 155201RISING MAIN FLOWMETER ANLG | l/s | WASTE | Y | WASTE:E32836
17367 | COKERS FROME | . | COKERS FROME . | E31428 | 173671OUTFLOW | l/s | WASTE | Y | WASTE:E31428
17797 | PILNING | TESCO CDC SPS | PILNING TESCO CDC SPS | E32586 | 177970FLOW METER ANG | l/s | WASTE | Y | WASTE:E32586
18015 | BOURNEMOUTH | COOPER DEAN DETENTION TANK | BOURNEMOUTH COOPER DEAN DETENTION TANK | E17827 | 180152FLOW TO OUTFALL | l/s | WASTE | Y | WASTE:E17827
15371 | CROSS | CROSS EAST | CROSS CROSS EAST | E6352 | 153710RISING MAIN FLOW | l/s | WASTE | N | WASTE:E6352
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20347 | 101330STATION FLOW | l/s | WASTE2 | N | WASTE2:E20347
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20366 | 101330REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E20366
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20367 | 101330DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E20367
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20368 | 101330DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E20368
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20375 | 101330PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20375
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20376 | 101330PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20376
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20377 | 101330PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20377
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20378 | 101330PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E20378
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20379 | 101330PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E20379
10133 | SALISBURY | THE CLOSE | SALISBURY THE CLOSE | E20380 | 101330PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E20380
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20432 | 101820STATION FLOW | l/s | WASTE2 | N | WASTE2:E20432
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20451 | 101820REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E20451
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20452 | 101820DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E20452
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20453 | 101820DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E20453
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20460 | 101820PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20460
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20461 | 101820PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20461
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20462 | 101820PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20462
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20463 | 101820PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E20463
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20464 | 101820PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E20464
10182 | TISBURY | WARDOUR | TISBURY WARDOUR | E20465 | 101820PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E20465
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20602 | 102920STATION FLOW | l/s | WASTE2 | N | WASTE2:E20602
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20621 | 102920REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E20621
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20622 | 102920DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E20622
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20623 | 102920DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E20623
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20630 | 102920PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20630
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20631 | 102920PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20631
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20632 | 102920PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20632
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20633 | 102920PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E20633
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20634 | 102920PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E20634
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | FORDINGBRIDGE DOWNWOOD CLOSE | E20635 | 102920PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E20635
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20857 | 104600STATION FLOW | l/s | WASTE2 | N | WASTE2:E20857
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20876 | 104600REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E20876
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20877 | 104600DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E20877
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20878 | 104600DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E20878
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20885 | 104600PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20885
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20886 | 104600PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20886
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20887 | 104600PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20887
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20888 | 104600PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E20888
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20889 | 104600PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E20889
10460 | SALISBURY | HEATH VEW DRIVE | SALISBURY HEATH VEW DRIVE | E20890 | 104600PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E20890
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20262 | 107120STATION FLOW | l/s | WASTE2 | N | WASTE2:E20262
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20281 | 107120REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E20281
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20282 | 107120DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E20282
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20283 | 107120DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E20283
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20290 | 107120PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20290
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20291 | 107120PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20291
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20292 | 107120PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20292
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20293 | 107120PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E20293
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20294 | 107120PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E20294
10712 | GILLINGHAM | WYKE HALL | GILLINGHAM WYKE HALL | E20295 | 107120PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E20295
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8007 | 108400STATION FLOW | l/s | WASTE2 | N | WASTE2:E8007
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8026 | 108400REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E8026
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8027 | 108400DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E8027
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8028 | 108400DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E8028
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8035 | 108400PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E8035
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8036 | 108400PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E8036
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8037 | 108400PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E8037
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8038 | 108400PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E8038
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8039 | 108400PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E8039
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | WEYMOUTH ABBOTSBURY ROAD FOUL AND SURFACE | E8040 | 108400PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E8040
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7922 | 116920STATION FLOW | l/s | WASTE2 | N | WASTE2:E7922
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7941 | 116920REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E7941
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7942 | 116920DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E7942
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7943 | 116920DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E7943
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7950 | 116920PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E7950
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7951 | 116920PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E7951
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7952 | 116920PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E7952
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7953 | 116920PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E7953
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7954 | 116920PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E7954
11692 | SALISBURY | GLENMORE BUSINESS PARK | SALISBURY GLENMORE BUSINESS PARK | E7955 | 116920PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E7955
12722 | BRIDGWATER | DURLEIGH ROAD (PUMPED NRV) | BRIDGWATER DURLEIGH ROAD (PUMPED NRV) | E21307 | 127220DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E21307
12722 | BRIDGWATER | DURLEIGH ROAD (PUMPED NRV) | BRIDGWATER DURLEIGH ROAD (PUMPED NRV) | E21308 | 127220DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E21308
12722 | BRIDGWATER | DURLEIGH ROAD (PUMPED NRV) | BRIDGWATER DURLEIGH ROAD (PUMPED NRV) | E21312 | 127220PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E21312
12865 | BRIDGWATER | OLD TAUNTON ROAD | BRIDGWATER OLD TAUNTON ROAD | E3321 | 128650INFLOW RATE ANG | l/s | WASTE2 | N | WASTE2:E3321
14002 | BATH | MIDLAND ROAD TWERTON | BATH MIDLAND ROAD TWERTON | E6664 | 14002ATWINNED SECTION UPSTR FLOW ANG | l/s | WASTE2 | N | WASTE2:E6664
14002 | BATH | MIDLAND ROAD TWERTON | BATH MIDLAND ROAD TWERTON | E6667 | 14002ATWINNED SECTION DOWNSTR FLOW ANG | l/s | WASTE2 | N | WASTE2:E6667
15237 | POOLE | MAGNA ROAD | POOLE MAGNA ROAD | E13836 | 152371PULSAR 500 TRIAL FLOW | l/s | WASTE | N | WASTE:E13836
15313 | HUISH EPISCOPI | PIBSBURY | HUISH EPISCOPI PIBSBURY | E19307 | 153131COMBINED UPSTREAM FLOW | l/s | WASTE | N | WASTE:E19307
15341 | BURNHAM-ON-SEA | LYNTON ROAD | BURNHAM-ON-SEA LYNTON ROAD | E6315 | 153410RISING MAIN FLOW | l/s | WASTE | N | WASTE:E6315
15629 | HAMBRIDGE | . | HAMBRIDGE . | E11969 | 156291RISING MAIN FLOWMETER AI | l/s | WASTE | N | WASTE:E11969
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21127 | 156371STATION FLOW | l/s | WASTE2 | N | WASTE2:E21127
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21146 | 156371REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E21146
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21147 | 156371DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E21147
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21148 | 156371DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E21148
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21155 | 156371PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E21155
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21156 | 156371PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E21156
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21157 | 156371PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E21157
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21158 | 156371PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E21158
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21159 | 156371PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E21159
15637 | STURMINSTER NEWTON | ROLLS MILL | STURMINSTER NEWTON ROLLS MILL | E21160 | 156371PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E21160
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20687 | 157680STATION FLOW | l/s | WASTE2 | N | WASTE2:E20687
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20706 | 157680REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E20706
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20707 | 157680DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E20707
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20708 | 157680DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E20708
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20715 | 157680PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20715
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20716 | 157680PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20716
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20717 | 157680PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20717
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20718 | 157680PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E20718
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20719 | 157680PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E20719
15768 | SALISBURY | KIVEL COURT SALISBURY | SALISBURY KIVEL COURT SALISBURY | E20720 | 157680PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E20720
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20772 | 157710STATION FLOW | l/s | WASTE2 | N | WASTE2:E20772
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20791 | 157710REAL STATION FLOW | l/s | WASTE2 | N | WASTE2:E20791
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20792 | 157710DERIVED STATION FLOW | l/s | WASTE2 | N | WASTE2:E20792
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20793 | 157710DERIVED INLET FLOW | l/s | WASTE2 | N | WASTE2:E20793
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20800 | 157710PUMP 1 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20800
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20801 | 157710PUMP 2 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20801
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20802 | 157710PUMP 3 DERIVED FLOW | l/s | WASTE2 | N | WASTE2:E20802
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20803 | 157710PUMP 1 FLOW | l/s | WASTE2 | N | WASTE2:E20803
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20804 | 157710PUMP 2 FLOW | l/s | WASTE2 | N | WASTE2:E20804
15771 | SALISBURY | GRANGE GARDENS | SALISBURY GRANGE GARDENS | E20805 | 157710PUMP 3 FLOW | l/s | WASTE2 | N | WASTE2:E20805
16920 | BRADFORD-ON-AVON | BARTON FARM TERMINAL P STN | BRADFORD-ON-AVON BARTON FARM TERMINAL P STN | E53533 | 169201DWF PUMP 1 FLOW AI | l/s | WASTE | N | WASTE:E53533
16920 | BRADFORD-ON-AVON | BARTON FARM TERMINAL P STN | BRADFORD-ON-AVON BARTON FARM TERMINAL P STN | E53535 | 169201DWF PUMP 2 FLOW AI | l/s | WASTE | N | WASTE:E53535
16920 | BRADFORD-ON-AVON | BARTON FARM TERMINAL P STN | BRADFORD-ON-AVON BARTON FARM TERMINAL P STN | E53537 | 169201DWF PUMP 3 FLOW AI | l/s | WASTE | N | WASTE:E53537
16920 | BRADFORD-ON-AVON | BARTON FARM TERMINAL P STN | BRADFORD-ON-AVON BARTON FARM TERMINAL P STN | E53539 | 169201STORM PUMP 1 FLOW AI | l/s | WASTE | N | WASTE:E53539
16920 | BRADFORD-ON-AVON | BARTON FARM TERMINAL P STN | BRADFORD-ON-AVON BARTON FARM TERMINAL P STN | E53541 | 169201STORM PUMP 2 FLOW AI | l/s | WASTE | N | WASTE:E53541
19827 | ST GEORGES | BRIMBLEWORTH FARM | ST GEORGES BRIMBLEWORTH FARM | E8673 | 198270RISING MAIN FLOW | l/s | WASTE | N | WASTE:E8673
15692 | ISLE BREWERS | . | ISLE BREWERS . | E11960 | 156921RISING MAIN FLOW | l/s | WASTE | N | WASTE:E11960
10312 | IRON ACTON | HOOVERS LANE | IRON ACTON HOOVERS LANE | E53850 | 103120COGMILL FARM FVRS3 FLOWMETER ANG | l/s | WASTE | N | WASTE:E53850
10312 | IRON ACTON | HOOVERS LANE | IRON ACTON HOOVERS LANE | E53852 | 103120COGMILL FARM FVS FLOWMETER ANG | l/s | WASTE | N | WASTE:E53852
10908 | WESTON-SUPER-MARE | AISECOME WAY SURFACE WATER | WESTON-SUPER-MARE AISECOME WAY SURFACE WATER | E38933 | 109080PUMP 1 FLOW ANG | l/s | WASTE | N | WASTE:E38933
10908 | WESTON-SUPER-MARE | AISECOME WAY SURFACE WATER | WESTON-SUPER-MARE AISECOME WAY SURFACE WATER | E38934 | 109080PUMP 2 FLOW ANG | l/s | WASTE | N | WASTE:E38934
11559 | TAUNTON | MOUNTSFIELD ROAD | TAUNTON MOUNTSFIELD ROAD | E1700 | 115590INFLOW RATE | l/s | WASTE2 | N | WASTE2:E1700
13033 | BRADFORD PEVERELL | GILES CROSS | BRADFORD PEVERELL GILES CROSS | E31400 | 130332STORM FLOW | l/s | WASTE | N | WASTE:E31400
13138 | GRITTLETON | WOODMANS LODGE | GRITTLETON WOODMANS LODGE | E2940 | 131380INLET FLOW | l/s | WASTE | N | WASTE:E2940
13283 | SPAXTON | . | SPAXTON . | E4867 | 132830OVER PUMPING BLACKMORE LANE FLOW | l/s | WASTE | N | WASTE:E4867
13340 | WESTON-SUPER-MARE | BLACK ROCK WINDWHISTLE ROAD | WESTON-SUPER-MARE BLACK ROCK WINDWHISTLE ROAD | E34387 | 133400STORM FLOW TO OUTFALL | l/s | WASTE | N | WASTE:E34387
13340 | WESTON-SUPER-MARE | BLACK ROCK WINDWHISTLE ROAD | WESTON-SUPER-MARE BLACK ROCK WINDWHISTLE ROAD | E34418 | 133400WSM RETURN FLOW | l/s | WASTE | N | WASTE:E34418
13340 | WESTON-SUPER-MARE | BLACK ROCK WINDWHISTLE ROAD | WESTON-SUPER-MARE BLACK ROCK WINDWHISTLE ROAD | E34429 | 133400STORM FLOW TO HEADWORKS ANG | l/s | WASTE | N | WASTE:E34429
13624 | CHRISTCHURCH | CLIFF DRIVE (FOUL AND SURFACE) | CHRISTCHURCH CLIFF DRIVE (FOUL AND SURFACE) | E21389 | 136240DISCHARGE FLOW | l/s | WASTE | N | WASTE:E21389
13624 | CHRISTCHURCH | CLIFF DRIVE (FOUL AND SURFACE) | CHRISTCHURCH CLIFF DRIVE (FOUL AND SURFACE) | E21390 | 136240UNTREATED FLOW | l/s | WASTE | N | WASTE:E21390
13624 | CHRISTCHURCH | CLIFF DRIVE (FOUL AND SURFACE) | CHRISTCHURCH CLIFF DRIVE (FOUL AND SURFACE) | E21392 | 136240DISCHARGE FLOW FROM E10078 | l/s | WASTE | N | WASTE:E21392
13624 | CHRISTCHURCH | CLIFF DRIVE (FOUL AND SURFACE) | CHRISTCHURCH CLIFF DRIVE (FOUL AND SURFACE) | E21394 | 136240TREATED FLOW | l/s | WASTE | N | WASTE:E21394
13639 | DURLEIGH | ENMORE ROAD 1 | DURLEIGH ENMORE ROAD 1 | E3158 | 136390INFLOW RATE ANG | l/s | WASTE2 | N | WASTE2:E3158
14002 | BATH | MIDLAND ROAD TWERTON | BATH MIDLAND ROAD TWERTON | E6611 | 14002AOLD RISING MAIN BACKUP FLOW ANG | l/s | WASTE2 | N | WASTE2:E6611
14075 | GLASTONBURY | NORTH LOAD BRIDGE | GLASTONBURY NORTH LOAD BRIDGE | E6284 | 140751INFLOW RATE ANG | l/s | WASTE2 | N | WASTE2:E6284
14157 | CALNE | ROUGH LEAZE | CALNE ROUGH LEAZE | E25468 | 141571COMPTON BASSETT FLOW | l/s | WASTE | N | WASTE:E25468
14272 | BRIANTSPUDDLE | . | BRIANTSPUDDLE . | E15332 | 142721RISING MAIN FLOW | l/s | WASTE | N | WASTE:E15332
14323 | AMESBURY | FLOWER LANE | AMESBURY FLOWER LANE | E9447 | 143230FLOW CHANNEL A | l/s | WASTE | Y | WASTE:E9447
14391 | STOKE ST GREGORY | NO 1 LANE END | STOKE ST GREGORY NO 1 LANE END | E13803 | 143911FLOW TO STORM | l/s | WASTE | N | WASTE:E13803
14510 | TROWBRIDGE | TERMINAL AT BRADFORD ROAD | TROWBRIDGE TERMINAL AT BRADFORD ROAD | E52940 | 145100LAUNDER WASHWATER FLOW AI | l/s | WASTE | N | WASTE:E52940
14577 | FORD | GREEN LANE | FORD GREEN LANE | E16410 | 145771FLOW FROM CASTLE VIEW SPS | l/s | WASTE | N | WASTE:E16410
15150 | OLDBURY | THE NAITE | OLDBURY THE NAITE | E51596 | 151502VACCUM TNK FLOW | l/s | WASTE | N | WASTE:E51596
15190 | MILBORNE ST ANDREW | MANOR FARM | MILBORNE ST ANDREW MANOR FARM | E7205 | 151901STORM OUTFLOW | l/s | WASTE | N | WASTE:E7205
15638 | MANNINGFORD | NO 4 PS PEWSEY | MANNINGFORD NO 4 PS PEWSEY | E19536 | 156380RISING MAIN FLOW ANG | l/s | WASTE | N | WASTE:E19536
16864 | WEYMOUTH | WESTON ROAD | WEYMOUTH WESTON ROAD | E5413 | 168641WEYMOUTH WESTON ROAD CSO FLOW | l/s | WASTE2 | N | WASTE2:E5413
16944 | CLEEVE | OLD CLEEVE FARM | CLEEVE OLD CLEEVE FARM | E5417 | 169441OLD CLEEVE FARM CSO FLOW | l/s | WASTE2 | N | WASTE2:E5417
17288 | TRULL | TAUNTON DEAN MOTORWAY SERVICES | TRULL TAUNTON DEAN MOTORWAY SERVICES | E8028 | 172880RISING MAIN FLOW | l/s | WASTE | N | WASTE:E8028
17552 | WESTON-SUPER-MARE | GREENFIELD PLACE O/S 15 | WESTON-SUPER-MARE GREENFIELD PLACE O/S 15 | E5419 | 175521GREENFIELD PLACE CSO FLOW | l/s | WASTE2 | N | WASTE2:E5419
17638 | PIDDLETRENTHIDE | R/O TRENT HOUSE (CSO6) | PIDDLETRENTHIDE R/O TRENT HOUSE (CSO6) | E25700 | 176381FLOW INFLOWRATE | l/s | WASTE | N | WASTE:E25700
17638 | PIDDLETRENTHIDE | R/O TRENT HOUSE (CSO6) | PIDDLETRENTHIDE R/O TRENT HOUSE (CSO6) | E25708 | 176381FLOW PUMP 1 FLOWRATE | l/s | WASTE | N | WASTE:E25708
17638 | PIDDLETRENTHIDE | R/O TRENT HOUSE (CSO6) | PIDDLETRENTHIDE R/O TRENT HOUSE (CSO6) | E25710 | 176381FLOW PUMP 2 FLOWRATE | l/s | WASTE | N | WASTE:E25710
17638 | PIDDLETRENTHIDE | R/O TRENT HOUSE (CSO6) | PIDDLETRENTHIDE R/O TRENT HOUSE (CSO6) | E25736 | 176381FLOW VOLUMEPUMPED | l/s | WASTE | N | WASTE:E25736
17638 | PIDDLETRENTHIDE | R/O TRENT HOUSE (CSO6) | PIDDLETRENTHIDE R/O TRENT HOUSE (CSO6) | E25737 | 176381FLOW OVERFLOWVOLUME | l/s | WASTE | N | WASTE:E25737
17638 | PIDDLETRENTHIDE | R/O TRENT HOUSE (CSO6) | PIDDLETRENTHIDE R/O TRENT HOUSE (CSO6) | E25742 | 176381FLOW PUMP 1 VOLUMEPUMPED | l/s | WASTE | N | WASTE:E25742
17638 | PIDDLETRENTHIDE | R/O TRENT HOUSE (CSO6) | PIDDLETRENTHIDE R/O TRENT HOUSE (CSO6) | E25747 | 176381FLOW PUMP 2 VOLUMEPUMPED | l/s | WASTE | N | WASTE:E25747
18015 | BOURNEMOUTH | COOPER DEAN DETENTION TANK | BOURNEMOUTH COOPER DEAN DETENTION TANK | E17828 | 180152CIS FLUM FLOW | l/s | WASTE | N | WASTE:E17828
10567 | #N/A | #N/A | #N/A | E6090 | 105670RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6090
12004 | #N/A | #N/A | #N/A | E15423 | 12004XEA330RETURN RES FLOW | l/s | WASTE |  | WASTE:E15423
12004 | #N/A | #N/A | #N/A | E15424 | 12004XEA331RTN TO ASHFORD RES FLOW | l/s | WASTE |  | WASTE:E15424
12007 | #N/A | #N/A | #N/A | E15422 | 12007XEA321STREAM FLOW FM08 | l/s | WASTE |  | WASTE:E15422
12029 | #N/A | #N/A | #N/A | E15429 | 12029XWASHWATER FLOW | l/s | WASTE |  | WASTE:E15429
12035 | #N/A | #N/A | #N/A | E15427 | 12035XEA333CHLOR OUTLET FLOW | l/s | WASTE |  | WASTE:E15427
12081 | #N/A | #N/A | #N/A | E15426 | 12081XWSHWTR FLOW TO RIVER | l/s | WASTE |  | WASTE:E15426
12089 | #N/A | #N/A | #N/A | E15428 | 12089XEA334WASHWATER TANK OUTFLOW | l/s | WASTE |  | WASTE:E15428
12928 | #N/A | #N/A | #N/A | E3078 | 129280RISING MAIN FLOWMETER | l/s | WASTE2 |  | WASTE2:E3078
12929 | #N/A | #N/A | #N/A | E3094 | 129290RISING MAIN FLOWMETER | l/s | WASTE2 |  | WASTE2:E3094
12930 | #N/A | #N/A | #N/A | E3110 | 129300RADIPOLE DWF RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E3110
12930 | #N/A | #N/A | #N/A | E3111 | 129300RADIPOLE STORM RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E3111
12931 | #N/A | #N/A | #N/A | E3126 | 129310RISING MAIN FLOWMETER | l/s | WASTE2 |  | WASTE2:E3126
12932 | #N/A | #N/A | #N/A | E3142 | 129320RISING MAIN FLOWMETER | l/s | WASTE2 |  | WASTE2:E3142
13001 | #N/A | #N/A | #N/A | E6151 | 130011EA001FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E6151
13001 | #N/A | #N/A | #N/A | E30383 | 130011FLOW TO TREATMENT AI | l/s | WASTE |  | WASTE:E30383
13001 | #N/A | #N/A | #N/A | E30387 | 130011SAND FILTER FEED FLOW AI | l/s | WASTE |  | WASTE:E30387
13001 | #N/A | #N/A | #N/A | E30402 | 130011FLOW TO SAND FILTER AI | l/s | WASTE |  | WASTE:E30402
13001 | #N/A | #N/A | #N/A | E30403 | 130011SAND FILTER 1 INLET FLOW AI | l/s | WASTE |  | WASTE:E30403
13001 | #N/A | #N/A | #N/A | E30404 | 130011SAND FILTER 2 INLET FLOW AI | l/s | WASTE |  | WASTE:E30404
13001 | #N/A | #N/A | #N/A | E30924 | 130011INLET FLOW FOR DOSE SET 1 | l/s | WASTE |  | WASTE:E30924
13001 | #N/A | #N/A | #N/A | E30925 | 130011INLET FLOW FOR DOSE SET 2 | l/s | WASTE |  | WASTE:E30925
13004 | #N/A | #N/A | #N/A | E55500 | 130040PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E55500
13004 | #N/A | #N/A | #N/A | E55508 | 130040PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E55508
13006 | #N/A | #N/A | #N/A | E1001 | 130060EA121MCERT INLET FLOW | l/s | WASTE |  | WASTE:E1001
13007 | #N/A | #N/A | #N/A | E1015 | 130070OUTLET FLOW | l/s | WASTE |  | WASTE:E1015
13007 | #N/A | #N/A | #N/A | E1016 | 130070EA371 FPF INLET FLOW | l/s | WASTE |  | WASTE:E1016
13007 | #N/A | #N/A | #N/A | E1017 | 130070FLOW TO STORM | l/s | WASTE |  | WASTE:E1017
13007 | #N/A | #N/A | #N/A | E1018 | 1300706 DWF OVERFLOW | l/s | WASTE |  | WASTE:E1018
13008 | #N/A | #N/A | #N/A | E19545 | 130081OUTLET FLOW | l/s | WASTE |  | WASTE:E19545
13008 | #N/A | #N/A | #N/A | E19553 | 130081FLOW 1 | l/s | WASTE |  | WASTE:E19553
13008 | #N/A | #N/A | #N/A | E19559 | 130081FLOCCULATION FLOW | l/s | WASTE |  | WASTE:E19559
13008 | #N/A | #N/A | #N/A | E19561 | 130081SLUDGE FEED FLOW | l/s | WASTE |  | WASTE:E19561
13008 | #N/A | #N/A | #N/A | E19569 | 130081FLOW 2 | l/s | WASTE |  | WASTE:E19569
13008 | #N/A | #N/A | #N/A | E37849 | 130081FTT FLOW | l/s | WASTE |  | WASTE:E37849
13008 | #N/A | #N/A | #N/A | E37850 | 130081EA002MCERT FLOW | l/s | WASTE |  | WASTE:E37850
13008 | #N/A | #N/A | #N/A | E37851 | 130081LOW LIFT FLOW | l/s | WASTE |  | WASTE:E37851
13012 | #N/A | #N/A | #N/A | E1030 | 130120EA003INLET FLOW | l/s | WASTE |  | WASTE:E1030
13013 | #N/A | #N/A | #N/A | E9735 | 130130EA122INLET FLOW | l/s | WASTE |  | WASTE:E9735
13013 | #N/A | #N/A | #N/A | E53738 | 130130PST TANK 1 FLOW MEASURE AI | l/s | WASTE |  | WASTE:E53738
13013 | #N/A | #N/A | #N/A | E53740 | 130130PST TANK 2 FLOW MEASURE AI | l/s | WASTE |  | WASTE:E53740
13013 | #N/A | #N/A | #N/A | E53742 | 130130PST TANK 3 FLOW MEASURE AI | l/s | WASTE |  | WASTE:E53742
13013 | #N/A | #N/A | #N/A | E53744 | 130130PST TANK 4 FLOW MEASURE AI | l/s | WASTE |  | WASTE:E53744
13013 | #N/A | #N/A | #N/A | E53746 | 130130PST TANK 5 FLOW MEASURE AI | l/s | WASTE |  | WASTE:E53746
13013 | #N/A | #N/A | #N/A | E53748 | 130130PST TANK 6 FLOW MEASURE AI | l/s | WASTE |  | WASTE:E53748
13013 | #N/A | #N/A | #N/A | E53750 | 130130SAS BAL TANK FLOW MEASURE AI | l/s | WASTE |  | WASTE:E53750
13013 | #N/A | #N/A | #N/A | E53752 | 130130RETN LIQ MANHOLE 8 FLOW MEASURE AI | l/s | WASTE |  | WASTE:E53752
13013 | #N/A | #N/A | #N/A | E53754 | 130130RETN LIQ FOOD WST FLOW MEASURE AI | l/s | WASTE |  | WASTE:E53754
13013 | #N/A | #N/A | #N/A | E53770 | 130130FOUL WATER FLOW | l/s | WASTE |  | WASTE:E53770
13013 | #N/A | #N/A | #N/A | E53771 | 130130TANK DRAINAGE FLOW | l/s | WASTE |  | WASTE:E53771
13013 | #N/A | #N/A | #N/A | E55078 | 130131CABOTS PARK RISING MAIN FLOW ANLG | l/s | WASTE |  | WASTE:E55078
13013 | #N/A | #N/A | #N/A | E55185 | 130132INLET FLOW RX TEMPORARY OS | l/s | WASTE |  | WASTE:E55185
13013 | #N/A | #N/A | #N/A | E55720 | 130130MITSI MCERT FLOWMETER ANLG | l/s | WASTE |  | WASTE:E55720
13015 | #N/A | #N/A | #N/A | E14849 | 130151EA123FINAL EFFLUENT OUTLET FLOW | l/s | WASTE |  | WASTE:E14849
13015 | #N/A | #N/A | #N/A | E32126 | 13015AEA368MCERTS FPF INLET FLOW ANG | l/s | WASTE |  | WASTE:E32126
13016 | #N/A | #N/A | #N/A | E11132 | 130160RECIRC FLOW ANALOGUE | l/s | WASTE |  | WASTE:E11132
13016 | #N/A | #N/A | #N/A | E14563 | 130160INLET FLOW 1 | l/s | WASTE |  | WASTE:E14563
13016 | #N/A | #N/A | #N/A | E14564 | 130160INLET FLOW 2 | l/s | WASTE |  | WASTE:E14564
13016 | #N/A | #N/A | #N/A | E14565 | 130160INLET FLOW 3 | l/s | WASTE |  | WASTE:E14565
13016 | #N/A | #N/A | #N/A | E14576 | 130160INLET FLOW 4 | l/s | WASTE |  | WASTE:E14576
13016 | #N/A | #N/A | #N/A | E23429 | 130160TANK 1 OXYGEN SPARGE FLOW AN | l/s | WASTE |  | WASTE:E23429
13016 | #N/A | #N/A | #N/A | E23430 | 130160DESLUDGE RETURN FLOW AN | l/s | WASTE |  | WASTE:E23430
13016 | #N/A | #N/A | #N/A | E23436 | 130160TANK 2 OXYGEN SPARGE FLOW AN | l/s | WASTE |  | WASTE:E23436
13016 | #N/A | #N/A | #N/A | E23437 | 130160SLUDGE PUMP RETURN FLOW AN | l/s | WASTE |  | WASTE:E23437
13016 | #N/A | #N/A | #N/A | E23438 | 130160STORM PUMP RETURN FLOW AN | l/s | WASTE |  | WASTE:E23438
13016 | #N/A | #N/A | #N/A | E23440 | 130160FLOW TO TREATMENT AN | l/s | WASTE |  | WASTE:E23440
13016 | #N/A | #N/A | #N/A | E23449 | 130160EA086MCERT FLOW | l/s | WASTE |  | WASTE:E23449
13016 | #N/A | #N/A | #N/A | E31179 | 130160SECONDARY DOSING WEIR FLOW | l/s | WASTE |  | WASTE:E31179
13016 | #N/A | #N/A | #N/A | E31180 | 130160SECONDARY DOSNG BELLMOUTH FLOW | l/s | WASTE |  | WASTE:E31180
13016 | #N/A | #N/A | #N/A | E53040 | 130160HIGH RATE FILTER FLOW | l/s | WASTE |  | WASTE:E53040
13016 | #N/A | #N/A | #N/A | E39830 | 130160PASS FWD FLW RAW SALTFORD STW | l/s | WASTE |  | WASTE:E39830
13016 | #N/A | #N/A | #N/A | E6237 | 13016AFLOW TO TREATMENT FLOW RATE NIVUS | l/s | WASTE2 |  | WASTE2:E6237
13016 | #N/A | #N/A | #N/A | E6238 | 13016AFLOW TO TREATMENT FLOW RATE PANAMETRICS | l/s | WASTE2 |  | WASTE2:E6238
13016 | #N/A | #N/A | #N/A | E6273 | 13016ASTORM TANK TO SLUDGE REC TANK FLOW METER AI | l/s | WASTE2 |  | WASTE2:E6273
13016 | #N/A | #N/A | #N/A | E6277 | 13016ASLUDGE PUMP STORM RETURN FLOW AI | l/s | WASTE2 |  | WASTE2:E6277
13016 | #N/A | #N/A | #N/A | E6278 | 13016ASTORM RETURN PS RETURN FLOW | l/s | WASTE2 |  | WASTE2:E6278
13016 | #N/A | #N/A | #N/A | E6392 | 13016ASTORM RETURN PS 1 RECIRC FLOWMETER AI | l/s | WASTE2 |  | WASTE2:E6392
13016 | #N/A | #N/A | #N/A | E6393 | 13016ASTORM RETURN PS 2 RECIRC FLOWMETER AI | l/s | WASTE2 |  | WASTE2:E6393
13018 | #N/A | #N/A | #N/A | E10443 | 130180DF360BOREHOLE FLOW | l/s | WASTE |  | WASTE:E10443
13018 | #N/A | #N/A | #N/A | E33590 | 130180BREAK TANK FLOW METER | l/s | WASTE |  | WASTE:E33590
13018 | #N/A | #N/A | #N/A | E33591 | 130180MESS ROOM FLOW METER | l/s | WASTE |  | WASTE:E33591
13018 | #N/A | #N/A | #N/A | E36142 | 130180DIGESTER 4 SLUDGE FEED FLOW | l/s | WASTE |  | WASTE:E36142
13018 | #N/A | #N/A | #N/A | E36143 | 130180DIGESTER 3 SLUDGE FEED FLOW | l/s | WASTE |  | WASTE:E36143
13018 | #N/A | #N/A | #N/A | E36144 | 130180DIGESTER 2 SLUDGE FEED FLOW | l/s | WASTE |  | WASTE:E36144
13018 | #N/A | #N/A | #N/A | E36145 | 130180DIGESTER 1 SLUDGE FEED FLOW | l/s | WASTE |  | WASTE:E36145
13018 | #N/A | #N/A | #N/A | E51046 | 130180SLUDGE IMPORT FM HOLDENH FLOW | l/s | WASTE |  | WASTE:E51046
13018 | #N/A | #N/A | #N/A | E51049 | 130180SLTH02 FEED FLOW ANG | l/s | WASTE |  | WASTE:E51049
13018 | #N/A | #N/A | #N/A | E51801 | 130180PRIMARY SLUDGE FLOW FEED STRAINPRESS | l/s | WASTE |  | WASTE:E51801
13018 | #N/A | #N/A | #N/A | E52089 | 130180LIQUORS RETN TO HOLDENH FLOW | l/s | WASTE |  | WASTE:E52089
13018 | #N/A | #N/A | #N/A | E33563 | 130180SLUDGE FEED FLW | l/s | WASTE |  | WASTE:E33563
13018 | #N/A | #N/A | #N/A | E33564 | 130180THICKENED SLUDGE FLW | l/s | WASTE |  | WASTE:E33564
13018 | #N/A | #N/A | #N/A | E51050 | 130180SAS2 THICKENED SLDGE FLW ANG | l/s | WASTE |  | WASTE:E51050
13021 | #N/A | #N/A | #N/A | E2360 | 130210EA004FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E2360
13021 | #N/A | #N/A | #N/A | E2362 | 130210MAX FINAL FLOW | l/s | WASTE |  | WASTE:E2362
13021 | #N/A | #N/A | #N/A | E2363 | 130210MIN FINAL FLOW | l/s | WASTE |  | WASTE:E2363
13022 | #N/A | #N/A | #N/A | E4413 | 130221EA125OUTFLOW | l/s | WASTE |  | WASTE:E4413
13022 | #N/A | #N/A | #N/A | E4414 | 130221EA126GRAVITY OUTFLOW | l/s | WASTE |  | WASTE:E4414
13022 | #N/A | #N/A | #N/A | E4558 | 13022EA3471INLET MCERT FLOW ANG | l/s | WASTE |  | WASTE:E4558
13022 | #N/A | #N/A | #N/A | E33292 | 130221HUMUS FEED PS FLOW ANG | l/s | WASTE |  | WASTE:E33292
13022 | #N/A | #N/A | #N/A | E33294 | 130221STONE MEDIA FILTER RECIRCULATION FLOW ANG | l/s | WASTE |  | WASTE:E33294
13022 | #N/A | #N/A | #N/A | E33295 | 130221PLASTIC MEDIA FILTER RECIRCULATION FLOW ANG | l/s | WASTE |  | WASTE:E33295
13024 | #N/A | #N/A | #N/A | E14968 | 130241BULBURY LANE FLOW | l/s | WASTE |  | WASTE:E14968
13024 | #N/A | #N/A | #N/A | E14969 | 130241EA217FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E14969
13024 | #N/A | #N/A | #N/A | E14971 | 130241FOX POUND FLOW ANG | l/s | WASTE |  | WASTE:E14971
13025 | #N/A | #N/A | #N/A | E2656 | 130250INLET FLOW | l/s | WASTE |  | WASTE:E2656
13025 | #N/A | #N/A | #N/A | E2658 | 130250INLET FLOW 2 | l/s | WASTE |  | WASTE:E2658
13025 | #N/A | #N/A | #N/A | E2660 | 130250MAX FLOW | l/s | WASTE |  | WASTE:E2660
13025 | #N/A | #N/A | #N/A | E2661 | 130250MIN FLOW | l/s | WASTE |  | WASTE:E2661
13025 | #N/A | #N/A | #N/A | E2663 | 130250EA005MCERT FLOWMETER ANG | l/s | WASTE |  | WASTE:E2663
13027 | #N/A | #N/A | #N/A | E24072 | 13027AEA127MCERT FLOW | l/s | WASTE |  | WASTE:E24072
13027 | #N/A | #N/A | #N/A | E55190 | 13027XINLET FLUME FLOW | l/s | WASTE |  | WASTE:E55190
13027 | #N/A | #N/A | #N/A | E55443 | 13027APUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E55443
13027 | #N/A | #N/A | #N/A | E55461 | 13027AINLET FLOW AI | l/s | WASTE |  | WASTE:E55461
13027 | #N/A | #N/A | #N/A | E55465 | 13027AMCERT FLOWMETER AI | l/s | WASTE |  | WASTE:E55465
13027 | #N/A | #N/A | #N/A | E55475 | 13027APUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E55475
13028 | #N/A | #N/A | #N/A | E1225 | 130280INLET FLOW | l/s | WASTE |  | WASTE:E1225
13028 | #N/A | #N/A | #N/A | E1226 | 130280RISING MAIN FLOW ANG | l/s | WASTE |  | WASTE:E1226
13028 | #N/A | #N/A | #N/A | E1229 | 130280INLET FLOW AVE | l/s | WASTE |  | WASTE:E1229
13028 | #N/A | #N/A | #N/A | E25136 | 130280EA128PST DIST CHAMBER FLOW | l/s | WASTE |  | WASTE:E25136
13028 | #N/A | #N/A | #N/A | E25156 | 130280RAS FLOW | l/s | WASTE |  | WASTE:E25156
13028 | #N/A | #N/A | #N/A | E50501 | 130280RAS FLOW 43-FIT-9006 AI | l/s | WASTE |  | WASTE:E50501
13028 | #N/A | #N/A | #N/A | E50503 | 130280BIOMAG FEED FLOW AI | l/s | WASTE |  | WASTE:E50503
13028 | #N/A | #N/A | #N/A | E50505 | 130280ASP LANE 34 FLOW AI | l/s | WASTE |  | WASTE:E50505
13028 | #N/A | #N/A | #N/A | E50506 | 130280POLY DOSING FLOW AI | l/s | WASTE |  | WASTE:E50506
13029 | #N/A | #N/A | #N/A | E8881 | 130290INLET FLOW 1 | l/s | WASTE |  | WASTE:E8881
13029 | #N/A | #N/A | #N/A | E8882 | 130290EA006INLET FLOW | l/s | WASTE |  | WASTE:E8882
13031 | #N/A | #N/A | #N/A | E3866 | 130310EA007OUTLET FLOW | l/s | WASTE |  | WASTE:E3866
13031 | #N/A | #N/A | #N/A | E14194 | 130310FLOW 1 | l/s | WASTE |  | WASTE:E14194
13031 | #N/A | #N/A | #N/A | E14195 | 130310FLOW 2 | l/s | WASTE |  | WASTE:E14195
13031 | #N/A | #N/A | #N/A | E36115 | 130310PUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E36115
13031 | #N/A | #N/A | #N/A | E36434 | 130310PUMP SET 2 SEWAGE FLOW | l/s | WASTE |  | WASTE:E36434
13031 | #N/A | #N/A | #N/A | E36442 | 130310PROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E36442
13032 | #N/A | #N/A | #N/A | E4431 | 130320INLET FLOW | l/s | WASTE |  | WASTE:E4431
13032 | #N/A | #N/A | #N/A | E4432 | 130320EA129OUTFLOW | l/s | WASTE |  | WASTE:E4432
13032 | #N/A | #N/A | #N/A | E4435 | 130320HILLFARRANCE RISING MAIN FLOW | l/s | WASTE |  | WASTE:E4435
13034 | #N/A | #N/A | #N/A | E5031 | 130340SQUARES ROAD FLOW | l/s | WASTE |  | WASTE:E5031
13034 | #N/A | #N/A | #N/A | E5033 | 130340BRADNEY BRIDGE FLOW | l/s | WASTE |  | WASTE:E5033
13034 | #N/A | #N/A | #N/A | E5034 | 130340BRISTOL ROAD FLOW | l/s | WASTE |  | WASTE:E5034
13034 | #N/A | #N/A | #N/A | E5035 | 130340UNOX INLET EFFLUENT FLOW | l/s | WASTE |  | WASTE:E5035
13034 | #N/A | #N/A | #N/A | E5036 | 130340OLD WORKS FLOW | l/s | WASTE |  | WASTE:E5036
13034 | #N/A | #N/A | #N/A | E5038 | 130340EAST QUAY FLOW | l/s | WASTE |  | WASTE:E5038
13034 | #N/A | #N/A | #N/A | E5048 | 130340EA138UV NEW MCERT FLOWMETER | l/s | WASTE |  | WASTE:E5048
13034 | #N/A | #N/A | #N/A | E5049 | 130340GERBER FLOW | l/s | WASTE |  | WASTE:E5049
13034 | #N/A | #N/A | #N/A | E5055 | 130340PUMP1 RETURN FLOW | l/s | WASTE |  | WASTE:E5055
13034 | #N/A | #N/A | #N/A | E5056 | 130340PUMP 2 RETURN FLOW | l/s | WASTE |  | WASTE:E5056
13034 | #N/A | #N/A | #N/A | E5060 | 130340RECIRCULATION FLOW | l/s | WASTE |  | WASTE:E5060
13034 | #N/A | #N/A | #N/A | E5077 | 130340FLOWMETER 2 FLOW | l/s | WASTE |  | WASTE:E5077
13034 | #N/A | #N/A | #N/A | E5089 | 130340SYSTEM FLOW | l/s | WASTE |  | WASTE:E5089
13034 | #N/A | #N/A | #N/A | E5090 | 130340FLOWMETER 1 FLOW | l/s | WASTE |  | WASTE:E5090
13034 | #N/A | #N/A | #N/A | E6821 | 130340EXPRESS PARKWAY ASP FLOW | l/s | WASTE |  | WASTE:E6821
13034 | #N/A | #N/A | #N/A | E9639 | 130340SALTLANDS OLD FLOWMETER | l/s | WASTE |  | WASTE:E9639
13034 | #N/A | #N/A | #N/A | E9640 | 130340BRISTOL ROAD FLOWMETER | l/s | WASTE |  | WASTE:E9640
13034 | #N/A | #N/A | #N/A | E9642 | 130340BRADNEY BRIDGE FLOWMETER | l/s | WASTE |  | WASTE:E9642
13034 | #N/A | #N/A | #N/A | E9644 | 130340EAST QUAY FLOWMETER | l/s | WASTE |  | WASTE:E9644
13034 | #N/A | #N/A | #N/A | E24940 | 130340REACTOR 1 INLET FLOW | l/s | WASTE |  | WASTE:E24940
13034 | #N/A | #N/A | #N/A | E24941 | 130340REACTOR 2 INLET FLOW | l/s | WASTE |  | WASTE:E24941
13034 | #N/A | #N/A | #N/A | E24942 | 130340REACTOR 3 INLET FLOW | l/s | WASTE |  | WASTE:E24942
13034 | #N/A | #N/A | #N/A | E24943 | 130340REACTOR 4 INLET FLOW | l/s | WASTE |  | WASTE:E24943
13034 | #N/A | #N/A | #N/A | E24944 | 130340REACTOR 5 INLET FLOW | l/s | WASTE |  | WASTE:E24944
13034 | #N/A | #N/A | #N/A | E24955 | 130340GBT SLUDGE TRANSFER FLOW | l/s | WASTE |  | WASTE:E24955
13034 | #N/A | #N/A | #N/A | E31296 | 13034AASP PST 3 FLOW | l/s | WASTE |  | WASTE:E31296
13034 | #N/A | #N/A | #N/A | E31308 | 13034AASP SAS FLOW | l/s | WASTE |  | WASTE:E31308
13034 | #N/A | #N/A | #N/A | E31311 | 13034AASP LANE 3 ZONE 3 AIR FLOW | l/s | WASTE |  | WASTE:E31311
13034 | #N/A | #N/A | #N/A | E31315 | 13034AASP PST 1 AND 2 FLOW | l/s | WASTE |  | WASTE:E31315
13034 | #N/A | #N/A | #N/A | E31316 | 13034AASP INLET FLOW | l/s | WASTE |  | WASTE:E31316
13034 | #N/A | #N/A | #N/A | E31324 | 13034AASP BLOWER AIR OUTFLOW | l/s | WASTE |  | WASTE:E31324
13034 | #N/A | #N/A | #N/A | E31327 | 13034AASP WORKS RETURN TO INLET FLOW | l/s | WASTE |  | WASTE:E31327
13034 | #N/A | #N/A | #N/A | E31329 | 13034AASP RAS FLOW | l/s | WASTE |  | WASTE:E31329
13034 | #N/A | #N/A | #N/A | E31336 | 13034AASP LANE 1 ZONE 1 AIR FLOW | l/s | WASTE |  | WASTE:E31336
13034 | #N/A | #N/A | #N/A | E31337 | 13034AASP LANE 2 ZONE 1 AIR FLOW | l/s | WASTE |  | WASTE:E31337
13034 | #N/A | #N/A | #N/A | E31338 | 13034AASP LANE 3 ZONE 1 AIR FLOW | l/s | WASTE |  | WASTE:E31338
13034 | #N/A | #N/A | #N/A | E31339 | 13034AASP LANE 1 ZONE 2 AIR FLOW | l/s | WASTE |  | WASTE:E31339
13034 | #N/A | #N/A | #N/A | E31340 | 13034AASP LANE 2 ZONE 2 AIR FLOW | l/s | WASTE |  | WASTE:E31340
13034 | #N/A | #N/A | #N/A | E31341 | 13034AASP LANE 3 ZONE 2 AIR FLOW | l/s | WASTE |  | WASTE:E31341
13034 | #N/A | #N/A | #N/A | E31342 | 13034AASP LANE 1 ZONE 3 AIR FLOW | l/s | WASTE |  | WASTE:E31342
13034 | #N/A | #N/A | #N/A | E31343 | 13034AASP LANE 2 ZONE 3 AIR FLOW | l/s | WASTE |  | WASTE:E31343
13034 | #N/A | #N/A | #N/A | E52971 | 130340GBT 2 SLUDGE FD FLOW AI | l/s | WASTE |  | WASTE:E52971
13034 | #N/A | #N/A | #N/A | E52973 | 130340GBT2 THICKENED SLUDGE FLOW AI | l/s | WASTE |  | WASTE:E52973
13035 | #N/A | #N/A | #N/A | E2841 | 130350RAS FLOW | l/s | WASTE |  | WASTE:E2841
13035 | #N/A | #N/A | #N/A | E2842 | 130350EA131MCERT FFT FLOW | l/s | WASTE |  | WASTE:E2842
13036 | #N/A | #N/A | #N/A | E15383 | 130361EA132FINAL EFF FLOW | l/s | WASTE |  | WASTE:E15383
13036 | #N/A | #N/A | #N/A | E15389 | 130361TEMP DUTCH WHEEL FLOWMETER AI | l/s | WASTE |  | WASTE:E15389
13037 | #N/A | #N/A | #N/A | E1865 | 130370EA008MCERT OUTLET FLOW | l/s | WASTE |  | WASTE:E1865
13037 | #N/A | #N/A | #N/A | E1867 | 130370MAX FLOW | l/s | WASTE |  | WASTE:E1867
13037 | #N/A | #N/A | #N/A | E1868 | 130370MIN FLOW | l/s | WASTE |  | WASTE:E1868
13037 | #N/A | #N/A | #N/A | E97979 | 13037APROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E97979
13037 | #N/A | #N/A | #N/A | E97984 | 13037APUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E97984
13037 | #N/A | #N/A | #N/A | E97989 | 13037APUMP SET 2 SEWAGE FLOW | l/s | WASTE |  | WASTE:E97989
13039 | #N/A | #N/A | #N/A | E3490 | 130391EA009MCERT INLET FLOW | l/s | WASTE |  | WASTE:E3490
13039 | #N/A | #N/A | #N/A | E23654 | 130391PUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E23654
13039 | #N/A | #N/A | #N/A | E54816 | 130391PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E54816
13039 | #N/A | #N/A | #N/A | E55039 | 130391PUMP SET 2 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E55039
13041 | #N/A | #N/A | #N/A | E5226 | 130410EA011FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E5226
13041 | #N/A | #N/A | #N/A | E5234 | 130410FINAL EFF FLOW AVE | l/s | WASTE |  | WASTE:E5234
13042 | #N/A | #N/A | #N/A | E2672 | 130420FLOWMETER | l/s | WASTE |  | WASTE:E2672
13043 | #N/A | #N/A | #N/A | E5316 | 130430COMBINED FLOW TO INLET | l/s | WASTE |  | WASTE:E5316
13043 | #N/A | #N/A | #N/A | E5317 | 130430FLOW TO FILTER BEDS | l/s | WASTE |  | WASTE:E5317
13043 | #N/A | #N/A | #N/A | E5321 | 130430EA133FINAL EFF FLOW | l/s | WASTE |  | WASTE:E5321
13043 | #N/A | #N/A | #N/A | E5323 | 130430SEWAGE TRANSFER FLOW TO INLET | l/s | WASTE |  | WASTE:E5323
13044 | #N/A | #N/A | #N/A | E13209 | 130440FLOW TO WORKS | l/s | WASTE |  | WASTE:E13209
13044 | #N/A | #N/A | #N/A | E13210 | 130440EA012FLOW TO WORKS | l/s | WASTE |  | WASTE:E13210
13044 | #N/A | #N/A | #N/A | E30682 | 13044BFLOW TO TREATMENT | l/s | WASTE |  | WASTE:E30682
13044 | #N/A | #N/A | #N/A | E30740 | 13044CDELIVERY FLOW | l/s | WASTE |  | WASTE:E30740
13044 | #N/A | #N/A | #N/A | E52956 | 130440FLOCCULATOR TANK INLET FLOW ANG | l/s | WASTE |  | WASTE:E52956
13044 | #N/A | #N/A | #N/A | E52962 | 130440PUMP SET 2 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E52962
13044 | #N/A | #N/A | #N/A | E30512 | 13044ATASF INLET FLW | l/s | WASTE |  | WASTE:E30512
13044 | #N/A | #N/A | #N/A | E30513 | 13044ATASF 1 FLW | l/s | WASTE |  | WASTE:E30513
13044 | #N/A | #N/A | #N/A | E30514 | 13044ATASF 2 FLW | l/s | WASTE |  | WASTE:E30514
13044 | #N/A | #N/A | #N/A | E30518 | 13044ATASF 3 FLW | l/s | WASTE |  | WASTE:E30518
13044 | #N/A | #N/A | #N/A | E30519 | 13044ATASF 4 FLW | l/s | WASTE |  | WASTE:E30519
13044 | #N/A | #N/A | #N/A | E30520 | 13044ATASF 5 FLW | l/s | WASTE |  | WASTE:E30520
13045 | #N/A | #N/A | #N/A | E1635 | 130450EA013INLET FLOW | l/s | WASTE |  | WASTE:E1635
13045 | #N/A | #N/A | #N/A | E31430 | 130451INCOMING FLOW ANLG | l/s | WASTE |  | WASTE:E31430
13045 | #N/A | #N/A | #N/A | E31431 | 130451RAS FLOWMETER 2 ANLG | l/s | WASTE |  | WASTE:E31431
13045 | #N/A | #N/A | #N/A | E31432 | 130451RAS FLOWMETER 1 ANLG | l/s | WASTE |  | WASTE:E31432
13045 | #N/A | #N/A | #N/A | E31433 | 130451RAS FLOWMETER 3 ANLG | l/s | WASTE |  | WASTE:E31433
13047 | #N/A | #N/A | #N/A | E4486 | 130470FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E4486
13047 | #N/A | #N/A | #N/A | E4487 | 130470EDM SPILL FLOW | l/s | WASTE |  | WASTE:E4487
13047 | #N/A | #N/A | #N/A | E27531 | 130470INLET WORKS FLOW 1 AN | l/s | WASTE |  | WASTE:E27531
13047 | #N/A | #N/A | #N/A | E27532 | 130470INLET WORKS FLOW 2 AN | l/s | WASTE |  | WASTE:E27532
13047 | #N/A | #N/A | #N/A | E27537 | 130470FLOW TO TREATMENT AN | l/s | WASTE |  | WASTE:E27537
13047 | #N/A | #N/A | #N/A | E32173 | 130470FILTER BED NO 2 FEED FLOW ANG | l/s | WASTE |  | WASTE:E32173
13047 | #N/A | #N/A | #N/A | E52667 | 130470EA219UV FEED FLOW ANG | l/s | WASTE |  | WASTE:E52667
13047 | #N/A | #N/A | #N/A | E56310 | 130470BACKWASH RETURN PUMPS FLOW ANG | l/s | WASTE |  | WASTE:E56310
13047 | #N/A | #N/A | #N/A | E56311 | 130470DISC FILTER PUMP FLOW ANG | l/s | WASTE |  | WASTE:E56311
13048 | #N/A | #N/A | #N/A | E1760 | 130481INLET FLOW | l/s | WASTE |  | WASTE:E1760
13048 | #N/A | #N/A | #N/A | E1761 | 130481EA134OUTLET FLOW | l/s | WASTE |  | WASTE:E1761
13048 | #N/A | #N/A | #N/A | E33099 | 130481EA OUTLET FLOW | l/s | WASTE |  | WASTE:E33099
13048 | #N/A | #N/A | #N/A | E33100 | 130481EA INLET FLOW | l/s | WASTE |  | WASTE:E33100
13050 | #N/A | #N/A | #N/A | E15487 | 130500INLET WORKS FLOW | l/s | WASTE |  | WASTE:E15487
13050 | #N/A | #N/A | #N/A | E15489 | 130500EA135CERNE ABBAS STW OUTFLOW | l/s | WASTE |  | WASTE:E15489
13050 | #N/A | #N/A | #N/A | E51081 | 130500SLUDGE TRANSFER FLOW ANG | l/s | WASTE |  | WASTE:E51081
13050 | #N/A | #N/A | #N/A | E6769 | 13050APROFILE STORM DOSING START FLOW | l/s | WASTE2 |  | WASTE2:E6769
13050 | #N/A | #N/A | #N/A | E6774 | 13050APUMP SET 1 SEWAGE FLOW AI | l/s | WASTE2 |  | WASTE2:E6774
13050 | #N/A | #N/A | #N/A | E7120 | 13050BEA345FFT FLOW MCERTS | l/s | WASTE2 |  | WASTE2:E7120
13050 | #N/A | #N/A | #N/A | E7125 | 13050BEA346BALANCE TANK OVERFLOW MCERTS FLOW | l/s | WASTE2 |  | WASTE2:E7125
13054 | #N/A | #N/A | #N/A | E1050 | 130540EA015INLET FLOW | l/s | WASTE |  | WASTE:E1050
13055 | #N/A | #N/A | #N/A | E2380 | 130550FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E2380
13055 | #N/A | #N/A | #N/A | E2381 | 130550INLET FLOW | l/s | WASTE |  | WASTE:E2381
13055 | #N/A | #N/A | #N/A | E2386 | 130550EA136MCERT OUTLET FLOW METER | l/s | WASTE |  | WASTE:E2386
13056 | #N/A | #N/A | #N/A | E24394 | 130561INLET FLOW | l/s | WASTE |  | WASTE:E24394
13056 | #N/A | #N/A | #N/A | E24395 | 130561EA262FFT FLOW AN | l/s | WASTE |  | WASTE:E24395
13056 | #N/A | #N/A | #N/A | E24430 | 130561SAS FLOW AN | l/s | WASTE |  | WASTE:E24430
13057 | #N/A | #N/A | #N/A | E3660 | 130570FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E3660
13057 | #N/A | #N/A | #N/A | E3665 | 130570EA016MCERT FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E3665
13057 | #N/A | #N/A | #N/A | E3666 | 130570TANK 1 SLUDGE DRAWOFF FLOW | l/s | WASTE |  | WASTE:E3666
13057 | #N/A | #N/A | #N/A | E3667 | 130570TANK 2 SLUDGE DRAWOFF FLOW | l/s | WASTE |  | WASTE:E3667
13057 | #N/A | #N/A | #N/A | E50213 | 130570RISING MAIN FLOW 1 | l/s | WASTE |  | WASTE:E50213
13057 | #N/A | #N/A | #N/A | E50214 | 130570RISING MAIN FLOW 2 | l/s | WASTE |  | WASTE:E50214
13057 | #N/A | #N/A | #N/A | E50250 | 130570PUMP SET 2 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E50250
13057 | #N/A | #N/A | #N/A | E50255 | 130570PUMP SET 2 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E50255
13057 | #N/A | #N/A | #N/A | E53501 | 130570PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E53501
13057 | #N/A | #N/A | #N/A | E53509 | 130570PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E53509
13057 | #N/A | #N/A | #N/A | E56870 | 13057APOLYMER DOSING PUMP 1 FLOW AI | l/s | WASTE |  | WASTE:E56870
13057 | #N/A | #N/A | #N/A | E56871 | 13057APOLYMER DOSING PUMP 2 FLOW AI | l/s | WASTE |  | WASTE:E56871
13057 | #N/A | #N/A | #N/A | E56875 | 13057ATHICKENED SLUDGE FLOW AI | l/s | WASTE |  | WASTE:E56875
13057 | #N/A | #N/A | #N/A | E56877 | 13057AGBT SLUDGE FLOW IN AI | l/s | WASTE |  | WASTE:E56877
13057 | #N/A | #N/A | #N/A | E56924 | 13057BMMF FILTER FEED PUMPING STATION FLOW RATE AI | l/s | WASTE |  | WASTE:E56924
13057 | #N/A | #N/A | #N/A | E56931 | 13057BDIRTY BACKWASH TANK DISCHARGE FLOW AI | l/s | WASTE |  | WASTE:E56931
13057 | #N/A | #N/A | #N/A | E96559 | 13057CAIR SCOUR FLOW | l/s | WASTE |  | WASTE:E96559
13057 | #N/A | #N/A | #N/A | E96562 | 13057CFILTER 1 OUTLET FLOW | l/s | WASTE |  | WASTE:E96562
13057 | #N/A | #N/A | #N/A | E97866 | 13057CFILTER 1 BACKWASH FLOW | l/s | WASTE |  | WASTE:E97866
13057 | #N/A | #N/A | #N/A | E97867 | 13057CFILTER 2 OUTLET FLOW | l/s | WASTE |  | WASTE:E97867
13057 | #N/A | #N/A | #N/A | E97868 | 13057CFILTER 2 BACKWASH FLOW | l/s | WASTE |  | WASTE:E97868
13057 | #N/A | #N/A | #N/A | E97869 | 13057CFILTER 3 OUTLET FLOW | l/s | WASTE |  | WASTE:E97869
13057 | #N/A | #N/A | #N/A | E97870 | 13057CFILTER 3 BACKWASH FLOW | l/s | WASTE |  | WASTE:E97870
13058 | #N/A | #N/A | #N/A | E1350 | 130580EA221INLET FLOW | l/s | WASTE |  | WASTE:E1350
13058 | #N/A | #N/A | #N/A | E1353 | 130580RISING MAIN FLOW | l/s | WASTE |  | WASTE:E1353
13058 | #N/A | #N/A | #N/A | E25962 | 130580NEW WORKS DRAIN FLOW AN | l/s | WASTE |  | WASTE:E25962
13058 | #N/A | #N/A | #N/A | E25966 | 130580SAND FILTER FEED FLOW AN | l/s | WASTE |  | WASTE:E25966
13058 | #N/A | #N/A | #N/A | E25972 | 130580SAND FILTER BWASH FLOW AN | l/s | WASTE |  | WASTE:E25972
13060 | #N/A | #N/A | #N/A | E9603 | 130601CHIDEOCK PASS FWD FLOW FROM SEATOWN | l/s | WASTE |  | WASTE:E9603
13060 | #N/A | #N/A | #N/A | E14047 | 130601EA358 FPF MCERTS FLOW METER ANALOGUE INPUT | l/s | WASTE |  | WASTE:E14047
13060 | #N/A | #N/A | #N/A | E14048 | 130601UV FLOW | l/s | WASTE |  | WASTE:E14048
13060 | #N/A | #N/A | #N/A | E14054 | 130601DERIVED FLOW TO BIOFILTERS | l/s | WASTE |  | WASTE:E14054
13060 | #N/A | #N/A | #N/A | E14056 | 130601EA137UV WATER FLOW RATE | l/s | WASTE |  | WASTE:E14056
13061 | #N/A | #N/A | #N/A | E4066 | 130610INLET FLOW | l/s | WASTE |  | WASTE:E4066
13061 | #N/A | #N/A | #N/A | E4067 | 130610EA017INLET FLOW | l/s | WASTE |  | WASTE:E4067
13061 | #N/A | #N/A | #N/A | E54029 | 130610PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E54029
13061 | #N/A | #N/A | #N/A | E54034 | 130610PUMP SET 2 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E54034
13061 | #N/A | #N/A | #N/A | E54042 | 130610PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E54042
13062 | #N/A | #N/A | #N/A | E3460 | 130621EA222EFFLUENT FLOW | l/s | WASTE |  | WASTE:E3460
13064 | #N/A | #N/A | #N/A | E4384 | 130640EA019OUTLET FLOW | l/s | WASTE |  | WASTE:E4384
13064 | #N/A | #N/A | #N/A | E4393 | 130640DEWATERER FEED FLOW | l/s | WASTE |  | WASTE:E4393
13064 | #N/A | #N/A | #N/A | E56631 | 13064BWASH WATER BOOSTER FLOW AI | l/s | WASTE |  | WASTE:E56631
13064 | #N/A | #N/A | #N/A | E76038 | 13064AMCERTS FLOW AI | l/s | WASTE |  | WASTE:E76038
13066 | #N/A | #N/A | #N/A | E8297 | 130660COMBINED FLOW TO THICKENED TANK | l/s | WASTE |  | WASTE:E8297
13066 | #N/A | #N/A | #N/A | E8298 | 130660DRUM 1 FEED FLOW | l/s | WASTE |  | WASTE:E8298
13066 | #N/A | #N/A | #N/A | E8299 | 130660DRUM 1 POLY FLOW | l/s | WASTE |  | WASTE:E8299
13066 | #N/A | #N/A | #N/A | E8300 | 130660DRUM 2 FEED FLOW | l/s | WASTE |  | WASTE:E8300
13066 | #N/A | #N/A | #N/A | E8301 | 130660DRUM 2 POLY FLOW | l/s | WASTE |  | WASTE:E8301
13066 | #N/A | #N/A | #N/A | E9896 | 130660INWRKS TREATMENT FLOW A | l/s | WASTE |  | WASTE:E9896
13066 | #N/A | #N/A | #N/A | E9897 | 130660INWRKS TREATMENT FLOW B | l/s | WASTE |  | WASTE:E9897
13066 | #N/A | #N/A | #N/A | E9902 | 130660FLOW FROM STORM 1 | l/s | WASTE |  | WASTE:E9902
13066 | #N/A | #N/A | #N/A | E9903 | 130660FLOW FROM STORM 2 | l/s | WASTE |  | WASTE:E9903
13066 | #N/A | #N/A | #N/A | E9917 | 130660SCOTTS HILL LANE SPS FLOW | l/s | WASTE |  | WASTE:E9917
13066 | #N/A | #N/A | #N/A | E9920 | 130660ASP 1 AND 2 RAS FLOW | l/s | WASTE |  | WASTE:E9920
13066 | #N/A | #N/A | #N/A | E9921 | 130660ASP 1 AND 2 SAS FLOW | l/s | WASTE |  | WASTE:E9921
13066 | #N/A | #N/A | #N/A | E11190 | 130660STORM FLOW | l/s | WASTE |  | WASTE:E11190
13066 | #N/A | #N/A | #N/A | E11193 | 130660EA021MINOR FLOW | l/s | WASTE |  | WASTE:E11193
13066 | #N/A | #N/A | #N/A | E11194 | 130660EA020MAJOR FLOW | l/s | WASTE |  | WASTE:E11194
13066 | #N/A | #N/A | #N/A | E11197 | 130660SOMERFORD BRIDGE FLOW | l/s | WASTE |  | WASTE:E11197
13066 | #N/A | #N/A | #N/A | E26779 | 130660PUREWELL SPS RISING MAIN FLOW | l/s | WASTE |  | WASTE:E26779
13066 | #N/A | #N/A | #N/A | E36357 | 130660BURTON PS FLOW ANG | l/s | WASTE |  | WASTE:E36357
13066 | #N/A | #N/A | #N/A | E36360 | 130660QUOMPS 2 SPS RISING MAIN FLOW | l/s | WASTE |  | WASTE:E36360
13066 | #N/A | #N/A | #N/A | E36362 | 130660AVON MILL LANE SPS RISING MAIN FLOW | l/s | WASTE |  | WASTE:E36362
13066 | #N/A | #N/A | #N/A | E38876 | 130660PUMP 1 FLOW | l/s | WASTE |  | WASTE:E38876
13066 | #N/A | #N/A | #N/A | E39193 | 130660PUMP 2 FLOW | l/s | WASTE |  | WASTE:E39193
13069 | #N/A | #N/A | #N/A | E3341 | 130690EA022INLET FLOW | l/s | WASTE |  | WASTE:E3341
13069 | #N/A | #N/A | #N/A | E3343 | 130690INLET FLOW | l/s | WASTE |  | WASTE:E3343
13070 | #N/A | #N/A | #N/A | E2870 | 130700EA023INLET FLOW | l/s | WASTE |  | WASTE:E2870
13071 | #N/A | #N/A | #N/A | E9604 | 130710INLET FLOW AVE | l/s | WASTE |  | WASTE:E9604
13071 | #N/A | #N/A | #N/A | E11051 | 130710EA024INLET FLOW | l/s | WASTE |  | WASTE:E11051
13072 | #N/A | #N/A | #N/A | E26065 | 130721OUTLET FLOW METER | l/s | WASTE |  | WASTE:E26065
13073 | #N/A | #N/A | #N/A | E1890 | 130730EA025INLET FLOW | l/s | WASTE |  | WASTE:E1890
13073 | #N/A | #N/A | #N/A | E1898 | 130730INLET FLOW AVE | l/s | WASTE |  | WASTE:E1898
13073 | #N/A | #N/A | #N/A | E30327 | 13073AFFT FLOW TO PRIM SED TANK | l/s | WASTE |  | WASTE:E30327
13075 | #N/A | #N/A | #N/A | E2890 | 130750EA275 FLOW FINAL EFFLUENT | l/s | WASTE |  | WASTE:E2890
13075 | #N/A | #N/A | #N/A | E2894 | 130750PUMPED FLOW TO SCREEN | l/s | WASTE |  | WASTE:E2894
13075 | #N/A | #N/A | #N/A | E2897 | 130750FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E2897
13075 | #N/A | #N/A | #N/A | E2901 | 130750ASSISTED STORM FLOW A | l/s | WASTE |  | WASTE:E2901
13075 | #N/A | #N/A | #N/A | E2902 | 130750ASSISTED STORM FLOW B | l/s | WASTE |  | WASTE:E2902
13075 | #N/A | #N/A | #N/A | E97817 | 13075AINLET PS OUTLET MCERT FLOWMETER AI | l/s | WASTE |  | WASTE:E97817
13075 | #N/A | #N/A | #N/A | E97820 | 13075ASTORM TRANSFER PS OUTLET FLOWMETER AI | l/s | WASTE |  | WASTE:E97820
13075 | #N/A | #N/A | #N/A | E97827 | 13075ATSR FEED PS OUTLET FLOWMETER TRANSMITTER AI | l/s | WASTE |  | WASTE:E97827
13075 | #N/A | #N/A | #N/A | E97830 | 13075ATSR BACKWASH BALANCE TANK OUTLET FLOWMETER AI | l/s | WASTE |  | WASTE:E97830
13075 | #N/A | #N/A | #N/A | E97842 | 13075AWORKS RETURN PS OUTLET FLOWMETER AI | l/s | WASTE |  | WASTE:E97842
13076 | #N/A | #N/A | #N/A | E1381 | 130760SCREEN WASHWATER FLOW | l/s | WASTE |  | WASTE:E1381
13077 | #N/A | #N/A | #N/A | E15968 | 130771FLOW FROM LAGOONS | l/s | WASTE |  | WASTE:E15968
13077 | #N/A | #N/A | #N/A | E15969 | 130771STORM TANK OVERFLOW | l/s | WASTE |  | WASTE:E15969
13077 | #N/A | #N/A | #N/A | E15972 | 130771INLET FLOW LEFT CHANNEL | l/s | WASTE |  | WASTE:E15972
13077 | #N/A | #N/A | #N/A | E6542 | 13077BUV INLET FLW ANG | l/s | WASTE2 |  | WASTE2:E6542
13077 | #N/A | #N/A | #N/A | E6353 | 13077APROFILE STORM DOSING START FLOW | l/s | WASTE2 |  | WASTE2:E6353
13077 | #N/A | #N/A | #N/A | E6358 | 13077APUMP SET 1 SEWAGE FLOW AI | l/s | WASTE2 |  | WASTE2:E6358
13077 | #N/A | #N/A | #N/A | E6518 | 13077BINLET FLOW ANG | l/s | WASTE2 |  | WASTE2:E6518
13077 | #N/A | #N/A | #N/A | E6519 | 13077BEA027MCERTS FLOW ANG | l/s | WASTE2 |  | WASTE2:E6519
13077 | #N/A | #N/A | #N/A | E6523 | 13077BCLOTH FILTER FEED FLOW ANG | l/s | WASTE2 |  | WASTE2:E6523
13077 | #N/A | #N/A | #N/A | E6531 | 13077BRECIRC FLOW ANG | l/s | WASTE2 |  | WASTE2:E6531
13077 | #N/A | #N/A | #N/A | E6536 | 13077BWORKS RETURN PS FLOW ANG | l/s | WASTE2 |  | WASTE2:E6536
13078 | #N/A | #N/A | #N/A | E9383 | 130780EA028INLET FLOW | l/s | WASTE |  | WASTE:E9383
13079 | #N/A | #N/A | #N/A | E2400 | 130790EA224MCERTS INLET FLOW | l/s | WASTE |  | WASTE:E2400
13083 | #N/A | #N/A | #N/A | E4086 | 130831EA030OUTLET FLOW | l/s | WASTE |  | WASTE:E4086
13084 | #N/A | #N/A | #N/A | E1900 | 130840FORMULA A FLOW | l/s | WASTE |  | WASTE:E1900
13084 | #N/A | #N/A | #N/A | E1902 | 130840EA031FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E1902
13084 | #N/A | #N/A | #N/A | E1903 | 130840FLOW TO WORKS | l/s | WASTE |  | WASTE:E1903
13084 | #N/A | #N/A | #N/A | E1908 | 130840CELL 1 INLET FLOW | l/s | WASTE |  | WASTE:E1908
13084 | #N/A | #N/A | #N/A | E1910 | 130840CELL 2 INLET FLOW | l/s | WASTE |  | WASTE:E1910
13084 | #N/A | #N/A | #N/A | E1912 | 130840CELL 3 INLET FLOW | l/s | WASTE |  | WASTE:E1912
13084 | #N/A | #N/A | #N/A | E1914 | 130840CELL 4 INLET FLOW | l/s | WASTE |  | WASTE:E1914
13084 | #N/A | #N/A | #N/A | E1917 | 130840BIOFOR PUMP FLOW | l/s | WASTE |  | WASTE:E1917
13084 | #N/A | #N/A | #N/A | E1922 | 130840BIOFOR COMMON WASHWATER FLOW | l/s | WASTE |  | WASTE:E1922
13086 | #N/A | #N/A | #N/A | E11928 | 130861EA032INLET FLOW | l/s | WASTE |  | WASTE:E11928
13086 | #N/A | #N/A | #N/A | E11931 | 130861FLOW TO TREATMENT WETLANDS AI | l/s | WASTE |  | WASTE:E11931
13086 | #N/A | #N/A | #N/A | E11932 | 130861FINAL EFFLUENT FLOW AI | l/s | WASTE |  | WASTE:E11932
13087 | #N/A | #N/A | #N/A | E3140 | 130870TREATMENT FLOW | l/s | WASTE |  | WASTE:E3140
13087 | #N/A | #N/A | #N/A | E3141 | 130870STORM FLOW | l/s | WASTE |  | WASTE:E3141
13087 | #N/A | #N/A | #N/A | E3142 | 130870EA139MCERT FINAL EFF FLOW | l/s | WASTE |  | WASTE:E3142
13088 | #N/A | #N/A | #N/A | E4526 | 130880FLOW TO WORKS | l/s | WASTE |  | WASTE:E4526
13090 | #N/A | #N/A | #N/A | E11210 | 130900INLET FLOW | l/s | WASTE |  | WASTE:E11210
13090 | #N/A | #N/A | #N/A | E11212 | 130900EA033MCERT INLET FLOW | l/s | WASTE |  | WASTE:E11212
13090 | #N/A | #N/A | #N/A | E11213 | 130900FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E11213
13090 | #N/A | #N/A | #N/A | E11280 | 130900REED BED 1 FLOW | l/s | WASTE |  | WASTE:E11280
13090 | #N/A | #N/A | #N/A | E11281 | 130900REED BED 2 FLOW | l/s | WASTE |  | WASTE:E11281
13090 | #N/A | #N/A | #N/A | E11282 | 130900REED BED 3 FLOW | l/s | WASTE |  | WASTE:E11282
13090 | #N/A | #N/A | #N/A | E11283 | 130900REED BED 4 FLOW | l/s | WASTE |  | WASTE:E11283
13090 | #N/A | #N/A | #N/A | E11284 | 130900REED BED 5 FLOW | l/s | WASTE |  | WASTE:E11284
13090 | #N/A | #N/A | #N/A | E11285 | 130900REED BED 6 FLOW | l/s | WASTE |  | WASTE:E11285
13091 | #N/A | #N/A | #N/A | E20734 | 130910FINAL FLOW | l/s | WASTE |  | WASTE:E20734
13091 | #N/A | #N/A | #N/A | E20735 | 130910DIDMARTON STW SAF FLOW METER | l/s | WASTE |  | WASTE:E20735
13091 | #N/A | #N/A | #N/A | E50001 | 130910EA225INLET FLOW | l/s | WASTE |  | WASTE:E50001
13092 | #N/A | #N/A | #N/A | E21783 | 130920EA141INLET FLOW | l/s | WASTE |  | WASTE:E21783
13094 | #N/A | #N/A | #N/A | E5535 | 130940EA142FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E5535
13095 | #N/A | #N/A | #N/A | E1935 | 130950INLET FLOW | l/s | WASTE |  | WASTE:E1935
13095 | #N/A | #N/A | #N/A | E1936 | 130950EA034FINAL EFF FLOW | l/s | WASTE |  | WASTE:E1936
13096 | #N/A | #N/A | #N/A | E9840 | 130960FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E9840
13096 | #N/A | #N/A | #N/A | E9841 | 130960FLOW TO STORM TANK | l/s | WASTE |  | WASTE:E9841
13096 | #N/A | #N/A | #N/A | E9843 | 130960PUMPED INLET FLOW | l/s | WASTE |  | WASTE:E9843
13096 | #N/A | #N/A | #N/A | E25529 | 130960FLOW TO FILTERS 3 AND 4 AN | l/s | WASTE |  | WASTE:E25529
13096 | #N/A | #N/A | #N/A | E25530 | 130960FLOW TO FILTERS 8 AND 9 AN | l/s | WASTE |  | WASTE:E25530
13096 | #N/A | #N/A | #N/A | E25531 | 130960FLOW TO DISTRIBUTION CHAMBER AN | l/s | WASTE |  | WASTE:E25531
13096 | #N/A | #N/A | #N/A | E31236 | 13096APRIMARY FERRIC DOSING PUMPS FLOWMETER | l/s | WASTE |  | WASTE:E31236
13096 | #N/A | #N/A | #N/A | E31237 | 13096ASECONDARY FERRIC DOSING PUMPS FLOWMETER | l/s | WASTE |  | WASTE:E31237
13096 | #N/A | #N/A | #N/A | E31366 | 130960RECIRC PUMPING STATION 3 FLOW | l/s | WASTE |  | WASTE:E31366
13096 | #N/A | #N/A | #N/A | E31368 | 130960FILTER 4 PUMPING STATION 4 FLOW | l/s | WASTE |  | WASTE:E31368
13096 | #N/A | #N/A | #N/A | E31370 | 130960FLOC PUMPING STATION FLOW | l/s | WASTE |  | WASTE:E31370
13096 | #N/A | #N/A | #N/A | E31373 | 130960LOWER INLET PUMPING STATION FLOW | l/s | WASTE |  | WASTE:E31373
13096 | #N/A | #N/A | #N/A | E31374 | 130960FINAL EFFLUENT OUTFLOW | l/s | WASTE |  | WASTE:E31374
13096 | #N/A | #N/A | #N/A | E31375 | 13096RECIRC PUMPING STATION 2 FLOW | l/s | WASTE |  | WASTE:E31375
13096 | #N/A | #N/A | #N/A | E31376 | 130960RECIRC PUMPING STATION 1 FLOW | l/s | WASTE |  | WASTE:E31376
13096 | #N/A | #N/A | #N/A | E31598 | 13096BRAW SLUDGE PS DELIVERY FLOWMTR | l/s | WASTE |  | WASTE:E31598
13096 | #N/A | #N/A | #N/A | E31602 | 13096BDRUM THICKENER FEED FLOWMETER | l/s | WASTE |  | WASTE:E31602
13096 | #N/A | #N/A | #N/A | E32047 | 13096AINLET FLOW FOR PUMP SET 1 | l/s | WASTE |  | WASTE:E32047
13096 | #N/A | #N/A | #N/A | E31599 | 13096BDELIV FLW FROM POLYMER DOSE P2 | l/s | WASTE |  | WASTE:E31599
13096 | #N/A | #N/A | #N/A | E31600 | 13096BDELIV FLW FROM POLYMER DOSE P1 | l/s | WASTE |  | WASTE:E31600
13096 | #N/A | #N/A | #N/A | E31601 | 13096BDEL FLW FROM THICKND SLDGE PMP | l/s | WASTE |  | WASTE:E31601
13098 | #N/A | #N/A | #N/A | E1953 | 130980EA143OUTFLOW | l/s | WASTE |  | WASTE:E1953
13098 | #N/A | #N/A | #N/A | E1958 | 130980FOUL WATER FLOW | l/s | WASTE |  | WASTE:E1958
13098 | #N/A | #N/A | #N/A | E1959 | 130980SLUDGE FLOW | l/s | WASTE |  | WASTE:E1959
13099 | #N/A | #N/A | #N/A | E16201 | 130991EA226INLET FLOW | l/s | WASTE |  | WASTE:E16201
13099 | #N/A | #N/A | #N/A | E31654 | 130991INLET FLOW SET 1 | l/s | WASTE |  | WASTE:E31654
13099 | #N/A | #N/A | #N/A | E31655 | 130991INLET FLOW SET 2 | l/s | WASTE |  | WASTE:E31655
13099 | #N/A | #N/A | #N/A | E31656 | 130991PUMP SET 1 FLOW RATE | l/s | WASTE |  | WASTE:E31656
13099 | #N/A | #N/A | #N/A | E31657 | 130991PUMP SET 2 FLOW RATE | l/s | WASTE |  | WASTE:E31657
13099 | #N/A | #N/A | #N/A | E31659 | 130991FLOC FEED FLOW METER ANG | l/s | WASTE |  | WASTE:E31659
13100 | #N/A | #N/A | #N/A | E1401 | 131000FLOW TO STORM | l/s | WASTE |  | WASTE:E1401
13100 | #N/A | #N/A | #N/A | E5406 | 131001FLOW TO STORM | l/s | WASTE2 |  | WASTE2:E5406
13101 | #N/A | #N/A | #N/A | E3155 | 131010INLET FLOW | l/s | WASTE |  | WASTE:E3155
13101 | #N/A | #N/A | #N/A | E3158 | 131010SAFF OUTLET FLOW | l/s | WASTE |  | WASTE:E3158
13101 | #N/A | #N/A | #N/A | E30444 | 131010STORM RETURN FLOW | l/s | WASTE |  | WASTE:E30444
13101 | #N/A | #N/A | #N/A | E30445 | 131010STORM OVERFLOW FLOW | l/s | WASTE |  | WASTE:E30445
13101 | #N/A | #N/A | #N/A | E31259 | 131010FILTER FEED FLOW | l/s | WASTE |  | WASTE:E31259
13101 | #N/A | #N/A | #N/A | E31260 | 131010RECIRC PUMP FLOW | l/s | WASTE |  | WASTE:E31260
13101 | #N/A | #N/A | #N/A | E97871 | 131010COMBINED RETURN FLOW ANG | l/s | WASTE |  | WASTE:E97871
13104 | #N/A | #N/A | #N/A | E3445 | 131041EA037FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E3445
13104 | #N/A | #N/A | #N/A | E3446 | 131041STORM FLOW | l/s | WASTE |  | WASTE:E3446
13104 | #N/A | #N/A | #N/A | E3449 | 131041TEMP OVERPUMPING FLOW METER | l/s | WASTE |  | WASTE:E3449
13104 | #N/A | #N/A | #N/A | E98019 | 13104APROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E98019
13104 | #N/A | #N/A | #N/A | E98024 | 13104APUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E98024
13104 | #N/A | #N/A | #N/A | E98051 | 13104BINLET PS FLOW AI | l/s | WASTE |  | WASTE:E98051
13105 | #N/A | #N/A | #N/A | E2185 | 131050FLOW TO STORM TANK | l/s | WASTE |  | WASTE:E2185
13105 | #N/A | #N/A | #N/A | E2186 | 131050EA038FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E2186
13105 | #N/A | #N/A | #N/A | E2191 | 131050FLOW CONTROL | l/s | WASTE |  | WASTE:E2191
13106 | #N/A | #N/A | #N/A | E1410 | 131060INLET FLOW | l/s | WASTE |  | WASTE:E1410
13106 | #N/A | #N/A | #N/A | E1411 | 131060EA144OUTLET FLOW | l/s | WASTE |  | WASTE:E1411
13106 | #N/A | #N/A | #N/A | E1428 | 131060INLET FLOW AVE | l/s | WASTE |  | WASTE:E1428
13107 | #N/A | #N/A | #N/A | E54920 | 131071INLET FLUME FLOW | l/s | WASTE |  | WASTE:E54920
13107 | #N/A | #N/A | #N/A | E54922 | 131071RISING MAIN FLOW ANG | l/s | WASTE |  | WASTE:E54922
13107 | #N/A | #N/A | #N/A | E54932 | 131071PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E54932
13107 | #N/A | #N/A | #N/A | E54944 | 131071PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E54944
13111 | #N/A | #N/A | #N/A | E13919 | 131110EA039OUTFALL FLOW | l/s | WASTE |  | WASTE:E13919
13111 | #N/A | #N/A | #N/A | E13920 | 131110SAF INLET FLOW ANLG | l/s | WASTE |  | WASTE:E13920
13113 | #N/A | #N/A | #N/A | E5456 | 131130EA146FINAL EFF FLOW | l/s | WASTE |  | WASTE:E5456
13116 | #N/A | #N/A | #N/A | E9239 | 131160EA380 MCERT SCRN WW FLOW ANG | l/s | WASTE |  | WASTE:E9239
13116 | #N/A | #N/A | #N/A | E10859 | 131160EA147FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E10859
13116 | #N/A | #N/A | #N/A | E10860 | 131160EA363 MCERT INLET FLOW ANG | l/s | WASTE |  | WASTE:E10860
13116 | #N/A | #N/A | #N/A | E53987 | 131160PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E53987
13116 | #N/A | #N/A | #N/A | E53995 | 131160PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E53995
13118 | #N/A | #N/A | #N/A | E5356 | 131180FLOW TO WORKS | l/s | WASTE |  | WASTE:E5356
13118 | #N/A | #N/A | #N/A | E5357 | 131180EA040FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E5357
13118 | #N/A | #N/A | #N/A | E35953 | 131180COAG DOSING SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E35953
13118 | #N/A | #N/A | #N/A | E35959 | 131180SEWERAGE FLOW | l/s | WASTE |  | WASTE:E35959
13120 | #N/A | #N/A | #N/A | E9403 | 131200EA041PULSAR FLOW | l/s | WASTE |  | WASTE:E9403
13120 | #N/A | #N/A | #N/A | E9404 | 131200SAF TANK INFLOW | l/s | WASTE |  | WASTE:E9404
13120 | #N/A | #N/A | #N/A | E32595 | 131200MBR FLOW | l/s | WASTE |  | WASTE:E32595
13121 | #N/A | #N/A | #N/A | E1430 | 131210EA042OUTFALL FLOW | l/s | WASTE |  | WASTE:E1430
13124 | #N/A | #N/A | #N/A | E4601 | 131241EA266FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E4601
13125 | #N/A | #N/A | #N/A | E1790 | 131251EA149INLET FLOW | l/s | WASTE |  | WASTE:E1790
13128 | #N/A | #N/A | #N/A | E9573 | 131280EA354 FPF MCERTS FLOW METER ANALOGUE INPUT | l/s | WASTE |  | WASTE:E9573
13128 | #N/A | #N/A | #N/A | E9575 | 131280STORM FLOW | l/s | WASTE |  | WASTE:E9575
13128 | #N/A | #N/A | #N/A | E9582 | 131280PRIMARY EFFLUENT PS 1 FLOW AN | l/s | WASTE |  | WASTE:E9582
13128 | #N/A | #N/A | #N/A | E9583 | 131280PRIMARY EFFLUENT PS 2 FLOW AN | l/s | WASTE |  | WASTE:E9583
13128 | #N/A | #N/A | #N/A | E30567 | 131281SLUDGE FLOW TO THICKENER 1 | l/s | WASTE |  | WASTE:E30567
13128 | #N/A | #N/A | #N/A | E30568 | 131281THICKENED SLUDGE FLOW | l/s | WASTE |  | WASTE:E30568
13128 | #N/A | #N/A | #N/A | E30575 | 131281CHEM DOSING FEED FLOW | l/s | WASTE |  | WASTE:E30575
13128 | #N/A | #N/A | #N/A | E30678 | 131281FERRIC INLET FLOW | l/s | WASTE |  | WASTE:E30678
13129 | #N/A | #N/A | #N/A | E4207 | 131291BRATCH LANE RISING MAIN FLOW | l/s | WASTE |  | WASTE:E4207
13129 | #N/A | #N/A | #N/A | E5305 | 131291FINAL EFFLUENT FLOW AVE | l/s | WASTE |  | WASTE:E5305
13129 | #N/A | #N/A | #N/A | E6161 | 131291INLET FLOW METER | l/s | WASTE |  | WASTE:E6161
13129 | #N/A | #N/A | #N/A | E31695 | 13129ASAND FILTER PS INLET FLOW AI | l/s | WASTE |  | WASTE:E31695
13129 | #N/A | #N/A | #N/A | E31699 | 13129ASAND FILTER 1 INLET FLOW AI | l/s | WASTE |  | WASTE:E31699
13129 | #N/A | #N/A | #N/A | E31701 | 13129ASAND FILTER 2 INLET FLOW AI | l/s | WASTE |  | WASTE:E31701
13129 | #N/A | #N/A | #N/A | E31705 | 13129ARETURN LIQUOR PUMPED FLOW AI | l/s | WASTE |  | WASTE:E31705
13129 | #N/A | #N/A | #N/A | E31708 | 13129AEA357FPF MCERTS FLOW METER ANALOGUE INPUT | l/s | WASTE |  | WASTE:E31708
13129 | #N/A | #N/A | #N/A | E31715 | 13129ASLUDGE PUMPED FLOW AI | l/s | WASTE |  | WASTE:E31715
13129 | #N/A | #N/A | #N/A | E31901 | 13129BINLET FLOW FOR DOSE SET 1 | l/s | WASTE |  | WASTE:E31901
13129 | #N/A | #N/A | #N/A | E31902 | 13129BINLET FLOW FOR DOSE SET 2 | l/s | WASTE |  | WASTE:E31902
13130 | #N/A | #N/A | #N/A | E3891 | 131300EA045MCERT INLET FLOW | l/s | WASTE |  | WASTE:E3891
13130 | #N/A | #N/A | #N/A | E31917 | 131300INLET FLOW | l/s | WASTE |  | WASTE:E31917
13130 | #N/A | #N/A | #N/A | E31918 | 131300STORM RETURN FLOW | l/s | WASTE |  | WASTE:E31918
13131 | #N/A | #N/A | #N/A | E4106 | 131310INLET FLOW ANALOGUE | l/s | WASTE |  | WASTE:E4106
13131 | #N/A | #N/A | #N/A | E4107 | 131310EA150INLET PUMP FLOW | l/s | WASTE |  | WASTE:E4107
13131 | #N/A | #N/A | #N/A | E4113 | 131310BALANCE TANK FLOW | l/s | WASTE |  | WASTE:E4113
13131 | #N/A | #N/A | #N/A | E4117 | 131310RECIRC FLOW | l/s | WASTE |  | WASTE:E4117
13131 | #N/A | #N/A | #N/A | E4118 | 131310EA151VSD FFT FLOW | l/s | WASTE |  | WASTE:E4118
13131 | #N/A | #N/A | #N/A | E4119 | 131310EA152STORM RETURN FLOW | l/s | WASTE |  | WASTE:E4119
13131 | #N/A | #N/A | #N/A | E5211 | 131310INLET FLOW 1 | l/s | WASTE |  | WASTE:E5211
13131 | #N/A | #N/A | #N/A | E22515 | 131310GBT DISCHARGE FLOW | l/s | WASTE |  | WASTE:E22515
13131 | #N/A | #N/A | #N/A | E31253 | 131310FFT FLOW | l/s | WASTE |  | WASTE:E31253
13131 | #N/A | #N/A | #N/A | E22522 | 131310RECIRC FLW | l/s | WASTE |  | WASTE:E22522
13132 | #N/A | #N/A | #N/A | E11839 | 131321 OUTLET FLOW | l/s | WASTE |  | WASTE:E11839
13132 | #N/A | #N/A | #N/A | E11850 | 131321FLOW TO TREATMENT SP | l/s | WASTE |  | WASTE:E11850
13132 | #N/A | #N/A | #N/A | E24292 | 131321RECIRC FLOW | l/s | WASTE |  | WASTE:E24292
13132 | #N/A | #N/A | #N/A | E24293 | 131321REQ FLOW TO TRICK FLTR | l/s | WASTE |  | WASTE:E24293
13132 | #N/A | #N/A | #N/A | E24300 | 131321EA046 MCERTS FLOW TO FULL TREATMENT | l/s | WASTE |  | WASTE:E24300
13132 | #N/A | #N/A | #N/A | E24315 | 131321SANDFILTER INLET FLOW | l/s | WASTE |  | WASTE:E24315
13132 | #N/A | #N/A | #N/A | E24317 | 131321SF BACKWASH FLOW | l/s | WASTE |  | WASTE:E24317
13132 | #N/A | #N/A | #N/A | E55049 | 131321FILTER FEED PS FLOW ANG | l/s | WASTE |  | WASTE:E55049
13132 | #N/A | #N/A | #N/A | E55585 | 131321PROFILE STORM DOSING START FLOW AI | l/s | WASTE |  | WASTE:E55585
13132 | #N/A | #N/A | #N/A | E55593 | 131321PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E55593
13132 | #N/A | #N/A | #N/A | E55598 | 131321PUMP SET 2 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E55598
13134 | #N/A | #N/A | #N/A | E3315 | 131340FLOW FROM STREET | l/s | WASTE |  | WASTE:E3315
13134 | #N/A | #N/A | #N/A | E3316 | 131340FLOW FROM PORCHESTAL | l/s | WASTE |  | WASTE:E3316
13134 | #N/A | #N/A | #N/A | E3317 | 131340OUTLET FLOW | l/s | WASTE |  | WASTE:E3317
13134 | #N/A | #N/A | #N/A | E38388 | 131340GLASTONBURY STW INLET FLOWMETER | l/s | WASTE |  | WASTE:E38388
13134 | #N/A | #N/A | #N/A | E38395 | 131340PUMP SET 2 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E38395
13134 | #N/A | #N/A | #N/A | E38400 | 131340COMBINED INLET FLOW | l/s | WASTE |  | WASTE:E38400
13134 | #N/A | #N/A | #N/A | E38402 | 131340RECIRCULATION FLOW SETPOINT | l/s | WASTE |  | WASTE:E38402
13134 | #N/A | #N/A | #N/A | E38403 | 131340SFFT FLOW SETPOINT | l/s | WASTE |  | WASTE:E38403
13134 | #N/A | #N/A | #N/A | E38413 | 131340PUMP SET 1 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E38413
13134 | #N/A | #N/A | #N/A | E38418 | 131340PUMP SET 2 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E38418
13134 | #N/A | #N/A | #N/A | E52174 | 131340TASF COMBINED FLOW | l/s | WASTE |  | WASTE:E52174
13134 | #N/A | #N/A | #N/A | E52766 | 131340TASF FLTR 1 FLOW ANG | l/s | WASTE |  | WASTE:E52766
13134 | #N/A | #N/A | #N/A | E52767 | 131340TASF FLTR 2 FLOW ANG | l/s | WASTE |  | WASTE:E52767
13134 | #N/A | #N/A | #N/A | E52768 | 131340TASF FLTR 3 FLOW ANG | l/s | WASTE |  | WASTE:E52768
13134 | #N/A | #N/A | #N/A | E52769 | 131340TASF FLTR 4 FLOW ANG | l/s | WASTE |  | WASTE:E52769
13134 | #N/A | #N/A | #N/A | E52770 | 131340TASF FLTR 5 FLOW ANG | l/s | WASTE |  | WASTE:E52770
13134 | #N/A | #N/A | #N/A | E52771 | 131340TASF FLTR 6 FLOW ANG | l/s | WASTE |  | WASTE:E52771
13134 | #N/A | #N/A | #N/A | E52772 | 131340TASF FLTR 7 FLOW ANG | l/s | WASTE |  | WASTE:E52772
13134 | #N/A | #N/A | #N/A | E52773 | 131340TASF FLTR 8 FLOW ANG | l/s | WASTE |  | WASTE:E52773
13134 | #N/A | #N/A | #N/A | E52923 | 131340RECIRCULATION FLOW | l/s | WASTE |  | WASTE:E52923
13134 | #N/A | #N/A | #N/A | E52936 | 131340INLET FLOW LASER | l/s | WASTE |  | WASTE:E52936
13134 | #N/A | #N/A | #N/A | E52937 | 131340INLET FLOW RADAR | l/s | WASTE |  | WASTE:E52937
13134 | #N/A | #N/A | #N/A | E55910 | 131340PANAMETRICS FFT FLOW | l/s | WASTE |  | WASTE:E55910
13134 | #N/A | #N/A | #N/A | E52786 | 131340FINAL EFF FLW ANG | l/s | WASTE |  | WASTE:E52786
13136 | #N/A | #N/A | #N/A | E8194 | 131360INLET TO SAFF FLOW | l/s | WASTE |  | WASTE:E8194
13136 | #N/A | #N/A | #N/A | E10682 | 131360EA154STW MCERT EFFLUENT FLOW | l/s | WASTE |  | WASTE:E10682
13137 | #N/A | #N/A | #N/A | E2920 | 131370EA047INLET FLOW | l/s | WASTE |  | WASTE:E2920
13140 | #N/A | #N/A | #N/A | E2430 | 131400EA155OUTFALL FLOW | l/s | WASTE |  | WASTE:E2430
13142 | #N/A | #N/A | #N/A | E2205 | 131420EA156OUTLET FLOW | l/s | WASTE |  | WASTE:E2205
13142 | #N/A | #N/A | #N/A | E2206 | 131420INLET FLOW | l/s | WASTE |  | WASTE:E2206
13143 | #N/A | #N/A | #N/A | E16526 | 131431EA271FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E16526
13143 | #N/A | #N/A | #N/A | E16528 | 131431TEMP HOLDING TANK FLOW METER | l/s | WASTE |  | WASTE:E16528
13144 | #N/A | #N/A | #N/A | E1967 | 131440EA048INLET FLOW | l/s | WASTE |  | WASTE:E1967
13144 | #N/A | #N/A | #N/A | E1968 | 131440INLET VALVE CONTROL FLOW | l/s | WASTE |  | WASTE:E1968
13146 | #N/A | #N/A | #N/A | E16540 | 131461EA049FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E16540
13146 | #N/A | #N/A | #N/A | E33455 | 131461FFT FLOW METER AI | l/s | WASTE |  | WASTE:E33455
13146 | #N/A | #N/A | #N/A | E6186 | 13146APROFILE STORM DOSING START FLOW | l/s | WASTE2 |  | WASTE2:E6186
13146 | #N/A | #N/A | #N/A | E6191 | 13146APUMP SET 1 SEWAGE FLOW | l/s | WASTE2 |  | WASTE2:E6191
13148 | #N/A | #N/A | #N/A | E2950 | 131480INLET FLOW | l/s | WASTE |  | WASTE:E2950
13149 | #N/A | #N/A | #N/A | E8169 | 131490EA269MCERT INLET FLOW | l/s | WASTE |  | WASTE:E8169
13150 | #N/A | #N/A | #N/A | E1440 | 131500EA230INLET FLOW | l/s | WASTE |  | WASTE:E1440
13152 | #N/A | #N/A | #N/A | E968 | 131520SCADA FLOW TO STORM STREAM 2 | l/s | WASTE |  | WASTE:E968
13152 | #N/A | #N/A | #N/A | E971 | 131520SCADA FLOW TO TMT STREAM 2 | l/s | WASTE |  | WASTE:E971
13152 | #N/A | #N/A | #N/A | E975 | 131520SCADA FLOW TO STORM STREAM 1 | l/s | WASTE |  | WASTE:E975
13152 | #N/A | #N/A | #N/A | E980 | 131520STREAM 1 RAS AB FLOW | l/s | WASTE |  | WASTE:E980
13152 | #N/A | #N/A | #N/A | E981 | 131520STREAM 1 RAS CD FLOW | l/s | WASTE |  | WASTE:E981
13152 | #N/A | #N/A | #N/A | E983 | 131520UV FLOW 2 | l/s | WASTE |  | WASTE:E983
13152 | #N/A | #N/A | #N/A | E984 | 131520UV FLOW 1 | l/s | WASTE |  | WASTE:E984
13152 | #N/A | #N/A | #N/A | E8558 | 131520EA157MCERT FLOW AB | l/s | WASTE |  | WASTE:E8558
13152 | #N/A | #N/A | #N/A | E8559 | 131520EA158MCERT FLOW CD | l/s | WASTE |  | WASTE:E8559
13152 | #N/A | #N/A | #N/A | E9335 | 131520FE STREAM 2 NIVUS FLOW | l/s | WASTE |  | WASTE:E9335
13152 | #N/A | #N/A | #N/A | E9336 | 131520FE STREAM 1 NIVUS FLOW | l/s | WASTE |  | WASTE:E9336
13152 | #N/A | #N/A | #N/A | E9337 | 131520FE COMBINED NIVUS FLOW | l/s | WASTE |  | WASTE:E9337
13152 | #N/A | #N/A | #N/A | E10020 | 131521STREAM 2 INLET FLOW | l/s | WASTE |  | WASTE:E10020
13152 | #N/A | #N/A | #N/A | E10049 | 131521FLOW TO STORM A | l/s | WASTE |  | WASTE:E10049
13152 | #N/A | #N/A | #N/A | E10050 | 131521FLOW TO STORM 2 | l/s | WASTE |  | WASTE:E10050
13152 | #N/A | #N/A | #N/A | E10056 | 131521AB RAS FLOW LS | l/s | WASTE |  | WASTE:E10056
13152 | #N/A | #N/A | #N/A | E10057 | 131521CD RAS FLOW LS | l/s | WASTE |  | WASTE:E10057
13152 | #N/A | #N/A | #N/A | E10058 | 131521EJ RAS FLOW LS | l/s | WASTE |  | WASTE:E10058
13152 | #N/A | #N/A | #N/A | E29561 | 131520STREAM 1 INLET FLOW | l/s | WASTE |  | WASTE:E29561
13152 | #N/A | #N/A | #N/A | E29568 | 131520STREAM 2 INLET FLOW | l/s | WASTE |  | WASTE:E29568
13152 | #N/A | #N/A | #N/A | E29569 | 131520STREAM 2 STORM FLOW | l/s | WASTE |  | WASTE:E29569
13152 | #N/A | #N/A | #N/A | E29571 | 131520EA277NEW TREATMENT FLOW | l/s | WASTE |  | WASTE:E29571
13152 | #N/A | #N/A | #N/A | E29574 | 131520STORM A FLOW | l/s | WASTE |  | WASTE:E29574
13152 | #N/A | #N/A | #N/A | E29575 | 131520STORM B FLOW | l/s | WASTE |  | WASTE:E29575
13152 | #N/A | #N/A | #N/A | E32198 | 131521STREAM 2 RAS FLOW ANG | l/s | WASTE |  | WASTE:E32198
13152 | #N/A | #N/A | #N/A | E33133 | 131520SUMMATED FLOW | l/s | WASTE |  | WASTE:E33133
13152 | #N/A | #N/A | #N/A | E56610 | 131521STREAM 1 TRANSFER COMMON FLOW AI | l/s | WASTE |  | WASTE:E56610
13152 | #N/A | #N/A | #N/A | E982 | 131520STREAM 2 RAS FLW | l/s | WASTE |  | WASTE:E982
13156 | #N/A | #N/A | #N/A | E2216 | 131560EA018INLET FLOW | l/s | WASTE |  | WASTE:E2216
13156 | #N/A | #N/A | #N/A | E7495 | 131561MARSTON MAGNA FLOW | l/s | WASTE2 |  | WASTE2:E7495
13156 | #N/A | #N/A | #N/A | E7496 | 131561YEOVILTON WEIR FLOW | l/s | WASTE2 |  | WASTE2:E7496
13156 | #N/A | #N/A | #N/A | E7497 | 131561WEST CAMEL FLOW | l/s | WASTE2 |  | WASTE2:E7497
13156 | #N/A | #N/A | #N/A | E7498 | 131561CHILTON CANTELLO FLOW | l/s | WASTE2 |  | WASTE2:E7498
13157 | #N/A | #N/A | #N/A | E12976 | 131571EA160FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E12976
13157 | #N/A | #N/A | #N/A | E12978 | 131571HRF FLOW METER | l/s | WASTE |  | WASTE:E12978
13158 | #N/A | #N/A | #N/A | E16578 | 131581EA161FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E16578
13158 | #N/A | #N/A | #N/A | E30333 | 131581INLET FLOW ANALOG | l/s | WASTE |  | WASTE:E30333
13158 | #N/A | #N/A | #N/A | E30334 | 131581SLUDGE FLOW ANALOG | l/s | WASTE |  | WASTE:E30334
13158 | #N/A | #N/A | #N/A | E30337 | 131581DRAININGS RETURN FLOW ANALOG | l/s | WASTE |  | WASTE:E30337
13158 | #N/A | #N/A | #N/A | E30348 | 131581IN FLOW SET 1 | l/s | WASTE |  | WASTE:E30348
13158 | #N/A | #N/A | #N/A | E30349 | 131581IN FLOW SET 2 | l/s | WASTE |  | WASTE:E30349
13158 | #N/A | #N/A | #N/A | E31239 | 13158ASANDFILTER FEED PS FLOW | l/s | WASTE |  | WASTE:E31239
13158 | #N/A | #N/A | #N/A | E31243 | 13158ASANDFILTER 1 IN FLOW | l/s | WASTE |  | WASTE:E31243
13158 | #N/A | #N/A | #N/A | E31244 | 13158ASANDFILTER 2 IN FLOW | l/s | WASTE |  | WASTE:E31244
13158 | #N/A | #N/A | #N/A | E31245 | 13158ASANDFILTER 3 IN FLOW | l/s | WASTE |  | WASTE:E31245
13158 | #N/A | #N/A | #N/A | E31263 | 13158ASTORM RETURN FLOW ANG | l/s | WASTE |  | WASTE:E31263
13160 | #N/A | #N/A | #N/A | E2236 | 131600EA051 MCERT INLET FLOW | l/s | WASTE |  | WASTE:E2236
13160 | #N/A | #N/A | #N/A | E2239 | 131600FLOW | l/s | WASTE |  | WASTE:E2239
13160 | #N/A | #N/A | #N/A | E54770 | 131600PUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E54770
13160 | #N/A | #N/A | #N/A | E54778 | 131600PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E54778
13161 | #N/A | #N/A | #N/A | E2130 | 131610EA052FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E2130
13161 | #N/A | #N/A | #N/A | E2148 | 131610FLOW TO TREATMENT AVE | l/s | WASTE |  | WASTE:E2148
13162 | #N/A | #N/A | #N/A | E55404 | 131622MCERTS FLOWMETER AI | l/s | WASTE |  | WASTE:E55404
13162 | #N/A | #N/A | #N/A | E55409 | 13162AINLET PS DWF FLOW AI | l/s | WASTE |  | WASTE:E55409
13162 | #N/A | #N/A | #N/A | E55410 | 13162ASTORM PUMP FLOW AI | l/s | WASTE |  | WASTE:E55410
13162 | #N/A | #N/A | #N/A | E55413 | 13162AEA162MCERTS INLET FLUME FLOW TO TREATMENT AI | l/s | WASTE |  | WASTE:E55413
13162 | #N/A | #N/A | #N/A | E55415 | 13162AFINAL FLOW AI | l/s | WASTE |  | WASTE:E55415
13162 | #N/A | #N/A | #N/A | E55427 | 13162APUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E55427
13162 | #N/A | #N/A | #N/A | E55435 | 13162APUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E55435
13162 | #N/A | #N/A | #N/A | E3300 | 131623MCERT FLOWMETER | l/s | WASTE2 |  | WASTE2:E3300
13163 | #N/A | #N/A | #N/A | E9007 | 131630FLOW TO TREATMENT OLD | l/s | WASTE |  | WASTE:E9007
13163 | #N/A | #N/A | #N/A | E9008 | 131630MCERTS FLOWMETER OLD | l/s | WASTE |  | WASTE:E9008
13163 | #N/A | #N/A | #N/A | E36738 | 131631S1 FLOW TO TREATMENT AI | l/s | WASTE |  | WASTE:E36738
13163 | #N/A | #N/A | #N/A | E36739 | 131631EA053 S1 MCERTS FLOW AI | l/s | WASTE |  | WASTE:E36739
13163 | #N/A | #N/A | #N/A | E36743 | 131631S1 SAMPLING CHAMBER FLOW | l/s | WASTE |  | WASTE:E36743
13163 | #N/A | #N/A | #N/A | E36753 | 131631BIOLOGICAL FILTER FEED PS FLOW | l/s | WASTE |  | WASTE:E36753
13163 | #N/A | #N/A | #N/A | E96317 | 13163BPROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E96317
13163 | #N/A | #N/A | #N/A | E96322 | 13163BPUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E96322
13164 | #N/A | #N/A | #N/A | E1245 | 131640EA054MCERT INLET FLOW | l/s | WASTE |  | WASTE:E1245
13165 | #N/A | #N/A | #N/A | E1455 | 131650INLET FLOW | l/s | WASTE |  | WASTE:E1455
13165 | #N/A | #N/A | #N/A | E1456 | 131650PUMP FLOW | l/s | WASTE |  | WASTE:E1456
13165 | #N/A | #N/A | #N/A | E1457 | 131650WARMLEY SEWER FLOW | l/s | WASTE |  | WASTE:E1457
13165 | #N/A | #N/A | #N/A | E1458 | 131650SALTFORD SEWER FLOW | l/s | WASTE |  | WASTE:E1458
13165 | #N/A | #N/A | #N/A | E1459 | 131650OUTLET FLOW | l/s | WASTE |  | WASTE:E1459
13165 | #N/A | #N/A | #N/A | E1460 | 131650EA231MCERT FFT FLOW | l/s | WASTE |  | WASTE:E1460
13165 | #N/A | #N/A | #N/A | E1461 | 131650NEW INLET FLOW | l/s | WASTE |  | WASTE:E1461
13165 | #N/A | #N/A | #N/A | E1464 | 131650COAG INLET FLOW | l/s | WASTE |  | WASTE:E1464
13165 | #N/A | #N/A | #N/A | E1485 | 131650RECIRC PLANT FLOWMETER 1 | l/s | WASTE |  | WASTE:E1485
13165 | #N/A | #N/A | #N/A | E1486 | 131650RECIRC PLANT FLOWMETER 2 | l/s | WASTE |  | WASTE:E1486
13168 | #N/A | #N/A | #N/A | E26075 | 131681EA272NEW INLET MCERT FLOW METER | l/s | WASTE |  | WASTE:E26075
13168 | #N/A | #N/A | #N/A | E26076 | 131681SCREEN WASHWATER MCERT FLOW | l/s | WASTE |  | WASTE:E26076
13168 | #N/A | #N/A | #N/A | E26088 | 131681FINAL EFFLUENT FLOW ANLG | l/s | WASTE |  | WASTE:E26088
13171 | #N/A | #N/A | #N/A | E2720 | 131710CLEVEDON FLOW | l/s | WASTE |  | WASTE:E2720
13171 | #N/A | #N/A | #N/A | E2726 | 131710OUTLET FLOW | l/s | WASTE |  | WASTE:E2726
13171 | #N/A | #N/A | #N/A | E2727 | 131710EA232MCERT DWF FLOW | l/s | WASTE |  | WASTE:E2727
13171 | #N/A | #N/A | #N/A | E12688 | 131710CH 1 WATER FLOW | l/s | WASTE |  | WASTE:E12688
13171 | #N/A | #N/A | #N/A | E12693 | 131710CH 2 WATER FLOW | l/s | WASTE |  | WASTE:E12693
13171 | #N/A | #N/A | #N/A | E26897 | 131710RETURN EFFLUENT FLOW | l/s | WASTE |  | WASTE:E26897
13171 | #N/A | #N/A | #N/A | E29208 | 131710DWF FLOW TO HRF 1 IN | l/s | WASTE |  | WASTE:E29208
13171 | #N/A | #N/A | #N/A | E29209 | 131710DWF FLOW TO HRF 2 IN | l/s | WASTE |  | WASTE:E29209
13171 | #N/A | #N/A | #N/A | E29210 | 131710STORM FLOW TO HRF 1 IN | l/s | WASTE |  | WASTE:E29210
13171 | #N/A | #N/A | #N/A | E29211 | 131710STORM FLOW TO HRF 2 IN | l/s | WASTE |  | WASTE:E29211
13171 | #N/A | #N/A | #N/A | E29212 | 131710BAF FLOW | l/s | WASTE |  | WASTE:E29212
13171 | #N/A | #N/A | #N/A | E96706 | 13171AMIXING VALVE INLET FLOW AI | l/s | WASTE |  | WASTE:E96706
13172 | #N/A | #N/A | #N/A | E10582 | 131720EA055FLOW TO WORKS ISCO | l/s | WASTE |  | WASTE:E10582
13172 | #N/A | #N/A | #N/A | E20177 | 131720UV FLOW | l/s | WASTE |  | WASTE:E20177
13172 | #N/A | #N/A | #N/A | E50047 | 131720DUTY RISING MAIN FLOW | l/s | WASTE |  | WASTE:E50047
13172 | #N/A | #N/A | #N/A | E50048 | 131720ASSIST RISING MAIN FLOW | l/s | WASTE |  | WASTE:E50048
13172 | #N/A | #N/A | #N/A | E9672 | 131720FLW TO TREATMENT | l/s | WASTE |  | WASTE:E9672
13172 | #N/A | #N/A | #N/A | E9675 | 131720STORM FLW TO STRM TNKS | l/s | WASTE |  | WASTE:E9675
13173 | #N/A | #N/A | #N/A | E8886 | 131730EA163INLET FLOW | l/s | WASTE |  | WASTE:E8886
13174 | #N/A | #N/A | #N/A | E4676 | 131741INLET FLOW | l/s | WASTE |  | WASTE:E4676
13174 | #N/A | #N/A | #N/A | E4677 | 131741EA164OUTLET FLOW | l/s | WASTE |  | WASTE:E4677
13175 | #N/A | #N/A | #N/A | E1820 | 131750INLET FLOW | l/s | WASTE |  | WASTE:E1820
13175 | #N/A | #N/A | #N/A | E1822 | 131750EA233INLET FLOW | l/s | WASTE |  | WASTE:E1822
13177 | #N/A | #N/A | #N/A | E1320 | 131770EA056FPF MCERTS FLOW METER ANALOGUE INPUT | l/s | WASTE |  | WASTE:E1320
13177 | #N/A | #N/A | #N/A | E1321 | 131770INCOMING RISING MAIN FLOW | l/s | WASTE |  | WASTE:E1321
13177 | #N/A | #N/A | #N/A | E1323 | 131770INLET FLOW | l/s | WASTE |  | WASTE:E1323
13177 | #N/A | #N/A | #N/A | E1338 | 131770INLET FLOW AVE | l/s | WASTE |  | WASTE:E1338
13178 | #N/A | #N/A | #N/A | E4141 | 131780EA165OUTFLOW | l/s | WASTE |  | WASTE:E4141
13180 | #N/A | #N/A | #N/A | E2980 | 131800EA234OUTLET FLOW | l/s | WASTE |  | WASTE:E2980
13181 | #N/A | #N/A | #N/A | E17370 | 131811LOPEN INLET FLOW | l/s | WASTE |  | WASTE:E17370
13181 | #N/A | #N/A | #N/A | E17388 | 131811SCREENS FLOW | l/s | WASTE |  | WASTE:E17388
13181 | #N/A | #N/A | #N/A | E17390 | 131811WASH WATER FLOW | l/s | WASTE |  | WASTE:E17390
13181 | #N/A | #N/A | #N/A | E17391 | 131811TNK 1 PERM FLOW | l/s | WASTE |  | WASTE:E17391
13181 | #N/A | #N/A | #N/A | E17392 | 131811TNK 2 PERM FLOW | l/s | WASTE |  | WASTE:E17392
13181 | #N/A | #N/A | #N/A | E17393 | 131811TNK 3 PERM FLOW | l/s | WASTE |  | WASTE:E17393
13181 | #N/A | #N/A | #N/A | E17394 | 131811TNK 4 PERM FLOW | l/s | WASTE |  | WASTE:E17394
13181 | #N/A | #N/A | #N/A | E17395 | 131811TNK 1 SLUDGE FLOW | l/s | WASTE |  | WASTE:E17395
13181 | #N/A | #N/A | #N/A | E17396 | 131811TNK 2 SLUDGE FLOW | l/s | WASTE |  | WASTE:E17396
13181 | #N/A | #N/A | #N/A | E17397 | 131811TNK 3 SLUDGE FLOW | l/s | WASTE |  | WASTE:E17397
13181 | #N/A | #N/A | #N/A | E17398 | 131811TNK 4 SLUDGE FLOW | l/s | WASTE |  | WASTE:E17398
13181 | #N/A | #N/A | #N/A | E17413 | 131811SEAVINGTON FLOW | l/s | WASTE |  | WASTE:E17413
13181 | #N/A | #N/A | #N/A | E17389 | 131811INFLUENT SCREENED FLW | l/s | WASTE |  | WASTE:E17389
13181 | #N/A | #N/A | #N/A | E17399 | 131811SLUDGE DRAW TNK FLW | l/s | WASTE |  | WASTE:E17399
13182 | #N/A | #N/A | #N/A | E2451 | 131821EA058FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E2451
13182 | #N/A | #N/A | #N/A | E7613 | 131821INLET FLOW | l/s | WASTE |  | WASTE:E7613
13184 | #N/A | #N/A | #N/A | E2995 | 131840EA235OUTLET FLOW | l/s | WASTE |  | WASTE:E2995
13187 | #N/A | #N/A | #N/A | E5630 | 131870EA236MCERT INLET FLOW | l/s | WASTE |  | WASTE:E5630
13188 | #N/A | #N/A | #N/A | E16774 | 131881INLET CHANNEL FLOW ANLG | l/s | WASTE |  | WASTE:E16774
13190 | #N/A | #N/A | #N/A | E9332 | 131900RISING MAIN FLOW AL | l/s | WASTE |  | WASTE:E9332
13190 | #N/A | #N/A | #N/A | E9411 | 131900EA355FPF MCERTS FLOW METER ANALOGUE INPUT | l/s | WASTE |  | WASTE:E9411
13190 | #N/A | #N/A | #N/A | E9412 | 131900OUTFALL FLOW | l/s | WASTE |  | WASTE:E9412
13190 | #N/A | #N/A | #N/A | E9415 | 131900STORM FLOW TO HARBOUR | l/s | WASTE |  | WASTE:E9415
13190 | #N/A | #N/A | #N/A | E17315 | 131900UV FLOW | l/s | WASTE |  | WASTE:E17315
13191 | #N/A | #N/A | #N/A | E16878 | 131911EA168FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E16878
13192 | #N/A | #N/A | #N/A | E16903 | 131922FINAL FLOW | l/s | WASTE |  | WASTE:E16903
13192 | #N/A | #N/A | #N/A | E55091 | 131922EFFLUENT SAMPLING CHAMBER FLOW ANG | l/s | WASTE |  | WASTE:E55091
13192 | #N/A | #N/A | #N/A | E55094 | 131922EA060INLET FLUME FLOW ANG | l/s | WASTE |  | WASTE:E55094
13192 | #N/A | #N/A | #N/A | E55102 | 131922PUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E55102
13192 | #N/A | #N/A | #N/A | E55110 | 131922PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E55110
13193 | #N/A | #N/A | #N/A | E3015 | 131930EA061INLET FLOW | l/s | WASTE |  | WASTE:E3015
13193 | #N/A | #N/A | #N/A | E3031 | 131930TANNERS BRIDGE RISING MAIN FLOW | l/s | WASTE |  | WASTE:E3031
13193 | #N/A | #N/A | #N/A | E3032 | 131930CORSTON RISING MAIN FLOW | l/s | WASTE |  | WASTE:E3032
13193 | #N/A | #N/A | #N/A | E3033 | 131930COWBRIDGE RISING MAIN FLOW | l/s | WASTE |  | WASTE:E3033
13193 | #N/A | #N/A | #N/A | E3034 | 131930TANNER BRIDGE RISING MAIN FLOW | l/s | WASTE |  | WASTE:E3034
13193 | #N/A | #N/A | #N/A | E26412 | 131930BELT PRESS FLOW | l/s | WASTE |  | WASTE:E26412
13196 | #N/A | #N/A | #N/A | E22884 | 131960EA062FLOW ANLG | l/s | WASTE |  | WASTE:E22884
13196 | #N/A | #N/A | #N/A | E32094 | 131960INLET FLOW ANG | l/s | WASTE |  | WASTE:E32094
13198 | #N/A | #N/A | #N/A | E56654 | 13198AEA256INLET CHANNEL FLOW TO WORKS MCERT | l/s | WASTE |  | WASTE:E56654
13198 | #N/A | #N/A | #N/A | E56655 | 13198AWORKS RETURN FLOW AI | l/s | WASTE |  | WASTE:E56655
13198 | #N/A | #N/A | #N/A | E56656 | 13198ATSR FEED PUMP STATION FLOW AI | l/s | WASTE |  | WASTE:E56656
13198 | #N/A | #N/A | #N/A | E56662 | 13198ATSR FILTER 1 FEED FLOW | l/s | WASTE |  | WASTE:E56662
13198 | #N/A | #N/A | #N/A | E56663 | 13198ATSR FILTER 2 FEED FLOW | l/s | WASTE |  | WASTE:E56663
13198 | #N/A | #N/A | #N/A | E96397 | 13198BPROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E96397
13198 | #N/A | #N/A | #N/A | E96402 | 13198BPUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E96402
13199 | #N/A | #N/A | #N/A | E19517 | 131991FINAL OUTLET FLOW | l/s | WASTE |  | WASTE:E19517
13199 | #N/A | #N/A | #N/A | E19521 | 131991INLET FLOW | l/s | WASTE |  | WASTE:E19521
13199 | #N/A | #N/A | #N/A | E7563 | 13199ASTORM RETURN FLOWMETER AI | l/s | WASTE2 |  | WASTE2:E7563
13199 | #N/A | #N/A | #N/A | E7568 | 13199AEA063INLET FLOWMETER MCERTS AI | l/s | WASTE2 |  | WASTE2:E7568
13199 | #N/A | #N/A | #N/A | E7624 | 13199BPROFILE STORM DOSING START FLOW | l/s | WASTE2 |  | WASTE2:E7624
13199 | #N/A | #N/A | #N/A | E7629 | 13199BPUMP SET 1 SEWAGE FLOW | l/s | WASTE2 |  | WASTE2:E7629
13200 | #N/A | #N/A | #N/A | E23720 | 132001SAF FEED FLOWMETER | l/s | WASTE |  | WASTE:E23720
13200 | #N/A | #N/A | #N/A | E23727 | 132001EA169INLET FLOWMETER FLOW | l/s | WASTE |  | WASTE:E23727
13200 | #N/A | #N/A | #N/A | E23766 | 132001RECIRCULATION FLOW AI | l/s | WASTE |  | WASTE:E23766
13200 | #N/A | #N/A | #N/A | E23775 | 132001WORKS BALANCE TANK OUTLET FLOW AI | l/s | WASTE |  | WASTE:E23775
13201 | #N/A | #N/A | #N/A | E2020 | 132011EA065FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E2020
13201 | #N/A | #N/A | #N/A | E2022 | 132011DUPLICATE MCERT FLOW | l/s | WASTE |  | WASTE:E2022
13202 | #N/A | #N/A | #N/A | E11749 | 132021TREATMENT FLOW | l/s | WASTE |  | WASTE:E11749
13202 | #N/A | #N/A | #N/A | E11750 | 132021EA170OUTFLOW | l/s | WASTE |  | WASTE:E11750
13204 | #N/A | #N/A | #N/A | E1260 | 132040EA171INLET FLOW | l/s | WASTE |  | WASTE:E1260
13204 | #N/A | #N/A | #N/A | E1262 | 132040SAF FLOW | l/s | WASTE |  | WASTE:E1262
13204 | #N/A | #N/A | #N/A | E9366 | 132040INLET FLUME FLOW | l/s | WASTE |  | WASTE:E9366
13204 | #N/A | #N/A | #N/A | E38636 | 132040FILTER LOW LIFT FLOW ANG | l/s | WASTE |  | WASTE:E38636
13204 | #N/A | #N/A | #N/A | E38637 | 132040INLET FLOW ANG | l/s | WASTE |  | WASTE:E38637
13204 | #N/A | #N/A | #N/A | E38639 | 132040RECIRC FLOW ANG | l/s | WASTE |  | WASTE:E38639
13204 | #N/A | #N/A | #N/A | E38650 | 132040MCERT FLOW OUT ANG | l/s | WASTE |  | WASTE:E38650
13205 | #N/A | #N/A | #N/A | E4161 | 132050FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E4161
13205 | #N/A | #N/A | #N/A | E4164 | 132050EA366MCERTS FPF FLOW METER | l/s | WASTE |  | WASTE:E4164
13207 | #N/A | #N/A | #N/A | E9430 | 132070EA173OUTLET FLOW | l/s | WASTE |  | WASTE:E9430
13207 | #N/A | #N/A | #N/A | E36151 | 132070FLOW TO TREATMENT ANG | l/s | WASTE |  | WASTE:E36151
13207 | #N/A | #N/A | #N/A | E36153 | 132070SAMPLE OVERFLOW CHAMBER ANG | l/s | WASTE |  | WASTE:E36153
13208 | #N/A | #N/A | #N/A | E2045 | 132080INLET FLOW | l/s | WASTE |  | WASTE:E2045
13208 | #N/A | #N/A | #N/A | E2046 | 132080EA174INLET FLOW | l/s | WASTE |  | WASTE:E2046
13208 | #N/A | #N/A | #N/A | E21847 | 132080FULL FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E21847
13208 | #N/A | #N/A | #N/A | E21832 | 132080SNDFILTR INLT FLW LVL | l/s | WASTE |  | WASTE:E21832
13208 | #N/A | #N/A | #N/A | E21834 | 132080SNDFILTR BLWR OUTLT FLW | l/s | WASTE |  | WASTE:E21834
13209 | #N/A | #N/A | #N/A | E1081 | 132090EA066INLET FLOW | l/s | WASTE |  | WASTE:E1081
13211 | #N/A | #N/A | #N/A | E2465 | 132110FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E2465
13211 | #N/A | #N/A | #N/A | E2466 | 132110EA067MCERT INLET FLOW | l/s | WASTE |  | WASTE:E2466
13212 | #N/A | #N/A | #N/A | E56579 | 13212AEA068 FPF MCERTS FLOW METER ANALOGUE INPUT | l/s | WASTE |  | WASTE:E56579
13214 | #N/A | #N/A | #N/A | E4706 | 132140INLET FLOW 1 | l/s | WASTE |  | WASTE:E4706
13214 | #N/A | #N/A | #N/A | E4708 | 132140EA175FINAL EFF FLOW | l/s | WASTE |  | WASTE:E4708
13215 | #N/A | #N/A | #N/A | E8892 | 132151FLOW TO OUTFALL PS | l/s | WASTE |  | WASTE:E8892
13215 | #N/A | #N/A | #N/A | E8899 | 132151HWRKS FLOW FROM MART RD | l/s | WASTE |  | WASTE:E8899
13215 | #N/A | #N/A | #N/A | E8900 | 132151HWRKS FLOW TO VILLAGS PS | l/s | WASTE |  | WASTE:E8900
13215 | #N/A | #N/A | #N/A | E8901 | 132151HWRKS FLOW FR VILLAGS PS | l/s | WASTE |  | WASTE:E8901
13215 | #N/A | #N/A | #N/A | E8902 | 132151HWRKS FLOW TO OUTFALL | l/s | WASTE |  | WASTE:E8902
13215 | #N/A | #N/A | #N/A | E8938 | 132151EA237PPS OUTFLOW ANLG | l/s | WASTE |  | WASTE:E8938
13215 | #N/A | #N/A | #N/A | E8943 | 132151SLUDGE FLOW TO CENTRIFUGE 2 | l/s | WASTE |  | WASTE:E8943
13215 | #N/A | #N/A | #N/A | E8944 | 132151INLET FLOW | l/s | WASTE |  | WASTE:E8944
13215 | #N/A | #N/A | #N/A | E8950 | 132151LIME DOSING FLOW RATE | l/s | WASTE |  | WASTE:E8950
13215 | #N/A | #N/A | #N/A | E8951 | 132151CENTRIFUGE 1 FLOW RATE | l/s | WASTE |  | WASTE:E8951
13215 | #N/A | #N/A | #N/A | E8952 | 132151CENTRIFUGE 2 POLY FLOW RATE | l/s | WASTE |  | WASTE:E8952
13215 | #N/A | #N/A | #N/A | E8966 | 132151SLG FLOW TO PRIM TREAT | l/s | WASTE |  | WASTE:E8966
13215 | #N/A | #N/A | #N/A | E8978 | 132151UV FLOW THROUGH UV | l/s | WASTE |  | WASTE:E8978
13215 | #N/A | #N/A | #N/A | E53793 | 132151INDIGENOUS SLUDGE FLOW ANG | l/s | WASTE |  | WASTE:E53793
13215 | #N/A | #N/A | #N/A | E53795 | 132151RTN LIQUORS CENTRATE FLOW ANG | l/s | WASTE |  | WASTE:E53795
13215 | #N/A | #N/A | #N/A | E54232 | 13215AINDIGENOUS SLUDGE FLOW AI | l/s | WASTE |  | WASTE:E54232
13215 | #N/A | #N/A | #N/A | E54234 | 13215ARETURN LIQ CENTRATE FLOW AI | l/s | WASTE |  | WASTE:E54234
13215 | #N/A | #N/A | #N/A | E96502 | 132151UV INLET FLOW AI | l/s | WASTE |  | WASTE:E96502
13215 | #N/A | #N/A | #N/A | E8916 | 132151HWCTRL SUMMED INLET FLWS | l/s | WASTE |  | WASTE:E8916
13219 | #N/A | #N/A | #N/A | E4741 | 132190FLOW TO WORKS | l/s | WASTE |  | WASTE:E4741
13219 | #N/A | #N/A | #N/A | E20570 | 132190ATSF INFLUENT FLOW AN | l/s | WASTE |  | WASTE:E20570
13220 | #N/A | #N/A | #N/A | E19526 | 132201EA070FLOW TO WORKS | l/s | WASTE |  | WASTE:E19526
13220 | #N/A | #N/A | #N/A | E19993 | 132201INLET FLOW 1 | l/s | WASTE |  | WASTE:E19993
13220 | #N/A | #N/A | #N/A | E50015 | 132201INCOMING RISING MAIN FLOW | l/s | WASTE |  | WASTE:E50015
13221 | #N/A | #N/A | #N/A | E3394 | 132210INLET FLOW | l/s | WASTE |  | WASTE:E3394
13222 | #N/A | #N/A | #N/A | E1100 | 132220EA176FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E1100
13222 | #N/A | #N/A | #N/A | E96782 | 13222APROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E96782
13222 | #N/A | #N/A | #N/A | E96787 | 13222APUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E96787
13223 | #N/A | #N/A | #N/A | E13192 | 132232EA072OUTLET FLOW | l/s | WASTE |  | WASTE:E13192
13223 | #N/A | #N/A | #N/A | E13193 | 132232FLOW TO WORKS | l/s | WASTE |  | WASTE:E13193
13226 | #N/A | #N/A | #N/A | E12326 | 132261EA073INLET FLOW | l/s | WASTE |  | WASTE:E12326
13226 | #N/A | #N/A | #N/A | E28428 | 13226ASAND FILTER FLOW 1 AN | l/s | WASTE |  | WASTE:E28428
13226 | #N/A | #N/A | #N/A | E28429 | 13226ASAND FILTER FLOW 2 AN | l/s | WASTE |  | WASTE:E28429
13227 | #N/A | #N/A | #N/A | E4171 | 132270EA074INLET FLOW | l/s | WASTE |  | WASTE:E4171
13229 | #N/A | #N/A | #N/A | E4186 | 132290EA367 FPF FLOW METER ANALOGUE INPUT MCERTS | l/s | WASTE |  | WASTE:E4186
13229 | #N/A | #N/A | #N/A | E4187 | 132290EA177FINAL EFF FLOW | l/s | WASTE |  | WASTE:E4187
13230 | #N/A | #N/A | #N/A | E14235 | 132301EA075PUMP FLW TO TREATMENT | l/s | WASTE |  | WASTE:E14235
13231 | #N/A | #N/A | #N/A | E2065 | 132310EA255FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E2065
13232 | #N/A | #N/A | #N/A | E7338 | 132320A31 TRICKETT CROSS RISING MAIN FLOW AL | l/s | WASTE |  | WASTE:E7338
13232 | #N/A | #N/A | #N/A | E9231 | 132320DUGDELL CLOSE RISING MAIN FLOW | l/s | WASTE |  | WASTE:E9231
13232 | #N/A | #N/A | #N/A | E9855 | 132320ASP FLOW | l/s | WASTE |  | WASTE:E9855
13232 | #N/A | #N/A | #N/A | E9856 | 132320FILTER FLOW | l/s | WASTE |  | WASTE:E9856
13232 | #N/A | #N/A | #N/A | E9857 | 132320ASP2 FLOW | l/s | WASTE |  | WASTE:E9857
13232 | #N/A | #N/A | #N/A | E9858 | 132320UNOX TO STORM FLOW | l/s | WASTE |  | WASTE:E9858
13232 | #N/A | #N/A | #N/A | E9859 | 132320EA238FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E9859
13232 | #N/A | #N/A | #N/A | E9877 | 132320RAS FLOW | l/s | WASTE |  | WASTE:E9877
13232 | #N/A | #N/A | #N/A | E9878 | 132320SAS FLOW | l/s | WASTE |  | WASTE:E9878
13232 | #N/A | #N/A | #N/A | E9880 | 132320ECO FLOW | l/s | WASTE |  | WASTE:E9880
13232 | #N/A | #N/A | #N/A | E14396 | 132320SLUDGE TRANSFER FLOW | l/s | WASTE |  | WASTE:E14396
13232 | #N/A | #N/A | #N/A | E18846 | 132320ASP 2 INLET FLOW AN | l/s | WASTE |  | WASTE:E18846
13232 | #N/A | #N/A | #N/A | E18847 | 132320ASP 2 RAS FLOW AN | l/s | WASTE |  | WASTE:E18847
13232 | #N/A | #N/A | #N/A | E18853 | 132320UV PUMPED FLOW | l/s | WASTE |  | WASTE:E18853
13232 | #N/A | #N/A | #N/A | E18854 | 132320UV FLOW | l/s | WASTE |  | WASTE:E18854
13235 | #N/A | #N/A | #N/A | E1715 | 132350INLET FLOW | l/s | WASTE |  | WASTE:E1715
13235 | #N/A | #N/A | #N/A | E1716 | 132350INCOMNG RISING MAIN FLOW | l/s | WASTE |  | WASTE:E1716
13235 | #N/A | #N/A | #N/A | E1717 | 132350EA076INLET FLOW | l/s | WASTE |  | WASTE:E1717
13235 | #N/A | #N/A | #N/A | E1724 | 132350INLET WORKS FLOWMETER | l/s | WASTE |  | WASTE:E1724
13235 | #N/A | #N/A | #N/A | E38720 | 132350PUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E38720
13235 | #N/A | #N/A | #N/A | E38731 | 132350PUMP SET 1 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E38731
13235 | #N/A | #N/A | #N/A | E96482 | 13235ABURST DETECTION FLOW AI | l/s | WASTE |  | WASTE:E96482
13237 | #N/A | #N/A | #N/A | E12732 | 132370PEWSEY JUBILEE SPS RISING MAIN FLOW | l/s | WASTE |  | WASTE:E12732
13237 | #N/A | #N/A | #N/A | E12733 | 132370MANNINGFORD NO4 PEWSEY SPS RISING MAIN FLOW | l/s | WASTE |  | WASTE:E12733
13237 | #N/A | #N/A | #N/A | E12739 | 132370FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E12739
13237 | #N/A | #N/A | #N/A | E12742 | 132370DOSING SET 2 - TASF FLOW | l/s | WASTE |  | WASTE:E12742
13237 | #N/A | #N/A | #N/A | E30472 | 13237AINLET FLOW ANG | l/s | WASTE |  | WASTE:E30472
13237 | #N/A | #N/A | #N/A | E30930 | 13237BFILTER 1 INLET FLOW | l/s | WASTE |  | WASTE:E30930
13237 | #N/A | #N/A | #N/A | E30932 | 13237BFILTER 2 INLET FLOW | l/s | WASTE |  | WASTE:E30932
13237 | #N/A | #N/A | #N/A | E30934 | 13237BFILTER 3 INLET FLOW | l/s | WASTE |  | WASTE:E30934
13237 | #N/A | #N/A | #N/A | E30936 | 13237BFILTER 4 INLET FLOW | l/s | WASTE |  | WASTE:E30936
13237 | #N/A | #N/A | #N/A | E30942 | 13237BEA077MCERTS FLOW | l/s | WASTE |  | WASTE:E30942
13237 | #N/A | #N/A | #N/A | E30946 | 13237BWORKS RTN FLOW | l/s | WASTE |  | WASTE:E30946
13237 | #N/A | #N/A | #N/A | E31079 | 13237CSLUDGE TRANSFER FLOWMETER | l/s | WASTE |  | WASTE:E31079
13238 | #N/A | #N/A | #N/A | E17202 | 132381EA078FINAL FLOW | l/s | WASTE |  | WASTE:E17202
13239 | #N/A | #N/A | #N/A | E5646 | 132390EA239FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E5646
13239 | #N/A | #N/A | #N/A | E55707 | 132390PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E55707
13239 | #N/A | #N/A | #N/A | E55715 | 132390PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E55715
13242 | #N/A | #N/A | #N/A | E5199 | 132421CREEKMOOR FLOW | l/s | WASTE |  | WASTE:E5199
13242 | #N/A | #N/A | #N/A | E5200 | 132421EAST QUAY FLOW | l/s | WASTE |  | WASTE:E5200
13242 | #N/A | #N/A | #N/A | E5202 | 132421FLOW TO STORM STORAGE PSTS | l/s | WASTE |  | WASTE:E5202
13242 | #N/A | #N/A | #N/A | E5276 | 132420STORM TANK 3 DRAIN FLOW | l/s | WASTE |  | WASTE:E5276
13242 | #N/A | #N/A | #N/A | E5277 | 132420STORM TANK 4 DRAIN FLOW | l/s | WASTE |  | WASTE:E5277
13242 | #N/A | #N/A | #N/A | E9993 | 132420COMBINED INFLOW | l/s | WASTE |  | WASTE:E9993
13242 | #N/A | #N/A | #N/A | E14527 | 132420 FINAL OUTFLOW | l/s | WASTE |  | WASTE:E14527
13242 | #N/A | #N/A | #N/A | E28597 | 132420EAST MAGFLO FLOW | l/s | WASTE |  | WASTE:E28597
13242 | #N/A | #N/A | #N/A | E28598 | 132420WEST MAGFLO FLOW | l/s | WASTE |  | WASTE:E28598
13242 | #N/A | #N/A | #N/A | E28599 | 1324203 BELT DE-WATERER NO.1 INFLOW | l/s | WASTE |  | WASTE:E28599
13242 | #N/A | #N/A | #N/A | E28602 | 1324203BELT DE-WATERER NO.2 INFLOW | l/s | WASTE |  | WASTE:E28602
13242 | #N/A | #N/A | #N/A | E28701 | 13242DRAW SEWAGE STORM TANK 1 FLOW AN | l/s | WASTE |  | WASTE:E28701
13242 | #N/A | #N/A | #N/A | E28702 | 13242DRAW SEWAGE STORM TANK 2 FLOW AN | l/s | WASTE |  | WASTE:E28702
13242 | #N/A | #N/A | #N/A | E28703 | 13242DRAW SEWAGE INLET FLOW AN | l/s | WASTE |  | WASTE:E28703
13242 | #N/A | #N/A | #N/A | E28825 | 132420SLUDGE FLOW TO THICKENERS AI | l/s | WASTE |  | WASTE:E28825
13242 | #N/A | #N/A | #N/A | E28832 | 132420POLYMER DOSING FLOW 1 | l/s | WASTE |  | WASTE:E28832
13242 | #N/A | #N/A | #N/A | E28833 | 132420POLYMER DOSING FLOW 2 | l/s | WASTE |  | WASTE:E28833
13242 | #N/A | #N/A | #N/A | E29943 | 13242ASBR FEED BAL TANK INFLOW | l/s | WASTE |  | WASTE:E29943
13242 | #N/A | #N/A | #N/A | E29948 | 13242ASBR SAS PUMP FLOW ACTUAL | l/s | WASTE |  | WASTE:E29948
13242 | #N/A | #N/A | #N/A | E29949 | 13242ASBR TANK INFLOW CURR | l/s | WASTE |  | WASTE:E29949
13242 | #N/A | #N/A | #N/A | E29953 | 13242ASBR DISCHG BAL TANK FLOW | l/s | WASTE |  | WASTE:E29953
13242 | #N/A | #N/A | #N/A | E30021 | 132420FINAL OUTFLOW | l/s | WASTE |  | WASTE:E30021
13242 | #N/A | #N/A | #N/A | E30025 | 13242BTSF SAND FILTER LIQUOR FLOW | l/s | WASTE |  | WASTE:E30025
13242 | #N/A | #N/A | #N/A | E30035 | 13242BTSF SBR BALANCE TANK FEED FLOW | l/s | WASTE |  | WASTE:E30035
13242 | #N/A | #N/A | #N/A | E30037 | 13242BBAF PLANT DISCHARGE FLOW | l/s | WASTE |  | WASTE:E30037
13242 | #N/A | #N/A | #N/A | E30086 | 132421BAF TRANSFER FLOW | l/s | WASTE |  | WASTE:E30086
13242 | #N/A | #N/A | #N/A | E32754 | 132421FLOW TO TREATMENT MEASURED | l/s | WASTE |  | WASTE:E32754
13242 | #N/A | #N/A | #N/A | E32755 | 132421FLOW TO BAF 1 AND 2 | l/s | WASTE |  | WASTE:E32755
13242 | #N/A | #N/A | #N/A | E32756 | 132421FLOW TO EASTERN WORKS | l/s | WASTE |  | WASTE:E32756
13242 | #N/A | #N/A | #N/A | E32757 | 132421FLOW TO WESTERN WORKS | l/s | WASTE |  | WASTE:E32757
13242 | #N/A | #N/A | #N/A | E32758 | 132421FLOW TO STORM TANKS | l/s | WASTE |  | WASTE:E32758
13242 | #N/A | #N/A | #N/A | E32760 | 132421FLOW TO TREATMENT TARGET SP | l/s | WASTE |  | WASTE:E32760
13242 | #N/A | #N/A | #N/A | E32784 | 132421BIOFOR CHANNEL OVERFLOW | l/s | WASTE |  | WASTE:E32784
13242 | #N/A | #N/A | #N/A | E32785 | 132421BAF OVERFLOW | l/s | WASTE |  | WASTE:E32785
13242 | #N/A | #N/A | #N/A | E39992 | 132421STERET RD FW SPS RISING MAIN FLOW | l/s | WASTE |  | WASTE:E39992
13242 | #N/A | #N/A | #N/A | E54065 | 13242YDEAMON CENTRATE RTN LIQ FLOW CONVERT | l/s | WASTE |  | WASTE:E54065
13242 | #N/A | #N/A | #N/A | E54066 | 13242YRTRN LIQUORS FLITRAT FLOW CONVERT | l/s | WASTE |  | WASTE:E54066
13242 | #N/A | #N/A | #N/A | E56426 | 132421RAW SEWAGE PS 2 RISING MAIN FLOW ANG | l/s | WASTE |  | WASTE:E56426
13242 | #N/A | #N/A | #N/A | E57984 | 13242YPOST DRUM FLOWMETER | l/s | WASTE |  | WASTE:E57984
13243 | #N/A | #N/A | #N/A | E11489 | 132430EA373 FPF - TDV WASHWATER MCERT FLOW | l/s | WASTE |  | WASTE:E11489
13243 | #N/A | #N/A | #N/A | E11507 | 132430EA241 FPF - TDV FLOW METER ANG INPUT MCERT | l/s | WASTE |  | WASTE:E11507
13243 | #N/A | #N/A | #N/A | E11526 | 132430INTERMEDIATE FLOW METER | l/s | WASTE |  | WASTE:E11526
13243 | #N/A | #N/A | #N/A | E13249 | 132430RAS FLOW | l/s | WASTE |  | WASTE:E13249
13243 | #N/A | #N/A | #N/A | E13250 | 132430SAS FLOW | l/s | WASTE |  | WASTE:E13250
13244 | #N/A | #N/A | #N/A | E1286 | 132440EA079INLET FLOW PLC ANLG | l/s | WASTE |  | WASTE:E1286
13244 | #N/A | #N/A | #N/A | E1287 | 132440RAS FLOW PLC ANLG | l/s | WASTE |  | WASTE:E1287
13244 | #N/A | #N/A | #N/A | E8398 | 132440INLET FLOW 1 | l/s | WASTE |  | WASTE:E8398
13248 | #N/A | #N/A | #N/A | E1530 | 132480EA179OUTLET FLOW | l/s | WASTE |  | WASTE:E1530
13248 | #N/A | #N/A | #N/A | E1532 | 132480INLET FLOW | l/s | WASTE |  | WASTE:E1532
13248 | #N/A | #N/A | #N/A | E1535 | 132480MCERT EA377 FPF - TDV FLOW METER ANG INPUT MCERT | l/s | WASTE |  | WASTE:E1535
13249 | #N/A | #N/A | #N/A | E17633 | 132491EA080MCERT FLOWMETER AN | l/s | WASTE |  | WASTE:E17633
13249 | #N/A | #N/A | #N/A | E35554 | 132491FLOW TO TREATMENT AN | l/s | WASTE |  | WASTE:E35554
13249 | #N/A | #N/A | #N/A | E35556 | 132491STORM OVERFLOW AN | l/s | WASTE |  | WASTE:E35556
13250 | #N/A | #N/A | #N/A | E56197 | 13250AEA261 FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E56197
13250 | #N/A | #N/A | #N/A | E56225 | 13250BPROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E56225
13250 | #N/A | #N/A | #N/A | E56230 | 13250BPUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E56230
13252 | #N/A | #N/A | #N/A | E1726 | 132520RECIRC FLOWMETER | l/s | WASTE |  | WASTE:E1726
13252 | #N/A | #N/A | #N/A | E1740 | 132520INLET FLOW 1 | l/s | WASTE |  | WASTE:E1740
13252 | #N/A | #N/A | #N/A | E1745 | 132520INLET FLOW | l/s | WASTE |  | WASTE:E1745
13253 | #N/A | #N/A | #N/A | E5132 | 132530FLOW 1 | l/s | WASTE |  | WASTE:E5132
13253 | #N/A | #N/A | #N/A | E5133 | 132530FLOW 2 | l/s | WASTE |  | WASTE:E5133
13253 | #N/A | #N/A | #N/A | E5139 | 13253BINLET FLOWMETER | l/s | WASTE |  | WASTE:E5139
13253 | #N/A | #N/A | #N/A | E5140 | 13253BMCERT FLOWMETER | l/s | WASTE |  | WASTE:E5140
13253 | #N/A | #N/A | #N/A | E9203 | 132530DURRINGTON FLOW AVE | l/s | WASTE |  | WASTE:E9203
13253 | #N/A | #N/A | #N/A | E9204 | 132530AMESBURY FLOW AVE | l/s | WASTE |  | WASTE:E9204
13253 | #N/A | #N/A | #N/A | E9205 | 132530BULFORD FLOW AVE | l/s | WASTE |  | WASTE:E9205
13253 | #N/A | #N/A | #N/A | E9437 | 132530EA082FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E9437
13253 | #N/A | #N/A | #N/A | E9439 | 132530DURRINGTON FLOW | l/s | WASTE |  | WASTE:E9439
13253 | #N/A | #N/A | #N/A | E9440 | 132530AMESBURY FLOW | l/s | WASTE |  | WASTE:E9440
13253 | #N/A | #N/A | #N/A | E9441 | 132530BULFORD FLOW | l/s | WASTE |  | WASTE:E9441
13253 | #N/A | #N/A | #N/A | E30243 | 13253ATASF 1 FLOW | l/s | WASTE |  | WASTE:E30243
13253 | #N/A | #N/A | #N/A | E30244 | 13253ATASF 2 FLOW | l/s | WASTE |  | WASTE:E30244
13253 | #N/A | #N/A | #N/A | E30245 | 13253ATASF 3 FLOW | l/s | WASTE |  | WASTE:E30245
13253 | #N/A | #N/A | #N/A | E30246 | 13253ATASF 4 FLOW | l/s | WASTE |  | WASTE:E30246
13253 | #N/A | #N/A | #N/A | E30247 | 13253ATASF 5 FLOW | l/s | WASTE |  | WASTE:E30247
13253 | #N/A | #N/A | #N/A | E30248 | 13253ATASF 6 FLOW | l/s | WASTE |  | WASTE:E30248
13253 | #N/A | #N/A | #N/A | E30249 | 13253ATASF 7 FLOW | l/s | WASTE |  | WASTE:E30249
13253 | #N/A | #N/A | #N/A | E30250 | 13253ATASF 8 FLOW | l/s | WASTE |  | WASTE:E30250
13253 | #N/A | #N/A | #N/A | E30863 | 13253CEXISTING SLDG FLOW | l/s | WASTE |  | WASTE:E30863
13254 | #N/A | #N/A | #N/A | E1121 | 132540EA180INLET FLOW | l/s | WASTE |  | WASTE:E1121
13254 | #N/A | #N/A | #N/A | E1123 | 132540SEVERN BEACH INCOMING RISING MAIN FLOW | l/s | WASTE |  | WASTE:E1123
13255 | #N/A | #N/A | #N/A | E8090 | 132550INLET FLOW 1 | l/s | WASTE |  | WASTE:E8090
13255 | #N/A | #N/A | #N/A | E9333 | 132550BICKERLEY SPS RISING MAIN FLOW AL | l/s | WASTE |  | WASTE:E9333
13255 | #N/A | #N/A | #N/A | E9334 | 132550MOORTOWN SPS RISING MAIN FLOW AL | l/s | WASTE |  | WASTE:E9334
13255 | #N/A | #N/A | #N/A | E9342 | 132550FLOW TO TREATMENT 2 | l/s | WASTE |  | WASTE:E9342
13255 | #N/A | #N/A | #N/A | E9343 | 132550FLOW TO TREATMENT 1 | l/s | WASTE |  | WASTE:E9343
13255 | #N/A | #N/A | #N/A | E9346 | 132550EA243MCERT FLOW | l/s | WASTE |  | WASTE:E9346
13255 | #N/A | #N/A | #N/A | E9355 | 132550ESDAILE LANE DISCHARGE FLOW | l/s | WASTE |  | WASTE:E9355
13255 | #N/A | #N/A | #N/A | E31633 | 132550PLC FLOW TO TREATMENT 1 | l/s | WASTE |  | WASTE:E31633
13255 | #N/A | #N/A | #N/A | E31634 | 132550PLC FLOW TO TREATMENT 2 | l/s | WASTE |  | WASTE:E31634
13255 | #N/A | #N/A | #N/A | E31744 | 132550PUMPSET 2 FLOW | l/s | WASTE |  | WASTE:E31744
13255 | #N/A | #N/A | #N/A | E31745 | 132550PUMPSET 3 FLOW | l/s | WASTE |  | WASTE:E31745
13255 | #N/A | #N/A | #N/A | E51811 | 132550MCERT INLET FLOW | l/s | WASTE |  | WASTE:E51811
13256 | #N/A | #N/A | #N/A | E6812 | 13256AEA084INLET PS FLOW AI | l/s | WASTE2 |  | WASTE2:E6812
13256 | #N/A | #N/A | #N/A | E6821 | 13256ARECIRC PS FLOW AI | l/s | WASTE2 |  | WASTE2:E6821
13256 | #N/A | #N/A | #N/A | E6846 | 13256BPROFILE STORM DOSING START FLOW | l/s | WASTE2 |  | WASTE2:E6846
13256 | #N/A | #N/A | #N/A | E6851 | 13256BPUMP SET 1 SEWAGE FLOW AI | l/s | WASTE2 |  | WASTE2:E6851
13257 | #N/A | #N/A | #N/A | E12947 | 132570EA181INLET FLOW | l/s | WASTE |  | WASTE:E12947
13257 | #N/A | #N/A | #N/A | E7025 | 13257CFFT FLOWMETER ANG | l/s | WASTE2 |  | WASTE2:E7025
13257 | #N/A | #N/A | #N/A | E7026 | 13257CFILTER CLEAR FEED FLOWMETER ANG | l/s | WASTE2 |  | WASTE2:E7026
13257 | #N/A | #N/A | #N/A | E7036 | 13257CDIRTY BACKWASH TRANSFER FLOWMETER ANG | l/s | WASTE2 |  | WASTE2:E7036
13257 | #N/A | #N/A | #N/A | E7074 | 13257APROFILE STORM DOSING START FLOW | l/s | WASTE2 |  | WASTE2:E7074
13257 | #N/A | #N/A | #N/A | E7079 | 13257APUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE2 |  | WASTE2:E7079
13257 | #N/A | #N/A | #N/A | E7084 | 13257APUMP SET 2 SEWAGE FLOW ANG | l/s | WASTE2 |  | WASTE2:E7084
13258 | #N/A | #N/A | #N/A | E8326 | 13258ADOSE SET 2 INLET FLOW | l/s | WASTE |  | WASTE:E8326
13258 | #N/A | #N/A | #N/A | E8328 | 13258ADOSE SET 3 INLET FLOW | l/s | WASTE |  | WASTE:E8328
13258 | #N/A | #N/A | #N/A | E9938 | 132580TREATMENT FLOW | l/s | WASTE |  | WASTE:E9938
13258 | #N/A | #N/A | #N/A | E9939 | 132580FLOW TO RIVER ANALOGUE | l/s | WASTE |  | WASTE:E9939
13258 | #N/A | #N/A | #N/A | E9940 | 132580EA085FINAL FLOW | l/s | WASTE |  | WASTE:E9940
13258 | #N/A | #N/A | #N/A | E32004 | 132580RECIRC FLOW AI | l/s | WASTE |  | WASTE:E32004
13258 | #N/A | #N/A | #N/A | E32006 | 132580RISING MAIN FLOW | l/s | WASTE |  | WASTE:E32006
13258 | #N/A | #N/A | #N/A | E32040 | 132580SEC INLET FLOW FOR DOSE SET 2 | l/s | WASTE |  | WASTE:E32040
13258 | #N/A | #N/A | #N/A | E32041 | 132580SEC INLET FLOW FOR DOSE SET 3 | l/s | WASTE |  | WASTE:E32041
13258 | #N/A | #N/A | #N/A | E13331 | 132580STORM TNK FLW TO RVR AN | l/s | WASTE |  | WASTE:E13331
13260 | #N/A | #N/A | #N/A | E4826 | 132600FLUME CHAMBER FLOW | l/s | WASTE |  | WASTE:E4826
13260 | #N/A | #N/A | #N/A | E4827 | 132600EA182OUTFLOW | l/s | WASTE |  | WASTE:E4827
13262 | #N/A | #N/A | #N/A | E1301 | 132620EA087FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E1301
13262 | #N/A | #N/A | #N/A | E54003 | 132620PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E54003
13262 | #N/A | #N/A | #N/A | E54004 | 132620PUMP SET 1 CHEMICAL FLOW AI | l/s | WASTE |  | WASTE:E54004
13262 | #N/A | #N/A | #N/A | E54008 | 132620PUMP SET 2 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E54008
13262 | #N/A | #N/A | #N/A | E54016 | 132620PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E54016
13264 | #N/A | #N/A | #N/A | E9500 | 132640EA244MCERT INLET FLOWMETER ANLG | l/s | WASTE |  | WASTE:E9500
13264 | #N/A | #N/A | #N/A | E24171 | 132640INLET FLOW TRANSMITTER AN | l/s | WASTE |  | WASTE:E24171
13264 | #N/A | #N/A | #N/A | E24202 | 132640ASP SAS FLOW AN | l/s | WASTE |  | WASTE:E24202
13264 | #N/A | #N/A | #N/A | E24203 | 132640ASP RAS FLOW AN | l/s | WASTE |  | WASTE:E24203
13264 | #N/A | #N/A | #N/A | E24208 | 132640FLOW TO DITCH | l/s | WASTE |  | WASTE:E24208
13264 | #N/A | #N/A | #N/A | E24213 | 132640RAS FLOW TODAY AN | l/s | WASTE |  | WASTE:E24213
13264 | #N/A | #N/A | #N/A | E24214 | 132640RAS FLOW YESTERDAY AN | l/s | WASTE |  | WASTE:E24214
13264 | #N/A | #N/A | #N/A | E24215 | 132640SAS FLOW TODAY AN | l/s | WASTE |  | WASTE:E24215
13264 | #N/A | #N/A | #N/A | E24216 | 132640SAS FLOW YESTERDAY AN | l/s | WASTE |  | WASTE:E24216
13264 | #N/A | #N/A | #N/A | E24218 | 132640TARGET RAS FLOW SET POINT | l/s | WASTE |  | WASTE:E24218
13264 | #N/A | #N/A | #N/A | E24219 | 132640DITCH RAS FLOW | l/s | WASTE |  | WASTE:E24219
13264 | #N/A | #N/A | #N/A | E30321 | 132640POLY FLOW ANG | l/s | WASTE |  | WASTE:E30321
13264 | #N/A | #N/A | #N/A | E24195 | 132640SETT SEWAGE TO ASP FLW AN | l/s | WASTE |  | WASTE:E24195
13266 | #N/A | #N/A | #N/A | E12019 | 132660EA183FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E12019
13266 | #N/A | #N/A | #N/A | E31056 | 132660FLOW TO FULL TREATMENT AI | l/s | WASTE |  | WASTE:E31056
13266 | #N/A | #N/A | #N/A | E31070 | 132660THICKENED SLUDGE FLOW AI | l/s | WASTE |  | WASTE:E31070
13267 | #N/A | #N/A | #N/A | E5381 | 132670FLOW TO WORKS | l/s | WASTE |  | WASTE:E5381
13267 | #N/A | #N/A | #N/A | E5382 | 132670EA088FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E5382
13267 | #N/A | #N/A | #N/A | E5386 | 132670LOAD BALANCE FLOW | l/s | WASTE |  | WASTE:E5386
13267 | #N/A | #N/A | #N/A | E13899 | 132670BAFF INFLOW | l/s | WASTE |  | WASTE:E13899
13267 | #N/A | #N/A | #N/A | E35447 | 132670TSF FEED FLOW METER ANG | l/s | WASTE |  | WASTE:E35447
13267 | #N/A | #N/A | #N/A | E35451 | 132670INLET FLOWMETER ANG | l/s | WASTE |  | WASTE:E35451
13267 | #N/A | #N/A | #N/A | E35454 | 132670BIOFILTR VESSEL 1 IRRATN FLOW ANG | l/s | WASTE |  | WASTE:E35454
13267 | #N/A | #N/A | #N/A | E35455 | 132670BIOFILTR VESSEL 2 IRRGTN FLOW ANG | l/s | WASTE |  | WASTE:E35455
13267 | #N/A | #N/A | #N/A | E35874 | 132670PUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E35874
13267 | #N/A | #N/A | #N/A | E35881 | 132670PUMP SET 2 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E35881
13267 | #N/A | #N/A | #N/A | E36061 | 132670PUMP SET 1 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E36061
13267 | #N/A | #N/A | #N/A | E36069 | 132670PUMP SET 2 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E36069
13267 | #N/A | #N/A | #N/A | E97957 | 132670PST COMMON DESLUDGE FLOW METER AI | l/s | WASTE |  | WASTE:E97957
13267 | #N/A | #N/A | #N/A | E35887 | 132670RECIRC FLW | l/s | WASTE |  | WASTE:E35887
13268 | #N/A | #N/A | #N/A | E2510 | 132680HRF RECIRC FLOW | l/s | WASTE |  | WASTE:E2510
13268 | #N/A | #N/A | #N/A | E2511 | 132680WORKS RETURN FLOW | l/s | WASTE |  | WASTE:E2511
13268 | #N/A | #N/A | #N/A | E2512 | 132680INLET FLOW | l/s | WASTE |  | WASTE:E2512
13268 | #N/A | #N/A | #N/A | E2516 | 132680FLOW TO STONE FILTERS | l/s | WASTE |  | WASTE:E2516
13268 | #N/A | #N/A | #N/A | E2527 | 132680OUTFALL FLOW ANLG | l/s | WASTE |  | WASTE:E2527
13268 | #N/A | #N/A | #N/A | E37759 | 132680PUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E37759
13268 | #N/A | #N/A | #N/A | E37766 | 132680PUMP SET 2 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E37766
13268 | #N/A | #N/A | #N/A | E37808 | 132680PUMP SET 1 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E37808
13268 | #N/A | #N/A | #N/A | E37817 | 132680PUMP SET 2 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E37817
13268 | #N/A | #N/A | #N/A | E53813 | 132680CRUDE PUMPED FLOWMETER 1 AI | l/s | WASTE |  | WASTE:E53813
13268 | #N/A | #N/A | #N/A | E53814 | 132680CRUDE PUMPED FLOWMETER 2 AI | l/s | WASTE |  | WASTE:E53814
13268 | #N/A | #N/A | #N/A | E53815 | 132680COMBINED CRUDE PUMPED FLOW AI | l/s | WASTE |  | WASTE:E53815
13268 | #N/A | #N/A | #N/A | E53818 | 132680RECIRCULATION FLOW AI | l/s | WASTE |  | WASTE:E53818
13268 | #N/A | #N/A | #N/A | E56475 | 132680MMF FEED FLOW ANG | l/s | WASTE |  | WASTE:E56475
13268 | #N/A | #N/A | #N/A | E56486 | 132680EA268FE MCERTS FLOWMETER ANG | l/s | WASTE |  | WASTE:E56486
13268 | #N/A | #N/A | #N/A | E56487 | 132680BACKWASH RETURN FLOW FLOWMETER ANG | l/s | WASTE |  | WASTE:E56487
13268 | #N/A | #N/A | #N/A | E56488 | 132680RECIRCULATION FLOWMETER ANG | l/s | WASTE |  | WASTE:E56488
13268 | #N/A | #N/A | #N/A | E56504 | 132680STORM TRANSFER PUMP 1 FLOW ANG | l/s | WASTE |  | WASTE:E56504
13268 | #N/A | #N/A | #N/A | E56505 | 132680STORM TRANSFER PUMP 2 FLOW ANG | l/s | WASTE |  | WASTE:E56505
13268 | #N/A | #N/A | #N/A | E56507 | 132680STORM 4 3 FLOWMETER ANG | l/s | WASTE |  | WASTE:E56507
13268 | #N/A | #N/A | #N/A | E7229 | 13268APUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE2 |  | WASTE2:E7229
13269 | #N/A | #N/A | #N/A | E3046 | 132690TREATMENT FLOW | l/s | WASTE |  | WASTE:E3046
13271 | #N/A | #N/A | #N/A | E18905 | 132711EA245INLET FLW MCERT | l/s | WASTE |  | WASTE:E18905
13274 | #N/A | #N/A | #N/A | E4226 | 132740EA186FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E4226
13275 | #N/A | #N/A | #N/A | E12072 | 132752SHREWTON SPS COMBINED LAMELLA OUTFALL FLOW | l/s | WASTE |  | WASTE:E12072
13275 | #N/A | #N/A | #N/A | E17864 | 132751INLET FLOW | l/s | WASTE |  | WASTE:E17864
13275 | #N/A | #N/A | #N/A | E31188 | 132752SAF 1 FLOW | l/s | WASTE |  | WASTE:E31188
13275 | #N/A | #N/A | #N/A | E31189 | 132752SAF 2 FLOW | l/s | WASTE |  | WASTE:E31189
13275 | #N/A | #N/A | #N/A | E31190 | 132752SAF 3 FLOW | l/s | WASTE |  | WASTE:E31190
13275 | #N/A | #N/A | #N/A | E31193 | 132752SHREWTON SPS STORM FLOW DISCHARGE | l/s | WASTE |  | WASTE:E31193
13275 | #N/A | #N/A | #N/A | E31206 | 132752PUMPED SLUDGE FLOW | l/s | WASTE |  | WASTE:E31206
13275 | #N/A | #N/A | #N/A | E31210 | 132752INLET FLOW | l/s | WASTE |  | WASTE:E31210
13276 | #N/A | #N/A | #N/A | E24060 | 132760EA188FINAL EFF FLOW | l/s | WASTE |  | WASTE:E24060
13278 | #N/A | #N/A | #N/A | E35378 | 132780MCERTS WASH WATER FLOW | l/s | WASTE |  | WASTE:E35378
13278 | #N/A | #N/A | #N/A | E35381 | 132780EA190INLET FLOW | l/s | WASTE |  | WASTE:E35381
13280 | #N/A | #N/A | #N/A | E3420 | 132800EA191FINAL EFF FLOW | l/s | WASTE |  | WASTE:E3420
13281 | #N/A | #N/A | #N/A | E2080 | 132810FLOW TO WORKS | l/s | WASTE |  | WASTE:E2080
13281 | #N/A | #N/A | #N/A | E2081 | 132810EA089FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E2081
13282 | #N/A | #N/A | #N/A | E2535 | 132820EA247OUTLET FLOW | l/s | WASTE |  | WASTE:E2535
13282 | #N/A | #N/A | #N/A | E2537 | 132820FILTER FEED FLOW | l/s | WASTE |  | WASTE:E2537
13282 | #N/A | #N/A | #N/A | E54786 | 132820PUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E54786
13282 | #N/A | #N/A | #N/A | E54795 | 132820PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E54795
13286 | #N/A | #N/A | #N/A | E29577 | 132860FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E29577
13286 | #N/A | #N/A | #N/A | E29579 | 132860EA356 FPF MCERTS FLOW METER ANALOGUE INPUT | l/s | WASTE |  | WASTE:E29579
13286 | #N/A | #N/A | #N/A | E29581 | 132860FILTER PUMP FLOW | l/s | WASTE |  | WASTE:E29581
13288 | #N/A | #N/A | #N/A | E13276 | 132881EA090WORKS INLET FLOW | l/s | WASTE |  | WASTE:E13276
13288 | #N/A | #N/A | #N/A | E29221 | 132881MAX INLET FLOW | l/s | WASTE |  | WASTE:E29221
13288 | #N/A | #N/A | #N/A | E29222 | 132881MIN INLET FLOW | l/s | WASTE |  | WASTE:E29222
13290 | #N/A | #N/A | #N/A | E4917 | 132900MCERT OUTFLOW | l/s | WASTE |  | WASTE:E4917
13290 | #N/A | #N/A | #N/A | E38139 | 132900EA091MCERT SCREENED INLET FLOW | l/s | WASTE |  | WASTE:E38139
13292 | #N/A | #N/A | #N/A | E18072 | 132921EA093FINAL EFF FLOW | l/s | WASTE |  | WASTE:E18072
13292 | #N/A | #N/A | #N/A | E18073 | 132921FFT FLOWMETER AI | l/s | WASTE |  | WASTE:E18073
13292 | #N/A | #N/A | #N/A | E55622 | 132921PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E55622
13292 | #N/A | #N/A | #N/A | E55630 | 132921PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E55630
13293 | #N/A | #N/A | #N/A | E4256 | 132930EA094TREATMENT FLOW | l/s | WASTE |  | WASTE:E4256
13295 | #N/A | #N/A | #N/A | E18137 | 132951EA194FINAL EFFLUENT OUTLET FLOW | l/s | WASTE |  | WASTE:E18137
13295 | #N/A | #N/A | #N/A | E18139 | 132951RISING MAIN FLOW ANG | l/s | WASTE |  | WASTE:E18139
13297 | #N/A | #N/A | #N/A | E11428 | 132971FINAL OUTLET FLOW AVE | l/s | WASTE |  | WASTE:E11428
13297 | #N/A | #N/A | #N/A | E52107 | 132972EA095INLET PS MCERT FLOW | l/s | WASTE |  | WASTE:E52107
13297 | #N/A | #N/A | #N/A | E52115 | 132972FINAL OUTLET FLOW AVE | l/s | WASTE |  | WASTE:E52115
13297 | #N/A | #N/A | #N/A | E52118 | 132972INLET PS FLOW AI | l/s | WASTE |  | WASTE:E52118
13297 | #N/A | #N/A | #N/A | E52124 | 132972HRF FEED FLOW | l/s | WASTE |  | WASTE:E52124
13297 | #N/A | #N/A | #N/A | E52125 | 132972HRF OUTLET FLOW | l/s | WASTE |  | WASTE:E52125
13297 | #N/A | #N/A | #N/A | E55023 | 132972PUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E55023
13297 | #N/A | #N/A | #N/A | E55034 | 132972PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E55034
13297 | #N/A | #N/A | #N/A | E18888 | 132971FINAL OUTLET FLW | l/s | WASTE |  | WASTE:E18888
13297 | #N/A | #N/A | #N/A | E18890 | 132971INLET PS FLW | l/s | WASTE |  | WASTE:E18890
13297 | #N/A | #N/A | #N/A | E52108 | 132972FINAL OUTLET FLW | l/s | WASTE |  | WASTE:E52108
13298 | #N/A | #N/A | #N/A | E10868 | 132980EA195FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E10868
13298 | #N/A | #N/A | #N/A | E10870 | 132980FLOW TO PRIMARY SED TANK 1 | l/s | WASTE |  | WASTE:E10870
13298 | #N/A | #N/A | #N/A | E10871 | 132980FLOW TO PRIMARY SED TANK 2 | l/s | WASTE |  | WASTE:E10871
13298 | #N/A | #N/A | #N/A | E10872 | 132980FLOW TO 2ND STAGE SUMP | l/s | WASTE |  | WASTE:E10872
13298 | #N/A | #N/A | #N/A | E10877 | 132980RISING MAIN FLOW FROM LWR STANTON SPS | l/s | WASTE |  | WASTE:E10877
13298 | #N/A | #N/A | #N/A | E50066 | 132980PUMP SET 2 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E50066
13298 | #N/A | #N/A | #N/A | E54218 | 132980PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E54218
13298 | #N/A | #N/A | #N/A | E54226 | 132980PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E54226
13303 | #N/A | #N/A | #N/A | E4057 | 133030EA096FLOW FROM WORKS | l/s | WASTE |  | WASTE:E4057
13304 | #N/A | #N/A | #N/A | E33331 | 133041EA097FFT FLOWRATE ANG | l/s | WASTE |  | WASTE:E33331
13304 | #N/A | #N/A | #N/A | E33345 | 133041FFT WORKS FLOWRATE ANG | l/s | WASTE |  | WASTE:E33345
13304 | #N/A | #N/A | #N/A | E33348 | 133041STORM RETURN FLOW ANG | l/s | WASTE |  | WASTE:E33348
13304 | #N/A | #N/A | #N/A | E33359 | 133041RAS DELIVERY FLOW ANG | l/s | WASTE |  | WASTE:E33359
13304 | #N/A | #N/A | #N/A | E33360 | 133041SAS DELIVERY FLOW ANG | l/s | WASTE |  | WASTE:E33360
13304 | #N/A | #N/A | #N/A | E34494 | 133041STORM FLOW | l/s | WASTE |  | WASTE:E34494
13304 | #N/A | #N/A | #N/A | E56559 | 133041PROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E56559
13304 | #N/A | #N/A | #N/A | E56564 | 133041PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E56564
13304 | #N/A | #N/A | #N/A | E96501 | 133041FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E96501
13304 | #N/A | #N/A | #N/A | E33333 | 133041SPETISBURY NO3 SPS FLW | l/s | WASTE |  | WASTE:E33333
13305 | #N/A | #N/A | #N/A | E5970 | 13305FDIGESTER 1 FLOW | l/s | WASTE |  | WASTE:E5970
13305 | #N/A | #N/A | #N/A | E5971 | 133050DIGESTER 2 FLOW | l/s | WASTE |  | WASTE:E5971
13305 | #N/A | #N/A | #N/A | E5989 | 133050DIG 3 SLUDGE FEED FLOW METER AN | l/s | WASTE |  | WASTE:E5989
13305 | #N/A | #N/A | #N/A | E5992 | 133050EA274RETURN LIQUOR FLOW | l/s | WASTE |  | WASTE:E5992
13305 | #N/A | #N/A | #N/A | E20906 | 133050FLOW TO FULL TREATMNT AN | l/s | WASTE |  | WASTE:E20906
13305 | #N/A | #N/A | #N/A | E20925 | 133050RETURN LIQUORS FLOW | l/s | WASTE |  | WASTE:E20925
13305 | #N/A | #N/A | #N/A | E20933 | 133050PST AUTO DESLUDGE TRANSFER FLOW DNP3 | l/s | WASTE |  | WASTE:E20933
13305 | #N/A | #N/A | #N/A | E20955 | 133050SAS DRAW OFF FLOW AN | l/s | WASTE |  | WASTE:E20955
13305 | #N/A | #N/A | #N/A | E20974 | 133050DERIVED ASP 1 FLOW | l/s | WASTE |  | WASTE:E20974
13305 | #N/A | #N/A | #N/A | E33466 | 133050GBT1 THICKENED SLUDGE FLOW | l/s | WASTE |  | WASTE:E33466
13305 | #N/A | #N/A | #N/A | E33469 | 13305FGBT POLY PUMP 1 FLOW | l/s | WASTE |  | WASTE:E33469
13305 | #N/A | #N/A | #N/A | E33470 | 133050GBT POLY PUMP 2 FLOW | l/s | WASTE |  | WASTE:E33470
13305 | #N/A | #N/A | #N/A | E33474 | 133050GBT2 THICKENED SLUDGE FLOW | l/s | WASTE |  | WASTE:E33474
13305 | #N/A | #N/A | #N/A | E36277 | 13305FINDIGENOUS RAW SLUDGE FLOW | l/s | WASTE |  | WASTE:E36277
13305 | #N/A | #N/A | #N/A | E36279 | 13305FGBT 1 RETURN LIQUORS FLOW | l/s | WASTE |  | WASTE:E36279
13305 | #N/A | #N/A | #N/A | E36281 | 13305FGBT 2 RETURN LIQUORS FLOW | l/s | WASTE |  | WASTE:E36281
13305 | #N/A | #N/A | #N/A | E36283 | 13305FLIQUOR RETURN FLOW | l/s | WASTE |  | WASTE:E36283
13305 | #N/A | #N/A | #N/A | E37774 | 133050ASP 2 FEED PS FLOW ANG | l/s | WASTE |  | WASTE:E37774
13305 | #N/A | #N/A | #N/A | E37793 | 133050RAS PUMPS FLOW ANG | l/s | WASTE |  | WASTE:E37793
13305 | #N/A | #N/A | #N/A | E37794 | 133050SAS FLOW | l/s | WASTE |  | WASTE:E37794
13305 | #N/A | #N/A | #N/A | E53328 | 13305FPST AUTO DESLUDGE TRANSFER FLOW DNP3 | l/s | WASTE |  | WASTE:E53328
13305 | #N/A | #N/A | #N/A | E53338 | 13305FDIG 3 SLUDGE FEED FLOW METER AN DNP3 | l/s | WASTE |  | WASTE:E53338
13305 | #N/A | #N/A | #N/A | E53399 | 13305FGBT POLY PUMP 2 FLOW DNP3 | l/s | WASTE |  | WASTE:E53399
13305 | #N/A | #N/A | #N/A | E53685 | 133050PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E53685
13305 | #N/A | #N/A | #N/A | E53690 | 133050PUMP SET 2 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E53690
13305 | #N/A | #N/A | #N/A | E53695 | 133050PUMP SET 3 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E53695
13305 | #N/A | #N/A | #N/A | E53706 | 13305FPUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E53706
13305 | #N/A | #N/A | #N/A | E53710 | 13305FPUMP SET 2 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E53710
13305 | #N/A | #N/A | #N/A | E53714 | 13305FPUMP SET 3 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E53714
13305 | #N/A | #N/A | #N/A | E53967 | 13305FDW LIQUOR RETURN FLOW DNP3 | l/s | WASTE |  | WASTE:E53967
13305 | #N/A | #N/A | #N/A | E53968 | 13305FDW LIQUOR BALANCE TANK OVERFLOW DNP3 | l/s | WASTE |  | WASTE:E53968
13305 | #N/A | #N/A | #N/A | E54901 | 133050DIG 4 SLDG FEED FLOW AI | l/s | WASTE |  | WASTE:E54901
13305 | #N/A | #N/A | #N/A | E6002 | 133050TREATMT FLW ANLG OUTPUT | l/s | WASTE |  | WASTE:E6002
13305 | #N/A | #N/A | #N/A | E6003 | 133050CONSENT FLW ANLG OUTPUT | l/s | WASTE |  | WASTE:E6003
13306 | #N/A | #N/A | #N/A | E9615 | 133060EA098FLOW TO WORKS | l/s | WASTE |  | WASTE:E9615
13306 | #N/A | #N/A | #N/A | E96357 | 13306APROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E96357
13306 | #N/A | #N/A | #N/A | E96362 | 13306APUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E96362
13306 | #N/A | #N/A | #N/A | E96367 | 13306APUMP SET 2 SEWAGE FLOW | l/s | WASTE |  | WASTE:E96367
13307 | #N/A | #N/A | #N/A | E3082 | 133070EA099OUTLET FLOW | l/s | WASTE |  | WASTE:E3082
13307 | #N/A | #N/A | #N/A | E3083 | 133070SCREENED INLET FLOW | l/s | WASTE |  | WASTE:E3083
13307 | #N/A | #N/A | #N/A | E29346 | 13307AFULL FLOW TO TREATMENT AN | l/s | WASTE |  | WASTE:E29346
13307 | #N/A | #N/A | #N/A | E29347 | 13307APRIMARY DESLUDGE PUMP FLOW AN | l/s | WASTE |  | WASTE:E29347
13307 | #N/A | #N/A | #N/A | E29392 | 13307BDOSE SET 1 INLET FLOW | l/s | WASTE |  | WASTE:E29392
13307 | #N/A | #N/A | #N/A | E29393 | 13307BDOSE SET 2 INLET FLOW | l/s | WASTE |  | WASTE:E29393
13307 | #N/A | #N/A | #N/A | E54276 | 133070MECANA FILTER FEED FLOW AI | l/s | WASTE |  | WASTE:E54276
13307 | #N/A | #N/A | #N/A | E54278 | 133070BACKWASH RETURN FLOW ANG | l/s | WASTE |  | WASTE:E54278
13307 | #N/A | #N/A | #N/A | E54284 | 133070RECIRC FLOW | l/s | WASTE |  | WASTE:E54284
13308 | #N/A | #N/A | #N/A | E55177 | 133081WORKS FLOWMETER ANG | l/s | WASTE |  | WASTE:E55177
13308 | #N/A | #N/A | #N/A | E55534 | 133081INLET FLUME FLOW ANG | l/s | WASTE |  | WASTE:E55534
13308 | #N/A | #N/A | #N/A | E55540 | 133081BYDEMILL BROOK FE FLOW ANG | l/s | WASTE |  | WASTE:E55540
13308 | #N/A | #N/A | #N/A | E55547 | 133081EA100INLET FLUME FLOW MCERTS ANG | l/s | WASTE |  | WASTE:E55547
13308 | #N/A | #N/A | #N/A | E55552 | 133081RAS PUMP FLOW ANG | l/s | WASTE |  | WASTE:E55552
13309 | #N/A | #N/A | #N/A | E1145 | 133090INLET FLOW | l/s | WASTE |  | WASTE:E1145
13309 | #N/A | #N/A | #N/A | E1146 | 133090STORM FLOW | l/s | WASTE |  | WASTE:E1146
13309 | #N/A | #N/A | #N/A | E11636 | 133091EA101INLET FLOW | l/s | WASTE |  | WASTE:E11636
13309 | #N/A | #N/A | #N/A | E11637 | 133091STORM FLOW | l/s | WASTE |  | WASTE:E11637
13309 | #N/A | #N/A | #N/A | E11644 | 133091FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E11644
13309 | #N/A | #N/A | #N/A | E11650 | 133091OUTFALL FLOW | l/s | WASTE |  | WASTE:E11650
13309 | #N/A | #N/A | #N/A | E53298 | 133091EA343WASHWATER FLOW | l/s | WASTE |  | WASTE:E53298
13309 | #N/A | #N/A | #N/A | E53299 | 133091INLET FLOW MINUS WASHWATER | l/s | WASTE |  | WASTE:E53299
13310 | #N/A | #N/A | #N/A | E2575 | 133100EA102FINAL EFF FLOW | l/s | WASTE |  | WASTE:E2575
13310 | #N/A | #N/A | #N/A | E54822 | 133101SLUDGE TRANSFER FLOW AI | l/s | WASTE |  | WASTE:E54822
13310 | #N/A | #N/A | #N/A | E54843 | 133101WASHWATER FLOW AI | l/s | WASTE |  | WASTE:E54843
13310 | #N/A | #N/A | #N/A | E54852 | 133101LIME PLANT DOSING FLOW 1 AI | l/s | WASTE |  | WASTE:E54852
13310 | #N/A | #N/A | #N/A | E54853 | 133101LIME PLANT DOSING FLOW 2 AI | l/s | WASTE |  | WASTE:E54853
13310 | #N/A | #N/A | #N/A | E54857 | 133101MBBR FEED PS FLOW AI | l/s | WASTE |  | WASTE:E54857
13310 | #N/A | #N/A | #N/A | E54866 | 133101PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E54866
13310 | #N/A | #N/A | #N/A | E54871 | 133101PUMP SET 2 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E54871
13310 | #N/A | #N/A | #N/A | E54879 | 133101PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E54879
13310 | #N/A | #N/A | #N/A | E54884 | 133101PUMP SET 2 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E54884
13310 | #N/A | #N/A | #N/A | E58390 | 133101BEER HACKETT RISING MAIN FLOW DUTY | l/s | WASTE |  | WASTE:E58390
13310 | #N/A | #N/A | #N/A | E58391 | 133101BEER HACKETT RISING MAIN FLOW STBY | l/s | WASTE |  | WASTE:E58391
13311 | #N/A | #N/A | #N/A | E32160 | 133110EA285OUTLET FLOW | l/s | WASTE |  | WASTE:E32160
13312 | #N/A | #N/A | #N/A | E2105 | 133120FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E2105
13312 | #N/A | #N/A | #N/A | E2106 | 133120EA197 MCERT FLOW | l/s | WASTE |  | WASTE:E2106
13312 | #N/A | #N/A | #N/A | E2107 | 133120CONTROLLED INLET FLOW | l/s | WASTE |  | WASTE:E2107
13313 | #N/A | #N/A | #N/A | E4638 | 133131EA198OUTFALL FLOW | l/s | WASTE |  | WASTE:E4638
13313 | #N/A | #N/A | #N/A | E4645 | 133131OUTFALL FLOW AVE | l/s | WASTE |  | WASTE:E4645
13313 | #N/A | #N/A | #N/A | E31772 | 13313AINLET FLOWMETER | l/s | WASTE |  | WASTE:E31772
13313 | #N/A | #N/A | #N/A | E31774 | 13313ATSF 1 FLOW | l/s | WASTE |  | WASTE:E31774
13313 | #N/A | #N/A | #N/A | E31775 | 13313ATSF 2 FLOW | l/s | WASTE |  | WASTE:E31775
13313 | #N/A | #N/A | #N/A | E31781 | 13313ATSF 3 FLOW | l/s | WASTE |  | WASTE:E31781
13313 | #N/A | #N/A | #N/A | E31782 | 13313ATSF 4 FLOW | l/s | WASTE |  | WASTE:E31782
13313 | #N/A | #N/A | #N/A | E31811 | 13313ATSF SUMMATED FLOW | l/s | WASTE |  | WASTE:E31811
13313 | #N/A | #N/A | #N/A | E31818 | 13313BINLET FLOW DOSE SET 1 | l/s | WASTE |  | WASTE:E31818
13313 | #N/A | #N/A | #N/A | E31819 | 13313BINLET FLOW DOSE SET 2 | l/s | WASTE |  | WASTE:E31819
13314 | #N/A | #N/A | #N/A | E3097 | 133140INLET FLOW | l/s | WASTE |  | WASTE:E3097
13315 | #N/A | #N/A | #N/A | E1165 | 133150EA199FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E1165
13317 | #N/A | #N/A | #N/A | E2295 | 133171EA103OUTLET FLOW | l/s | WASTE |  | WASTE:E2295
13318 | #N/A | #N/A | #N/A | E3997 | 133181LDC IMPORT FLOW TO INLET | l/s | WASTE |  | WASTE:E3997
13318 | #N/A | #N/A | #N/A | E4005 | 133181SLUDGE IMPORT PUMP 1 FLOW | l/s | WASTE |  | WASTE:E4005
13318 | #N/A | #N/A | #N/A | E4010 | 133181SLUDGE IMPORT PUMP 2 FLOW | l/s | WASTE |  | WASTE:E4010
13318 | #N/A | #N/A | #N/A | E4021 | 133180INLET FLOW | l/s | WASTE |  | WASTE:E4021
13318 | #N/A | #N/A | #N/A | E4023 | 133180MCERT FLOW | l/s | WASTE |  | WASTE:E4023
13318 | #N/A | #N/A | #N/A | E4025 | 133180INLET FLOW MEAN | l/s | WASTE |  | WASTE:E4025
13318 | #N/A | #N/A | #N/A | E17511 | 133181INLET FLOW 1 | l/s | WASTE |  | WASTE:E17511
13318 | #N/A | #N/A | #N/A | E37049 | 133181APD PLANT BIOMASS FLOWRATE ANG | l/s | WASTE |  | WASTE:E37049
13318 | #N/A | #N/A | #N/A | E37056 | 133181DIG 1 HEAT EXCHANGR SLDG FLOWRATE | l/s | WASTE |  | WASTE:E37056
13318 | #N/A | #N/A | #N/A | E37063 | 133181DIG 2 HEAT EXCHANGR SLDG FLOWRATE | l/s | WASTE |  | WASTE:E37063
13318 | #N/A | #N/A | #N/A | E37088 | 133181CHP INLET HOT WATER FLOWRATE | l/s | WASTE |  | WASTE:E37088
13318 | #N/A | #N/A | #N/A | E37099 | 133181WATER CIRC FLOW | l/s | WASTE |  | WASTE:E37099
13318 | #N/A | #N/A | #N/A | E37100 | 133181SLUDGE CIRCULATION FLOW | l/s | WASTE |  | WASTE:E37100
13318 | #N/A | #N/A | #N/A | E37107 | 133181APD BYPASS FLOW FT3001 | l/s | WASTE |  | WASTE:E37107
13318 | #N/A | #N/A | #N/A | E37108 | 133181APD PLANT BIOMASS FLOW FT2001 | l/s | WASTE |  | WASTE:E37108
13318 | #N/A | #N/A | #N/A | E37111 | 133181BELT THICKENER 1 FLOWRATE ANG | l/s | WASTE |  | WASTE:E37111
13318 | #N/A | #N/A | #N/A | E37112 | 133181THICKENED SLUDGE FLOWRATE | l/s | WASTE |  | WASTE:E37112
13318 | #N/A | #N/A | #N/A | E37113 | 133181BELT THICKENER 2 FLOWRATE | l/s | WASTE |  | WASTE:E37113
13318 | #N/A | #N/A | #N/A | E37260 | 13318A PULSAR INLET FLOW METER | l/s | WASTE |  | WASTE:E37260
13318 | #N/A | #N/A | #N/A | E37328 | 13318APOLY PUMP 1 FLOW RATE | l/s | WASTE |  | WASTE:E37328
13318 | #N/A | #N/A | #N/A | E37329 | 13318APOLY PUMP 2 FLOW RATE | l/s | WASTE |  | WASTE:E37329
13318 | #N/A | #N/A | #N/A | E37356 | 133181APD TO MAD FEED FLOW FT001 | l/s | WASTE |  | WASTE:E37356
13318 | #N/A | #N/A | #N/A | E38837 | 13318AHUMUS RETURN PS FLOW | l/s | WASTE |  | WASTE:E38837
13318 | #N/A | #N/A | #N/A | E39700 | 13318ALIQUORS RETURN FLOW ANG | l/s | WASTE |  | WASTE:E39700
13318 | #N/A | #N/A | #N/A | E50262 | 133181TEMP PRIMARY FERRIC DOSING INLET FLOW AL | l/s | WASTE |  | WASTE:E50262
13318 | #N/A | #N/A | #N/A | E52794 | 13318AINDIGENOUS SLUDGE FLOW | l/s | WASTE |  | WASTE:E52794
13318 | #N/A | #N/A | #N/A | E52797 | 13318ASLUDGE THICKENING LIQUORS FLOW | l/s | WASTE |  | WASTE:E52797
13318 | #N/A | #N/A | #N/A | E52798 | 13318ASLUDGE DEWATERING LIQUORS FLOW | l/s | WASTE |  | WASTE:E52798
13318 | #N/A | #N/A | #N/A | E53420 | 133180TASF FEED FLOW ANG | l/s | WASTE |  | WASTE:E53420
13318 | #N/A | #N/A | #N/A | E53423 | 133180BACKWASH FLOW ANG | l/s | WASTE |  | WASTE:E53423
13318 | #N/A | #N/A | #N/A | E53424 | 133180FILTER 1 FLOW ANG | l/s | WASTE |  | WASTE:E53424
13318 | #N/A | #N/A | #N/A | E53425 | 133180FILTER 2 FLOW ANG | l/s | WASTE |  | WASTE:E53425
13318 | #N/A | #N/A | #N/A | E53426 | 133180FILTER 3 FLOW ANG | l/s | WASTE |  | WASTE:E53426
13318 | #N/A | #N/A | #N/A | E53427 | 133180FILTER 4 FLOW ANG | l/s | WASTE |  | WASTE:E53427
13318 | #N/A | #N/A | #N/A | E53428 | 133180FILTER 5 FLOW ANG | l/s | WASTE |  | WASTE:E53428
13318 | #N/A | #N/A | #N/A | E53429 | 133180FILTER 6 FLOW ANG | l/s | WASTE |  | WASTE:E53429
13318 | #N/A | #N/A | #N/A | E53430 | 133180FILTER 7 FLOW ANG | l/s | WASTE |  | WASTE:E53430
13318 | #N/A | #N/A | #N/A | E53431 | 133180FILTER 8 FLOW ANG | l/s | WASTE |  | WASTE:E53431
13318 | #N/A | #N/A | #N/A | E53432 | 133180FILTER 9 FLOW ANG | l/s | WASTE |  | WASTE:E53432
13318 | #N/A | #N/A | #N/A | E53433 | 133180FILTER 10 FLOW ANG | l/s | WASTE |  | WASTE:E53433
13318 | #N/A | #N/A | #N/A | E53449 | 133180TASF BYPASS 1 FLOW ANG | l/s | WASTE |  | WASTE:E53449
13318 | #N/A | #N/A | #N/A | E53450 | 133180TASF BYPASS 2 FLOW ANG | l/s | WASTE |  | WASTE:E53450
13318 | #N/A | #N/A | #N/A | E54472 | 133181FINAL EFFLUENT FLOWMETER ANG | l/s | WASTE |  | WASTE:E54472
13318 | #N/A | #N/A | #N/A | E96644 | 13318BPRIMARY PROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E96644
13318 | #N/A | #N/A | #N/A | E96649 | 13318BPRIMARY PUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E96649
13318 | #N/A | #N/A | #N/A | E96736 | 133181FLOCCULATION TANK 1 FLOW ANG | l/s | WASTE |  | WASTE:E96736
13318 | #N/A | #N/A | #N/A | E96737 | 133181FLOCCULATION TANK 2 FLOW ANG | l/s | WASTE |  | WASTE:E96737
13318 | #N/A | #N/A | #N/A | E96738 | 133181FLOCCULATION TANK 3 FLOW ANG | l/s | WASTE |  | WASTE:E96738
13318 | #N/A | #N/A | #N/A | E96739 | 133181FLOCCULATION TANK 4 FLOW ANG | l/s | WASTE |  | WASTE:E96739
13318 | #N/A | #N/A | #N/A | E4034 | 133180WORKS OUTLET FLW | l/s | WASTE |  | WASTE:E4034
13319 | #N/A | #N/A | #N/A | E3605 | 133190TREATMENT FLOW | l/s | WASTE |  | WASTE:E3605
13319 | #N/A | #N/A | #N/A | E3607 | 133190EA104MCERT INLET FLOW | l/s | WASTE |  | WASTE:E3607
13319 | #N/A | #N/A | #N/A | E3610 | 133190EDM STORM LAGOON OVERFLOW | l/s | WASTE |  | WASTE:E3610
13320 | #N/A | #N/A | #N/A | E21801 | 133200EA201INLET FLOW | l/s | WASTE |  | WASTE:E21801
13320 | #N/A | #N/A | #N/A | E31585 | 13320ADRUM FILTERS FEED PS FLOW | l/s | WASTE |  | WASTE:E31585
13320 | #N/A | #N/A | #N/A | E31586 | 13320AWORKS INLET FLOWMETER ANG | l/s | WASTE |  | WASTE:E31586
13320 | #N/A | #N/A | #N/A | E31591 | 13320ASLUDGE TRANSFER FLOW | l/s | WASTE |  | WASTE:E31591
13320 | #N/A | #N/A | #N/A | E31765 | 13320BDOSE SET 1 INLET FLOW | l/s | WASTE |  | WASTE:E31765
13320 | #N/A | #N/A | #N/A | E31766 | 13320BDOSE SET 2 INLET FLOW | l/s | WASTE |  | WASTE:E31766
13322 | #N/A | #N/A | #N/A | E14381 | 133222EA105OUTLET MCERT FLOW | l/s | WASTE |  | WASTE:E14381
13322 | #N/A | #N/A | #N/A | E35553 | 133222BAFF FLOW | l/s | WASTE |  | WASTE:E35553
13323 | #N/A | #N/A | #N/A | E4291 | 133230FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E4291
13324 | #N/A | #N/A | #N/A | E14580 | 133241HOLTON HEATH FLOW | l/s | WASTE |  | WASTE:E14580
13324 | #N/A | #N/A | #N/A | E14586 | 133241WAREHAM FLOWS | l/s | WASTE |  | WASTE:E14586
13324 | #N/A | #N/A | #N/A | E14587 | 133241SANDFORD SPS FLOW | l/s | WASTE |  | WASTE:E14587
13324 | #N/A | #N/A | #N/A | E14588 | 133241AERATION FLOW | l/s | WASTE |  | WASTE:E14588
13324 | #N/A | #N/A | #N/A | E14630 | 133241EA202UV FLOW | l/s | WASTE |  | WASTE:E14630
13324 | #N/A | #N/A | #N/A | E56443 | 133241EA348 MCERTS PST 1 FLOW AI | l/s | WASTE |  | WASTE:E56443
13324 | #N/A | #N/A | #N/A | E56444 | 133241EA349 MCERTS PST 2 FLOW AI | l/s | WASTE |  | WASTE:E56444
13324 | #N/A | #N/A | #N/A | E56445 | 133241EA350 MCERTS ASP FLOW AI | l/s | WASTE |  | WASTE:E56445
13324 | #N/A | #N/A | #N/A | E56446 | 133241STORM AND WORKS RETURN FLOW AI | l/s | WASTE |  | WASTE:E56446
13324 | #N/A | #N/A | #N/A | E56447 | 133241EA352 MCERTS BACKWASH RETURN FLOW AI | l/s | WASTE |  | WASTE:E56447
13324 | #N/A | #N/A | #N/A | E56450 | 133241TSF FEED PS FLOW AI | l/s | WASTE |  | WASTE:E56450
13324 | #N/A | #N/A | #N/A | E56451 | 133241TSF RECIRC FLOW AI | l/s | WASTE |  | WASTE:E56451
13324 | #N/A | #N/A | #N/A | E56462 | 133241TSF 1 FLOW AI | l/s | WASTE |  | WASTE:E56462
13324 | #N/A | #N/A | #N/A | E56463 | 133241TSF 2 FLOW AI | l/s | WASTE |  | WASTE:E56463
13324 | #N/A | #N/A | #N/A | E56464 | 133241TSF 3 FLOW AI | l/s | WASTE |  | WASTE:E56464
13324 | #N/A | #N/A | #N/A | E56465 | 133241TSF 4 FLOW AI | l/s | WASTE |  | WASTE:E56465
13324 | #N/A | #N/A | #N/A | E56466 | 133241TSF 5 FLOW AI | l/s | WASTE |  | WASTE:E56466
13324 | #N/A | #N/A | #N/A | E56471 | 133241EA351 MCERTS WORKS RETURN FLOW | l/s | WASTE |  | WASTE:E56471
13324 | #N/A | #N/A | #N/A | E56472 | 133241STORM RETURN FLOW | l/s | WASTE |  | WASTE:E56472
13325 | #N/A | #N/A | #N/A | E4336 | 133250OUTLET FLOW | l/s | WASTE |  | WASTE:E4336
13325 | #N/A | #N/A | #N/A | E4338 | 133250SLUDGE PLANT OUTFLOW | l/s | WASTE |  | WASTE:E4338
13325 | #N/A | #N/A | #N/A | E4341 | 133250EA107MCERT FLOW TO AERATION | l/s | WASTE |  | WASTE:E4341
13325 | #N/A | #N/A | #N/A | E4342 | 133250EA106MCERT FLOW TO FILTER | l/s | WASTE |  | WASTE:E4342
13325 | #N/A | #N/A | #N/A | E4343 | 133250SUMMATED FLOW | l/s | WASTE |  | WASTE:E4343
13325 | #N/A | #N/A | #N/A | E29301 | 13325ARAS LINE 1 FLOW ANG | l/s | WASTE |  | WASTE:E29301
13325 | #N/A | #N/A | #N/A | E29302 | 13325ARAS LINE 2 FLOW ANG | l/s | WASTE |  | WASTE:E29302
13325 | #N/A | #N/A | #N/A | E29830 | 13325BSAND FILTER 1 FEED FLOW | l/s | WASTE |  | WASTE:E29830
13325 | #N/A | #N/A | #N/A | E29831 | 13325BSAND FILTER 2 FEED FLOW | l/s | WASTE |  | WASTE:E29831
13325 | #N/A | #N/A | #N/A | E29832 | 13325BSAND FILTER 3 FEED FLOW | l/s | WASTE |  | WASTE:E29832
13325 | #N/A | #N/A | #N/A | E52994 | 133250INLET FLOW TO FILTER BEDS | l/s | WASTE |  | WASTE:E52994
13325 | #N/A | #N/A | #N/A | E52995 | 133250INLET FLOW TO OXIDATION DITCH | l/s | WASTE |  | WASTE:E52995
13325 | #N/A | #N/A | #N/A | E52997 | 133250INLET SCREEN 2 WASHWATER FLOW | l/s | WASTE |  | WASTE:E52997
13325 | #N/A | #N/A | #N/A | E52998 | 133250COMPACTOR 1 WASHWATER FLOW | l/s | WASTE |  | WASTE:E52998
13325 | #N/A | #N/A | #N/A | E53005 | 133250COMPACTOR 2 WASHWATER FLOW | l/s | WASTE |  | WASTE:E53005
13325 | #N/A | #N/A | #N/A | E56802 | 13325CPROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E56802
13325 | #N/A | #N/A | #N/A | E56807 | 13325CPUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E56807
13325 | #N/A | #N/A | #N/A | E56812 | 13325CPUMP SET 2 SEWAGE FLOW | l/s | WASTE |  | WASTE:E56812
13325 | #N/A | #N/A | #N/A | E56817 | 13325CPUMP SET 3 SEWAGE FLOW | l/s | WASTE |  | WASTE:E56817
13325 | #N/A | #N/A | #N/A | E52991 | 133250INLET SCREEN 1 WASHWTR FLW | l/s | WASTE |  | WASTE:E52991
13325 | #N/A | #N/A | #N/A | E52992 | 133250LAUNDER CHANNEL WASHWTR FLW | l/s | WASTE |  | WASTE:E52992
13329 | #N/A | #N/A | #N/A | E10882 | 133290EA108INLET FLOW | l/s | WASTE |  | WASTE:E10882
13330 | #N/A | #N/A | #N/A | E5108 | 133300FLOWMETER | l/s | WASTE |  | WASTE:E5108
13330 | #N/A | #N/A | #N/A | E31036 | 133300EA109FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E31036
13330 | #N/A | #N/A | #N/A | E31045 | 133300DERIVED WETTING FLOW RATE | l/s | WASTE |  | WASTE:E31045
13330 | #N/A | #N/A | #N/A | E31046 | 133300DERIVED DILUTION FLOW RATE | l/s | WASTE |  | WASTE:E31046
13330 | #N/A | #N/A | #N/A | E52588 | 133300PUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E52588
13330 | #N/A | #N/A | #N/A | E52595 | 133300PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E52595
13331 | #N/A | #N/A | #N/A | E4301 | 133310EA204FLOW TO FULL TREATMENT | l/s | WASTE |  | WASTE:E4301
13332 | #N/A | #N/A | #N/A | E3290 | 133320TREATMENT FLOW | l/s | WASTE |  | WASTE:E3290
13332 | #N/A | #N/A | #N/A | E3291 | 133320STORM FLOW 1 | l/s | WASTE |  | WASTE:E3291
13332 | #N/A | #N/A | #N/A | E3292 | 133320STORM FLOW 2 | l/s | WASTE |  | WASTE:E3292
13332 | #N/A | #N/A | #N/A | E3301 | 133320SLUDGE DISCHARGE FLOW | l/s | WASTE |  | WASTE:E3301
13332 | #N/A | #N/A | #N/A | E3303 | 133320EA205FULL FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E3303
13332 | #N/A | #N/A | #N/A | E3304 | 133320EA322TREATMENT FLOW 1 OLD LH | l/s | WASTE |  | WASTE:E3304
13332 | #N/A | #N/A | #N/A | E3305 | 133320EA323TREATMENT FLOW 2 NEW RH | l/s | WASTE |  | WASTE:E3305
13332 | #N/A | #N/A | #N/A | E3308 | 133320RISING MAIN FLOW FROM MILL LN SPS | l/s | WASTE |  | WASTE:E3308
13332 | #N/A | #N/A | #N/A | E38154 | 133320PUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E38154
13332 | #N/A | #N/A | #N/A | E38161 | 133320PUMP SET 2 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E38161
13332 | #N/A | #N/A | #N/A | E38172 | 133320PUMP SET 1 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E38172
13332 | #N/A | #N/A | #N/A | E38177 | 133320PUMP SET 2 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E38177
13336 | #N/A | #N/A | #N/A | E3555 | 133360FLOWMETER 2 FLOW | l/s | WASTE |  | WASTE:E3555
13336 | #N/A | #N/A | #N/A | E3559 | 133360POLY FLOW TO CENTRIFUGE | l/s | WASTE |  | WASTE:E3559
13336 | #N/A | #N/A | #N/A | E3746 | 133360FLOW TO ACTIVATED SLUDGE | l/s | WASTE |  | WASTE:E3746
13336 | #N/A | #N/A | #N/A | E3747 | 133360FLOW FROM AS BYPASS | l/s | WASTE |  | WASTE:E3747
13336 | #N/A | #N/A | #N/A | E3748 | 133360RAS FLOW TO PRE MIXER | l/s | WASTE |  | WASTE:E3748
13336 | #N/A | #N/A | #N/A | E3766 | 133360RECIRC FLOW | l/s | WASTE |  | WASTE:E3766
13336 | #N/A | #N/A | #N/A | E3773 | 133360EA110MCERT FLOW | l/s | WASTE |  | WASTE:E3773
13336 | #N/A | #N/A | #N/A | E3785 | 133360UV CHANNEL FLOW | l/s | WASTE |  | WASTE:E3785
13336 | #N/A | #N/A | #N/A | E3786 | 133360UV FLOW | l/s | WASTE |  | WASTE:E3786
13336 | #N/A | #N/A | #N/A | E7907 | 133360LIQUORS RETURN FLOW TO INLET | l/s | WASTE |  | WASTE:E7907
13336 | #N/A | #N/A | #N/A | E21004 | 133360RETURNS FLOW | l/s | WASTE |  | WASTE:E21004
13336 | #N/A | #N/A | #N/A | E21006 | 133360OUTLET FLOW | l/s | WASTE |  | WASTE:E21006
13336 | #N/A | #N/A | #N/A | E35547 | 133360SAS FLOW | l/s | WASTE |  | WASTE:E35547
13336 | #N/A | #N/A | #N/A | E35550 | 133360HRF INFLOW 1 | l/s | WASTE |  | WASTE:E35550
13336 | #N/A | #N/A | #N/A | E35551 | 133360HRF INFLOW 2 | l/s | WASTE |  | WASTE:E35551
13336 | #N/A | #N/A | #N/A | E35552 | 133360REQUIRED HIGHBRIDGE FLOW SET POINT | l/s | WASTE |  | WASTE:E35552
13336 | #N/A | #N/A | #N/A | E51876 | 133360SLOWAY LANE INLET FLOW | l/s | WASTE |  | WASTE:E51876
13336 | #N/A | #N/A | #N/A | E52813 | 133360INDIGENOUS SLUDGE FLOW | l/s | WASTE |  | WASTE:E52813
13336 | #N/A | #N/A | #N/A | E52815 | 133360LIQUOR RETURN SLUDGE FLOW | l/s | WASTE |  | WASTE:E52815
13336 | #N/A | #N/A | #N/A | E55834 | 13336ADWF FLOW RATE AI | l/s | WASTE |  | WASTE:E55834
13336 | #N/A | #N/A | #N/A | E55835 | 13336AHIGH FEED FLOW RATE AI | l/s | WASTE |  | WASTE:E55835
13336 | #N/A | #N/A | #N/A | E55850 | 13336ARAS FLOW RATE AI | l/s | WASTE |  | WASTE:E55850
13336 | #N/A | #N/A | #N/A | E55851 | 13336ASAS FLOW RATE AI | l/s | WASTE |  | WASTE:E55851
13336 | #N/A | #N/A | #N/A | E56289 | 13336BPST DESLUDGE FLOW RATE AI | l/s | WASTE |  | WASTE:E56289
13336 | #N/A | #N/A | #N/A | E56290 | 13336BRAW SLUDGE FLOW AI | l/s | WASTE |  | WASTE:E56290
13336 | #N/A | #N/A | #N/A | E56296 | 13336BFINAL EFFLUENT WASHWATER FLOW AI | l/s | WASTE |  | WASTE:E56296
13338 | #N/A | #N/A | #N/A | E13985 | 133380EA338MCERTS NORTHACRE FLOW | l/s | WASTE |  | WASTE:E13985
13338 | #N/A | #N/A | #N/A | E13986 | 133380NABP BALANCE TANK OUTLET FLOW | l/s | WASTE |  | WASTE:E13986
13338 | #N/A | #N/A | #N/A | E14031 | 133380MCERTS TOWN INLET FLOW | l/s | WASTE |  | WASTE:E14031
13338 | #N/A | #N/A | #N/A | E14041 | 133380EA337MCERTS TOWN INLET FLOW | l/s | WASTE |  | WASTE:E14041
13338 | #N/A | #N/A | #N/A | E14521 | 133380TASF BYPASS FLOW | l/s | WASTE |  | WASTE:E14521
13338 | #N/A | #N/A | #N/A | E27547 | 133380SAND FILTER BYPASS FLOW | l/s | WASTE |  | WASTE:E27547
13338 | #N/A | #N/A | #N/A | E55121 | 133380ASP ANOXIC SELECTOR FEED FLOW AI | l/s | WASTE |  | WASTE:E55121
13338 | #N/A | #N/A | #N/A | E55122 | 133380ANOXIC SELECTOR POCKET 2 FLOW AI | l/s | WASTE |  | WASTE:E55122
13338 | #N/A | #N/A | #N/A | E55123 | 133380FILTERS TO ASP FEED PS FLOW AI | l/s | WASTE |  | WASTE:E55123
13338 | #N/A | #N/A | #N/A | E55125 | 133380ASP FEED PS FLOW AI | l/s | WASTE |  | WASTE:E55125
13338 | #N/A | #N/A | #N/A | E55140 | 133380ASP SAS FLOW | l/s | WASTE |  | WASTE:E55140
13338 | #N/A | #N/A | #N/A | E55392 | 133380DIRTY WATER FLOW AI | l/s | WASTE |  | WASTE:E55392
13338 | #N/A | #N/A | #N/A | E55399 | 133380WW LOWLIFT PS FLOW AI | l/s | WASTE |  | WASTE:E55399
13338 | #N/A | #N/A | #N/A | E55402 | 133380WW COMMON FLOW AI | l/s | WASTE |  | WASTE:E55402
13338 | #N/A | #N/A | #N/A | E55403 | 133380EA339MCERTS WW TOWN FLOW | l/s | WASTE |  | WASTE:E55403
13338 | #N/A | #N/A | #N/A | E55565 | 133380BIOFILTER RECIRC PS FLOW AI | l/s | WASTE |  | WASTE:E55565
13338 | #N/A | #N/A | #N/A | E55566 | 133380TASF FEED FLOW AI | l/s | WASTE |  | WASTE:E55566
13338 | #N/A | #N/A | #N/A | E55572 | 133380TASF FILTER 1 FLOW AI | l/s | WASTE |  | WASTE:E55572
13338 | #N/A | #N/A | #N/A | E55574 | 133380TASF FILTER 2 FLOW AI | l/s | WASTE |  | WASTE:E55574
13338 | #N/A | #N/A | #N/A | E55576 | 133380TASF FILTER 3 FLOW AI | l/s | WASTE |  | WASTE:E55576
13338 | #N/A | #N/A | #N/A | E55919 | 133380NABP INLET TO ASP FLOW | l/s | WASTE |  | WASTE:E55919
13338 | #N/A | #N/A | #N/A | E14514 | 133380INLET FLW FOR PMP SET 1 | l/s | WASTE |  | WASTE:E14514
13338 | #N/A | #N/A | #N/A | E14515 | 133380INLET FLW FOR PMP SET 2 | l/s | WASTE |  | WASTE:E14515
13339 | #N/A | #N/A | #N/A | E3255 | 133390EA207FINAL EFFLUENT OUTLET FLOW | l/s | WASTE |  | WASTE:E3255
13341 | #N/A | #N/A | #N/A | E3961 | 133410INLET FLOW | l/s | WASTE |  | WASTE:E3961
13342 | #N/A | #N/A | #N/A | E12990 | 133422SBR OUTLET FLOW STANDBY | l/s | WASTE |  | WASTE:E12990
13342 | #N/A | #N/A | #N/A | E12991 | 133422STORM FLOW | l/s | WASTE |  | WASTE:E12991
13342 | #N/A | #N/A | #N/A | E12992 | 133422SBR OUTLET FLOW | l/s | WASTE |  | WASTE:E12992
13342 | #N/A | #N/A | #N/A | E12993 | 133422BAND SCREEN 1 FLOW | l/s | WASTE |  | WASTE:E12993
13342 | #N/A | #N/A | #N/A | E12994 | 133422BAND SCREEN 2 FLOW | l/s | WASTE |  | WASTE:E12994
13342 | #N/A | #N/A | #N/A | E12995 | 133422BAND SCREEN 3 FLOW | l/s | WASTE |  | WASTE:E12995
13342 | #N/A | #N/A | #N/A | E12996 | 133422BAND SCREEN 4 FLOW | l/s | WASTE |  | WASTE:E12996
13342 | #N/A | #N/A | #N/A | E12997 | 133422EA208FLOW TO SBRS FLOWMETER 2 | l/s | WASTE |  | WASTE:E12997
13342 | #N/A | #N/A | #N/A | E13000 | 133422POTABLE WATER FLOW | l/s | WASTE |  | WASTE:E13000
13342 | #N/A | #N/A | #N/A | E13015 | 133422FLOW TO SBRS | l/s | WASTE |  | WASTE:E13015
13342 | #N/A | #N/A | #N/A | E13020 | 133422THICKENERS FLOW | l/s | WASTE |  | WASTE:E13020
13342 | #N/A | #N/A | #N/A | E13023 | 133422CENTRIFUGE FEED FLOW | l/s | WASTE |  | WASTE:E13023
13342 | #N/A | #N/A | #N/A | E25038 | 133422FE WASH WATER FLOW | l/s | WASTE |  | WASTE:E25038
13342 | #N/A | #N/A | #N/A | E25044 | 133422SLUDGE FLOW 1 | l/s | WASTE |  | WASTE:E25044
13342 | #N/A | #N/A | #N/A | E25045 | 133422SLUDGE FLOW 2 | l/s | WASTE |  | WASTE:E25045
13342 | #N/A | #N/A | #N/A | E25046 | 133422SLUDGE FLOW 3 | l/s | WASTE |  | WASTE:E25046
13342 | #N/A | #N/A | #N/A | E57976 | 13342BDRUM THICKENER FEED P1 FLOW | l/s | WASTE |  | WASTE:E57976
13342 | #N/A | #N/A | #N/A | E57977 | 13342BDRUM THICKENER FEED P2 FLOW | l/s | WASTE |  | WASTE:E57977
13342 | #N/A | #N/A | #N/A | E57978 | 13342BDRUM THICKENER FEED P3 FLOW | l/s | WASTE |  | WASTE:E57978
13342 | #N/A | #N/A | #N/A | E13018 | 133422FINAL EFFLUENT FLW | l/s | WASTE |  | WASTE:E13018
13345 | #N/A | #N/A | #N/A | E1590 | 133450EA209EFF OUTFLOW | l/s | WASTE |  | WASTE:E1590
13346 | #N/A | #N/A | #N/A | E2796 | 133460EA210FLOW TO WORKS | l/s | WASTE |  | WASTE:E2796
13346 | #N/A | #N/A | #N/A | E2806 | 133460TEMP RAS FLOW | l/s | WASTE |  | WASTE:E2806
13346 | #N/A | #N/A | #N/A | E23501 | 133460RAS FLOW | l/s | WASTE |  | WASTE:E23501
13346 | #N/A | #N/A | #N/A | E54395 | 133460INLET FLOWMETER 1 AI | l/s | WASTE |  | WASTE:E54395
13346 | #N/A | #N/A | #N/A | E54396 | 133460INLET FLOWMETER 2 AI | l/s | WASTE |  | WASTE:E54396
13346 | #N/A | #N/A | #N/A | E54401 | 133460SCREEN 1 WASHWATER FLOW AI | l/s | WASTE |  | WASTE:E54401
13346 | #N/A | #N/A | #N/A | E54402 | 133460SCREEN 2 WASHWATER FLOW AI | l/s | WASTE |  | WASTE:E54402
13346 | #N/A | #N/A | #N/A | E54403 | 133460LAUNDER CHANNEL WASHWATER FLOW AI | l/s | WASTE |  | WASTE:E54403
13346 | #N/A | #N/A | #N/A | E54404 | 133460COMPACTOR 1 AND 2 FLOW AI | l/s | WASTE |  | WASTE:E54404
13346 | #N/A | #N/A | #N/A | E54405 | 133460PISTA GRIT UNIT WASHWATER FLOW AI | l/s | WASTE |  | WASTE:E54405
13346 | #N/A | #N/A | #N/A | E54409 | 133460INLET DRAINAGE PS RETURN FLOW AI | l/s | WASTE |  | WASTE:E54409
13346 | #N/A | #N/A | #N/A | E54411 | 133460FLOW TO WORKS AI | l/s | WASTE |  | WASTE:E54411
13346 | #N/A | #N/A | #N/A | E54412 | 133460EA336WASHWATER MAIN DELIVERY FLOW AI | l/s | WASTE |  | WASTE:E54412
13346 | #N/A | #N/A | #N/A | E54417 | 133460RETURN PUMP FLOW | l/s | WASTE |  | WASTE:E54417
13347 | #N/A | #N/A | #N/A | E1185 | 133470INLET FLOW | l/s | WASTE |  | WASTE:E1185
13349 | #N/A | #N/A | #N/A | E9821 | 133490EA112FLOW TO FILTERS | l/s | WASTE |  | WASTE:E9821
13349 | #N/A | #N/A | #N/A | E9822 | 133490EA113FLOW TO AERATION | l/s | WASTE |  | WASTE:E9822
13349 | #N/A | #N/A | #N/A | E9825 | 133490STORM OVERFLOW TO RIVER | l/s | WASTE |  | WASTE:E9825
13349 | #N/A | #N/A | #N/A | E21008 | 133490UV FEED PUMP FLOW | l/s | WASTE |  | WASTE:E21008
13349 | #N/A | #N/A | #N/A | E21010 | 133490UV FLOW | l/s | WASTE |  | WASTE:E21010
13350 | #N/A | #N/A | #N/A | E10660 | 133500EA114TREATMENT FLOW | l/s | WASTE |  | WASTE:E10660
13350 | #N/A | #N/A | #N/A | E27563 | 133500IMPORT SLUDGE FLOW | l/s | WASTE |  | WASTE:E27563
13350 | #N/A | #N/A | #N/A | E56727 | 13350APROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E56727
13350 | #N/A | #N/A | #N/A | E56732 | 13350APUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E56732
13351 | #N/A | #N/A | #N/A | E9632 | 133510EA211MCERT FLOW | l/s | WASTE |  | WASTE:E9632
13351 | #N/A | #N/A | #N/A | E6953 | 13351ASTORM TANK 4 RETURN FLOW AI | l/s | WASTE2 |  | WASTE2:E6953
13351 | #N/A | #N/A | #N/A | E6958 | 13351ADIRTY BACKWASH RETURN FLOW AI | l/s | WASTE2 |  | WASTE2:E6958
13351 | #N/A | #N/A | #N/A | E6962 | 13351AMMF FEED FLOW AI | l/s | WASTE2 |  | WASTE2:E6962
13351 | #N/A | #N/A | #N/A | E6968 | 13351AWORKS FLOW AI | l/s | WASTE2 |  | WASTE2:E6968
13351 | #N/A | #N/A | #N/A | E6997 | 13351APROFILE STORM DOSING START FLOW | l/s | WASTE2 |  | WASTE2:E6997
13351 | #N/A | #N/A | #N/A | E7002 | 13351APUMP SET 1 SEWAGE FLOW | l/s | WASTE2 |  | WASTE2:E7002
13351 | #N/A | #N/A | #N/A | E7007 | 13351APUMP SET 2 SEWAGE FLOW | l/s | WASTE2 |  | WASTE2:E7007
13352 | #N/A | #N/A | #N/A | E3976 | 133520INLET FLOW | l/s | WASTE |  | WASTE:E3976
13352 | #N/A | #N/A | #N/A | E3977 | 133520MCERTS FLOW | l/s | WASTE |  | WASTE:E3977
13353 | #N/A | #N/A | #N/A | E18683 | 133531EA116FINAL FLOW | l/s | WASTE |  | WASTE:E18683
13353 | #N/A | #N/A | #N/A | E31728 | 133531DOSE SET 1 INLET FLOW | l/s | WASTE |  | WASTE:E31728
13353 | #N/A | #N/A | #N/A | E31729 | 133531DOSE SET 2 INLET FLOW | l/s | WASTE |  | WASTE:E31729
13353 | #N/A | #N/A | #N/A | E31736 | 133531EA364 MCERT BALANCE TK1 FLOW ANG | l/s | WASTE |  | WASTE:E31736
13353 | #N/A | #N/A | #N/A | E31737 | 133531EA364 MCERT BALANCE TK2 FLOW ANG | l/s | WASTE |  | WASTE:E31737
13353 | #N/A | #N/A | #N/A | E18689 | 133531RISING MAIN FLW LITTLE HANG LANGFORD | l/s | WASTE |  | WASTE:E18689
13354 | #N/A | #N/A | #N/A | E403 | 133540WIV GRAMPIAN FOODS FLOW OOR | l/s | WASTE |  | WASTE:E403
13354 | #N/A | #N/A | #N/A | E4646 | 133541EA118MCERT FLOW TO TREAT | l/s | WASTE |  | WASTE:E4646
13354 | #N/A | #N/A | #N/A | E4656 | 133541SAS FLOW MAX | l/s | WASTE |  | WASTE:E4656
13354 | #N/A | #N/A | #N/A | E4657 | 133541SAS FLOW MIN | l/s | WASTE |  | WASTE:E4657
13354 | #N/A | #N/A | #N/A | E4658 | 133541SAS FLOW OOR | l/s | WASTE |  | WASTE:E4658
13354 | #N/A | #N/A | #N/A | E4661 | 133541GRAMPION FOODS FLOW MAX | l/s | WASTE |  | WASTE:E4661
13354 | #N/A | #N/A | #N/A | E4662 | 133541GRAMPION FOODS FLOW MIN | l/s | WASTE |  | WASTE:E4662
13354 | #N/A | #N/A | #N/A | E4663 | 133541GRAMPION FOODS FLOW OOR | l/s | WASTE |  | WASTE:E4663
13354 | #N/A | #N/A | #N/A | E31510 | 133541FLOW FROM GRAMPIAN FOODS AI | l/s | WASTE |  | WASTE:E31510
13354 | #N/A | #N/A | #N/A | E31519 | 133541FFT FLOW MEASUREMENT FLOW AI | l/s | WASTE |  | WASTE:E31519
13354 | #N/A | #N/A | #N/A | E31539 | 133541RAS FLOW METER AI | l/s | WASTE |  | WASTE:E31539
13354 | #N/A | #N/A | #N/A | E31540 | 133541FFT FLOW METER AI | l/s | WASTE |  | WASTE:E31540
13354 | #N/A | #N/A | #N/A | E31541 | 133541SAS FLOWMETER AI | l/s | WASTE |  | WASTE:E31541
13354 | #N/A | #N/A | #N/A | E31556 | 133541POLY DOSING PUMP FLOW AI | l/s | WASTE |  | WASTE:E31556
13354 | #N/A | #N/A | #N/A | E31560 | 133541THICKENED SLUDGE FLOW AI | l/s | WASTE |  | WASTE:E31560
13355 | #N/A | #N/A | #N/A | E4937 | 133550STORM FLOW | l/s | WASTE |  | WASTE:E4937
13355 | #N/A | #N/A | #N/A | E4938 | 133550EA117MCERT FLOW | l/s | WASTE |  | WASTE:E4938
13358 | #N/A | #N/A | #N/A | E3270 | 133580EA119TREATMENT FLOW | l/s | WASTE |  | WASTE:E3270
13358 | #N/A | #N/A | #N/A | E3271 | 133580STORM FLOW | l/s | WASTE |  | WASTE:E3271
13358 | #N/A | #N/A | #N/A | E3272 | 133580RETURN SLUDGE FLOW | l/s | WASTE |  | WASTE:E3272
13358 | #N/A | #N/A | #N/A | E3274 | 133580INLET FLOW | l/s | WASTE |  | WASTE:E3274
13358 | #N/A | #N/A | #N/A | E3276 | 133580WASHWATER MCERT FLOW | l/s | WASTE |  | WASTE:E3276
13359 | #N/A | #N/A | #N/A | E22461 | 133591TRADE INLET FLOW | l/s | WASTE |  | WASTE:E22461
13359 | #N/A | #N/A | #N/A | E25185 | 133591COAG INLET FLOWMETER AN | l/s | WASTE |  | WASTE:E25185
13359 | #N/A | #N/A | #N/A | E25192 | 133591INLET LULWORTH FLOW | l/s | WASTE |  | WASTE:E25192
13359 | #N/A | #N/A | #N/A | E25199 | 133591ASP2 RAS FLOW AN | l/s | WASTE |  | WASTE:E25199
13359 | #N/A | #N/A | #N/A | E25200 | 133591ASP2 SAS FLOW AN | l/s | WASTE |  | WASTE:E25200
13359 | #N/A | #N/A | #N/A | E25207 | 133591ASP1 RAS FLOW AN | l/s | WASTE |  | WASTE:E25207
13359 | #N/A | #N/A | #N/A | E25208 | 133591ASP1 SAS FLOW AN | l/s | WASTE |  | WASTE:E25208
13359 | #N/A | #N/A | #N/A | E25225 | 133591SLUDGE FEED FLOW AN | l/s | WASTE |  | WASTE:E25225
13359 | #N/A | #N/A | #N/A | E25226 | 133591POLYMER FLOW AN | l/s | WASTE |  | WASTE:E25226
13359 | #N/A | #N/A | #N/A | E25227 | 133591SLUDGE TRANSFER FLOW AN | l/s | WASTE |  | WASTE:E25227
13359 | #N/A | #N/A | #N/A | E25228 | 133591DRUM RETURN FLOW AN | l/s | WASTE |  | WASTE:E25228
13359 | #N/A | #N/A | #N/A | E25229 | 133591TREATED EFFLUENT FLOW AN | l/s | WASTE |  | WASTE:E25229
13359 | #N/A | #N/A | #N/A | E29298 | 133591EAST BURTON FLOW | l/s | WASTE |  | WASTE:E29298
13360 | #N/A | #N/A | #N/A | E3115 | 133600INLET FLOW | l/s | WASTE |  | WASTE:E3115
13360 | #N/A | #N/A | #N/A | E6470 | 133600FLOCCULATOR INLET FLOW | l/s | WASTE |  | WASTE:E6470
13360 | #N/A | #N/A | #N/A | E26987 | 13360ASLUDGE THICKENER 1 FEED FLOW | l/s | WASTE |  | WASTE:E26987
13360 | #N/A | #N/A | #N/A | E26989 | 13360AEA273MCERTFLOW TO TREATMENT | l/s | WASTE |  | WASTE:E26989
13360 | #N/A | #N/A | #N/A | E26991 | 13360ASLUDGE THICKENER 2 FEED FLOW | l/s | WASTE |  | WASTE:E26991
13360 | #N/A | #N/A | #N/A | E27197 | 13360BINLET FLOW 1 AN | l/s | WASTE |  | WASTE:E27197
13360 | #N/A | #N/A | #N/A | E27496 | 13360CFILTER 1 FLOW AN | l/s | WASTE |  | WASTE:E27496
13360 | #N/A | #N/A | #N/A | E27501 | 13360CFILTER 2 FLOW AN | l/s | WASTE |  | WASTE:E27501
13360 | #N/A | #N/A | #N/A | E27505 | 13360CFILTER 3 FLOW AN | l/s | WASTE |  | WASTE:E27505
13360 | #N/A | #N/A | #N/A | E52811 | 133600SECONDARY DOSING SEWAGE FLOW | l/s | WASTE |  | WASTE:E52811
13360 | #N/A | #N/A | #N/A | E53127 | 133600POA FLOW RATE ANG | l/s | WASTE |  | WASTE:E53127
13360 | #N/A | #N/A | #N/A | E3120 | 133600FILTER 12 PS FLW | l/s | WASTE |  | WASTE:E3120
13360 | #N/A | #N/A | #N/A | E3122 | 133600FILTER 12 RECIRC PS FLW | l/s | WASTE |  | WASTE:E3122
13361 | #N/A | #N/A | #N/A | E1205 | 133610INLET FLOW | l/s | WASTE |  | WASTE:E1205
13361 | #N/A | #N/A | #N/A | E1207 | 133610EA252OUTLET FLOW | l/s | WASTE |  | WASTE:E1207
13364 | #N/A | #N/A | #N/A | E9648 | 133640FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E9648
13364 | #N/A | #N/A | #N/A | E97881 | 13364AMCERT FLOW ANG | l/s | WASTE |  | WASTE:E97881
13364 | #N/A | #N/A | #N/A | E97883 | 13364AINLET PUMPING STATION FLOW ANG | l/s | WASTE |  | WASTE:E97883
13364 | #N/A | #N/A | #N/A | E97890 | 13364ASAF FEED FLOW ANG | l/s | WASTE |  | WASTE:E97890
13364 | #N/A | #N/A | #N/A | E97893 | 13364AWORKS RETURN PUMPING STATION FLOW ANG | l/s | WASTE |  | WASTE:E97893
13364 | #N/A | #N/A | #N/A | E97929 | 13364BPROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E97929
13364 | #N/A | #N/A | #N/A | E97934 | 13364BPUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E97934
13366 | #N/A | #N/A | #N/A | E2615 | 133660FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E2615
13366 | #N/A | #N/A | #N/A | E2620 | 133660H R F FLOW | l/s | WASTE |  | WASTE:E2620
13366 | #N/A | #N/A | #N/A | E35659 | 133660HRF 1 PS FLOW ANG | l/s | WASTE |  | WASTE:E35659
13366 | #N/A | #N/A | #N/A | E35662 | 133660HRF 2 PS FLOW ANG | l/s | WASTE |  | WASTE:E35662
13366 | #N/A | #N/A | #N/A | E35687 | 133660FILTER FEED FLOW 1 | l/s | WASTE |  | WASTE:E35687
13366 | #N/A | #N/A | #N/A | E35698 | 133660FILTER FEED FLOW 2 | l/s | WASTE |  | WASTE:E35698
13366 | #N/A | #N/A | #N/A | E35856 | 133660COAG DOSING HRF 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E35856
13366 | #N/A | #N/A | #N/A | E35863 | 133660COAG DOSING HRF 2 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E35863
13366 | #N/A | #N/A | #N/A | E36017 | 133660HRF 1 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E36017
13366 | #N/A | #N/A | #N/A | E36024 | 133660HRF 2 HIGH SEWAGE FLOW SETPOINT | l/s | WASTE |  | WASTE:E36024
13367 | #N/A | #N/A | #N/A | E2593 | 133670FLOW TO DIGESTER 1 | l/s | WASTE |  | WASTE:E2593
13367 | #N/A | #N/A | #N/A | E2594 | 133670FLOW TO DIGESTER 2 | l/s | WASTE |  | WASTE:E2594
13367 | #N/A | #N/A | #N/A | E2596 | 133670FLOW TO DIGESTER 3 | l/s | WASTE |  | WASTE:E2596
13367 | #N/A | #N/A | #N/A | E2608 | 133670SLUDGE FLOW ONTO BELTPRESS | l/s | WASTE |  | WASTE:E2608
13367 | #N/A | #N/A | #N/A | E2609 | 133670WASH WATER FLOW ONTO BELTPRESS | l/s | WASTE |  | WASTE:E2609
13367 | #N/A | #N/A | #N/A | E39885 | 133670WW BSTR PUMPS FLOW AI | l/s | WASTE |  | WASTE:E39885
13367 | #N/A | #N/A | #N/A | E50021 | 133670LIQUOR PLANT FEED FLOW | l/s | WASTE |  | WASTE:E50021
13367 | #N/A | #N/A | #N/A | E50022 | 133670LIQUOR PLANT RETURN FLOW | l/s | WASTE |  | WASTE:E50022
13368 | #N/A | #N/A | #N/A | E2640 | 133680EA214INLET FLOW | l/s | WASTE |  | WASTE:E2640
13368 | #N/A | #N/A | #N/A | E2642 | 133680MAX INLET FLOW | l/s | WASTE |  | WASTE:E2642
13368 | #N/A | #N/A | #N/A | E2643 | 133680MIN INLET FLOW | l/s | WASTE |  | WASTE:E2643
13469 | #N/A | #N/A | #N/A | E3373 | 134690RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E3373
13514 | #N/A | #N/A | #N/A | E4966 | 135140EA286FINAL OUTFLOW | l/s | WASTE |  | WASTE:E4966
13514 | #N/A | #N/A | #N/A | E29218 | 135140MAX FINAL OUTFLOW | l/s | WASTE |  | WASTE:E29218
13514 | #N/A | #N/A | #N/A | E29219 | 135140MIN FINAL OUTFLOW | l/s | WASTE |  | WASTE:E29219
13515 | #N/A | #N/A | #N/A | E5859 | 135150EA240 TRANS PUMP FLOW AN | l/s | WASTE |  | WASTE:E5859
13515 | #N/A | #N/A | #N/A | E5860 | 135150OUTFALL FLOW AN | l/s | WASTE |  | WASTE:E5860
13515 | #N/A | #N/A | #N/A | E5861 | 135150TIDAL OUTLET FLOW AN | l/s | WASTE |  | WASTE:E5861
13515 | #N/A | #N/A | #N/A | E5876 | 135150TNK 1 PERMEATE FLOW AN | l/s | WASTE |  | WASTE:E5876
13515 | #N/A | #N/A | #N/A | E5878 | 135150TNK 2 PERMEATE FLOW AN | l/s | WASTE |  | WASTE:E5878
13515 | #N/A | #N/A | #N/A | E5883 | 135150TNK 3 PERMEATE FLOW AN | l/s | WASTE |  | WASTE:E5883
13515 | #N/A | #N/A | #N/A | E5885 | 135150TNK 4 PERMEATE FLOW AN | l/s | WASTE |  | WASTE:E5885
13515 | #N/A | #N/A | #N/A | E5931 | 135150OUTLET FLOW | l/s | WASTE |  | WASTE:E5931
13515 | #N/A | #N/A | #N/A | E55264 | 135150OUTFALL FLOW V NOTCH WEIR AI | l/s | WASTE |  | WASTE:E55264
13515 | #N/A | #N/A | #N/A | E55291 | 135150MBR TANKS 1 AND 3 DIFFUSER WASH FLOW AI | l/s | WASTE |  | WASTE:E55291
13515 | #N/A | #N/A | #N/A | E55292 | 135150MBR TANKS 2 AND 4 DIFFUSER WASH FLOW AI | l/s | WASTE |  | WASTE:E55292
13515 | #N/A | #N/A | #N/A | E55301 | 135150MBR T1 MODULE A PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55301
13515 | #N/A | #N/A | #N/A | E55302 | 135150MBR T1 MODULE B PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55302
13515 | #N/A | #N/A | #N/A | E55303 | 135150MBR T1 MODULE C PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55303
13515 | #N/A | #N/A | #N/A | E55304 | 135150MBR T1 MODULE D PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55304
13515 | #N/A | #N/A | #N/A | E55305 | 135150MBR T1 MODULE E PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55305
13515 | #N/A | #N/A | #N/A | E55306 | 135150MBR T1 MODULE F PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55306
13515 | #N/A | #N/A | #N/A | E55307 | 135150MBR T1 PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55307
13515 | #N/A | #N/A | #N/A | E55308 | 135150MBR T2 MODULE A PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55308
13515 | #N/A | #N/A | #N/A | E55309 | 135150MBR T2 MODULE B PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55309
13515 | #N/A | #N/A | #N/A | E55310 | 135150MBR T2 MODULE C PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55310
13515 | #N/A | #N/A | #N/A | E55311 | 135150MBR T2 MODULE D PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55311
13515 | #N/A | #N/A | #N/A | E55312 | 135150MBR T2 MODULE E PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55312
13515 | #N/A | #N/A | #N/A | E55313 | 135150MBR T2 MODULE F PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55313
13515 | #N/A | #N/A | #N/A | E55314 | 135150MBR T2 PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55314
13515 | #N/A | #N/A | #N/A | E55315 | 135150MBR T3 MODULE A PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55315
13515 | #N/A | #N/A | #N/A | E55316 | 135150MBR T3 MODULE B PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55316
13515 | #N/A | #N/A | #N/A | E55317 | 135150MBR T3 MODULE C PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55317
13515 | #N/A | #N/A | #N/A | E55318 | 135150MBR T3 MODULE D PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55318
13515 | #N/A | #N/A | #N/A | E55319 | 135150MBR T3 MODULE E PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55319
13515 | #N/A | #N/A | #N/A | E55320 | 135150MBR T3 MODULE F PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55320
13515 | #N/A | #N/A | #N/A | E55321 | 135150MBR T3 PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55321
13515 | #N/A | #N/A | #N/A | E55322 | 135150MBR T4 MODULE A PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55322
13515 | #N/A | #N/A | #N/A | E55323 | 135150MBR T4 MODULE B PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55323
13515 | #N/A | #N/A | #N/A | E55324 | 135150MBR T4 MODULE C PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55324
13515 | #N/A | #N/A | #N/A | E55325 | 135150MBR T4 MODULE D PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55325
13515 | #N/A | #N/A | #N/A | E55326 | 135150MBR T4 MODULE E PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55326
13515 | #N/A | #N/A | #N/A | E55327 | 135150MBR T4 MODULE F PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55327
13515 | #N/A | #N/A | #N/A | E55328 | 135150MBR T4 PERMEATE FLOW AI | l/s | WASTE |  | WASTE:E55328
13515 | #N/A | #N/A | #N/A | E5862 | 135150DESLDG FLW TO STORE TNKS | l/s | WASTE |  | WASTE:E5862
13516 | #N/A | #N/A | #N/A | E12142 | 135160BELT THICKENER FEED FLOW | l/s | WASTE |  | WASTE:E12142
13522 | #N/A | #N/A | #N/A | E11360 | 135220EA059FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E11360
13522 | #N/A | #N/A | #N/A | E11362 | 135220MICROSCREEN FLOW | l/s | WASTE |  | WASTE:E11362
13522 | #N/A | #N/A | #N/A | E11366 | 135220SAF 1 INLET FLOW | l/s | WASTE |  | WASTE:E11366
13522 | #N/A | #N/A | #N/A | E11367 | 135220SAF 2 INLET FLOW | l/s | WASTE |  | WASTE:E11367
13522 | #N/A | #N/A | #N/A | E52573 | 135220PUMP SET 1 SEWAGE FLOW ANG | l/s | WASTE |  | WASTE:E52573
13522 | #N/A | #N/A | #N/A | E52580 | 135220PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E52580
13591 | #N/A | #N/A | #N/A | E3391 | 135910RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E3391
13593 | #N/A | #N/A | #N/A | E6018 | 135930RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6018
13594 | #N/A | #N/A | #N/A | E3382 | 135940FORGE HOUSE RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E3382
13594 | #N/A | #N/A | #N/A | E3383 | 135940BRENT KNOLL RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E3383
13595 | #N/A | #N/A | #N/A | E6027 | 135950RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6027
13596 | #N/A | #N/A | #N/A | E6036 | 135960RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6036
13597 | #N/A | #N/A | #N/A | E6045 | 135970RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6045
13598 | #N/A | #N/A | #N/A | E6063 | 135980RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6063
13599 | #N/A | #N/A | #N/A | E6081 | 135990RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6081
13612 | #N/A | #N/A | #N/A | E6072 | 136120RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6072
13632 | #N/A | #N/A | #N/A | E6009 | 136320RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6009
13667 | #N/A | #N/A | #N/A | E6157 | 13667ARISING MAIN FLOW AI | l/s | WASTE2 |  | WASTE2:E6157
13667 | #N/A | #N/A | #N/A | E6159 | 13667ARISING MAIN FLOW SETPOINT AI | l/s | WASTE2 |  | WASTE2:E6159
13676 | #N/A | #N/A | #N/A | E6099 | 136760RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6099
13677 | #N/A | #N/A | #N/A | E6108 | 136770RISING MAIN FLOWMETER ANLG | l/s | WASTE2 |  | WASTE2:E6108
13728 | #N/A | #N/A | #N/A | E4092 | 137280RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E4092
13729 | #N/A | #N/A | #N/A | E4164 | 137290RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E4164
13730 | #N/A | #N/A | #N/A | E4068 | 137300RISING MAIN FLOW 1 | l/s | WASTE2 |  | WASTE2:E4068
13730 | #N/A | #N/A | #N/A | E4069 | 137300RISING MAIN FLOW 2 | l/s | WASTE2 |  | WASTE2:E4069
13743 | #N/A | #N/A | #N/A | E4116 | 137430RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E4116
13755 | #N/A | #N/A | #N/A | E4140 | 137550RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E4140
13880 | #N/A | #N/A | #N/A | E7245 | 138800RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E7245
13886 | #N/A | #N/A | #N/A | E7269 | 138860RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E7269
13887 | #N/A | #N/A | #N/A | E7293 | 138870RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E7293
13888 | #N/A | #N/A | #N/A | E7317 | 138880RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E7317
13889 | #N/A | #N/A | #N/A | E7341 | 138890RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E7341
14031 | #N/A | #N/A | #N/A | E7850 | 140310RISING MAIN FLOW ANG | l/s | WASTE2 |  | WASTE2:E7850
14810 | #N/A | #N/A | #N/A | E8138 | 148100RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E8138
14811 | #N/A | #N/A | #N/A | E8114 | 148110RISING MAIN FLOW | l/s | WASTE2 |  | WASTE2:E8114
17062 | #N/A | #N/A | #N/A | E24115 | 170620UV FLOW | l/s | WASTE |  | WASTE:E24115
17081 | #N/A | #N/A | #N/A | E24262 | 170811FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E24262
17081 | #N/A | #N/A | #N/A | E24271 | 170811PUMPED FLOW | l/s | WASTE |  | WASTE:E24271
17258 | #N/A | #N/A | #N/A | E26038 | 172580INLET FLOW | l/s | WASTE |  | WASTE:E26038
17375 | #N/A | #N/A | #N/A | E30488 | 173750EA278FINAL EFF DISCHARGE FLOW ANG | l/s | WASTE |  | WASTE:E30488
17375 | #N/A | #N/A | #N/A | E30496 | 173750EA359FPF MCERTS FLOW METER ANALOGUE INPUT | l/s | WASTE |  | WASTE:E30496
17430 | #N/A | #N/A | #N/A | E31135 | 174300FE DISCHARGE FLOW ANG | l/s | WASTE |  | WASTE:E31135
17430 | #N/A | #N/A | #N/A | E31286 | 174300EA279PUMPING STN MCERT FLOW | l/s | WASTE |  | WASTE:E31286
17549 | #N/A | #N/A | #N/A | E32975 | 175490SAF FLOW ANLG | l/s | WASTE |  | WASTE:E32975
17968 | #N/A | #N/A | #N/A | E50440 | 179680EA288MCERT FLOW ANG | l/s | WASTE |  | WASTE:E50440
17968 | #N/A | #N/A | #N/A | E96443 | 17968APROFILE STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E96443
17968 | #N/A | #N/A | #N/A | E96448 | 17968APUMP SET 1 SEWAGE FLOW | l/s | WASTE |  | WASTE:E96448
19031 | #N/A | #N/A | #N/A | E55637 | 190310EA010MCERTS INLET SCREEN FLOW AI | l/s | WASTE |  | WASTE:E55637
19031 | #N/A | #N/A | #N/A | E55641 | 190310MECANA FEED FLOW AI | l/s | WASTE |  | WASTE:E55641
19031 | #N/A | #N/A | #N/A | E55654 | 190310PUMP SET 1 SEWAGE FLOW AI | l/s | WASTE |  | WASTE:E55654
19031 | #N/A | #N/A | #N/A | E55662 | 190310PUMP SET 1 STORM DOSING START FLOW | l/s | WASTE |  | WASTE:E55662
19155 | #N/A | #N/A | #N/A | E10350 | 191550RECIRC FLOW | l/s | WASTE |  | WASTE:E10350
19155 | #N/A | #N/A | #N/A | E10361 | 191550EA325MCERT INLT SHAFT FLOW 1 | l/s | WASTE |  | WASTE:E10361
19155 | #N/A | #N/A | #N/A | E10362 | 191550EA326MCERT INLT SHAFT FLOW 2 | l/s | WASTE |  | WASTE:E10362
19155 | #N/A | #N/A | #N/A | E10363 | 191550EA327MCERT MERRYBEE FLOW | l/s | WASTE |  | WASTE:E10363
19155 | #N/A | #N/A | #N/A | E13178 | 191550CERTIFIED FLOW | l/s | WASTE |  | WASTE:E13178
19155 | #N/A | #N/A | #N/A | E13183 | 191550COMBINED FFT FLOW | l/s | WASTE |  | WASTE:E13183
19155 | #N/A | #N/A | #N/A | E34717 | 191550SETTLED SEWAGE PS OUTLET FLOW AI | l/s | WASTE |  | WASTE:E34717
19155 | #N/A | #N/A | #N/A | E34736 | 191550RAS PUMPS FLOWMETER AI | l/s | WASTE |  | WASTE:E34736
19155 | #N/A | #N/A | #N/A | E34737 | 191550SAS PUMPS FLOWMETER AI | l/s | WASTE |  | WASTE:E34737
19155 | #N/A | #N/A | #N/A | E34795 | 191550STORM PUMPS 4 TO 6 FLOW | l/s | WASTE |  | WASTE:E34795
19155 | #N/A | #N/A | #N/A | E34799 | 191550STORM PUMPS 1 TO 3 FLOW | l/s | WASTE |  | WASTE:E34799
19155 | #N/A | #N/A | #N/A | E34807 | 191550NEW UV PLANT FLOW ANG | l/s | WASTE |  | WASTE:E34807
19155 | #N/A | #N/A | #N/A | E13177 | 191550RETURN FLW TO BLACK ROCK | l/s | WASTE |  | WASTE:E13177
19156 | #N/A | #N/A | #N/A | E8532 | 191560EA014FLOW TO TREATMENT | l/s | WASTE |  | WASTE:E8532
19156 | #N/A | #N/A | #N/A | E8538 | 191560WORKS DRAIN RETURN FLOW | l/s | WASTE |  | WASTE:E8538
19156 | #N/A | #N/A | #N/A | E8539 | 191560INTERMEDIATE PUMPED FLOW | l/s | WASTE |  | WASTE:E8539
19156 | #N/A | #N/A | #N/A | E52869 | 191560COAG FLOW ACCUMULATOR | l/s | WASTE |  | WASTE:E52869
19539 | #N/A | #N/A | #N/A | E12562 | 195390STORM OVERFLOW SCRN FLW | l/s | WASTE |  | WASTE:E12562
19539 | #N/A | #N/A | #N/A | E12573 | 195390EA215MCERT FLOW TO SBR | l/s | WASTE |  | WASTE:E12573
19539 | #N/A | #N/A | #N/A | E12594 | 195390EDM STORM OFLOW | l/s | WASTE |  | WASTE:E12594
19539 | #N/A | #N/A | #N/A | E12595 | 195390STORM TRANSFER FLOW | l/s | WASTE |  | WASTE:E12595
19539 | #N/A | #N/A | #N/A | E12596 | 195390EA369MCERT FLOW TO SBRS | l/s | WASTE |  | WASTE:E12596
19539 | #N/A | #N/A | #N/A | E25488 | 195390POLY DOSING PUMP 1 FLOW | l/s | WASTE |  | WASTE:E25488
19539 | #N/A | #N/A | #N/A | E25489 | 195390DRUM THKNR FEED PMP1 FLOW | l/s | WASTE |  | WASTE:E25489
19539 | #N/A | #N/A | #N/A | E25493 | 195390POLY DOSING PUMP 2 FLOW | l/s | WASTE |  | WASTE:E25493
19539 | #N/A | #N/A | #N/A | E25494 | 195390DRUM THKNR FEED PMP2 FLOW | l/s | WASTE |  | WASTE:E25494
19539 | #N/A | #N/A | #N/A | E12562 | 195390STORM OVERFLOW SCRN FLW | l/s | WASTE |  | WASTE:E12562
19541 | #N/A | #N/A | #N/A | E11410 | 195410MBBR FLOW | l/s | WASTE |  | WASTE:E11410
19541 | #N/A | #N/A | #N/A | E12157 | 195410VERIFICATION FLOW MONITOR | l/s | WASTE |  | WASTE:E12157
19541 | #N/A | #N/A | #N/A | E12164 | 195410INL OUTFALL PS FLOW | l/s | WASTE |  | WASTE:E12164
19541 | #N/A | #N/A | #N/A | E12165 | 195410INL TUNNEL PUMP FLOW | l/s | WASTE |  | WASTE:E12165
19541 | #N/A | #N/A | #N/A | E12167 | 195410EA196MCERT INL DWF TO MEMB FLOW | l/s | WASTE |  | WASTE:E12167
19541 | #N/A | #N/A | #N/A | E12171 | 195410INL PERM TO OUTFALL FLOW | l/s | WASTE |  | WASTE:E12171
19541 | #N/A | #N/A | #N/A | E12219 | 195410MEM AERATION TANK 1 FLOW | l/s | WASTE |  | WASTE:E12219
19541 | #N/A | #N/A | #N/A | E12224 | 195410MEM PROSPECT FM SLG FLOW | l/s | WASTE |  | WASTE:E12224
19541 | #N/A | #N/A | #N/A | E12225 | 195410UV PLANT UV FLOW | l/s | WASTE |  | WASTE:E12225
19541 | #N/A | #N/A | #N/A | E12226 | 195410MEM AERATION TANK 3 FLOW | l/s | WASTE |  | WASTE:E12226
19541 | #N/A | #N/A | #N/A | E12230 | 195410MEM AERATION TANK 4 FLOW | l/s | WASTE |  | WASTE:E12230
19541 | #N/A | #N/A | #N/A | E12234 | 195410MEM AERATION TANK 5 FLOW | l/s | WASTE |  | WASTE:E12234
19541 | #N/A | #N/A | #N/A | E12238 | 195410MEM AERATION TANK 6 FLOW | l/s | WASTE |  | WASTE:E12238
19541 | #N/A | #N/A | #N/A | E54949 | 195410SCREEN FEED FLOW AI | l/s | WASTE |  | WASTE:E54949
19541 | #N/A | #N/A | #N/A | E54951 | 195410PARABOLIC SCRN SLG DISCHARGE FLOW AI | l/s | WASTE |  | WASTE:E54951
19541 | #N/A | #N/A | #N/A | E54953 | 195410RECIRCULATION TANK FEED FLOW AI | l/s | WASTE |  | WASTE:E54953
19541 | #N/A | #N/A | #N/A | E54955 | 195410RECIRCULATION FLOW AI | l/s | WASTE |  | WASTE:E54955
19541 | #N/A | #N/A | #N/A | E54956 | 195410PERMEATE DISCHARGE FLOW AI | l/s | WASTE |  | WASTE:E54956
19541 | #N/A | #N/A | #N/A | E54963 | 195410BACKWASH FLOW AI | l/s | WASTE |  | WASTE:E54963
19541 | #N/A | #N/A | #N/A | E54971 | 195410MBBR UV FINAL EFFLUENT FLOWMETER AI | l/s | WASTE |  | WASTE:E54971
19541 | #N/A | #N/A | #N/A | E12184 | 195410INL NA OH SCB REC TK FLW | l/s | WASTE |  | WASTE:E12184
19556 | #N/A | #N/A | #N/A | E12813 | 195560STORM FLOW TO RIVER | l/s | WASTE |  | WASTE:E12813
19556 | #N/A | #N/A | #N/A | E12822 | 195560EA246FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E12822
19556 | #N/A | #N/A | #N/A | E12826 | 195560MAG FLOW METER | l/s | WASTE |  | WASTE:E12826
19556 | #N/A | #N/A | #N/A | E50265 | 195560SF FLOW | l/s | WASTE |  | WASTE:E50265
19685 | #N/A | #N/A | #N/A | E9525 | 196850STORM OVERFLOW | l/s | WASTE |  | WASTE:E9525
19685 | #N/A | #N/A | #N/A | E9526 | 196850EA254FINAL EFFLUENT FLOW | l/s | WASTE |  | WASTE:E9526
19705 | #N/A | #N/A | #N/A | E12350 | 197051INLET FLOW | l/s | WASTE |  | WASTE:E12350
19705 | #N/A | #N/A | #N/A | E12355 | 197051TREATED EFFLUENT FLOW | l/s | WASTE |  | WASTE:E12355
19705 | #N/A | #N/A | #N/A | E12356 | 197051STORM OVERFLOW EFFLUENT | l/s | WASTE |  | WASTE:E12356
19705 | #N/A | #N/A | #N/A | E12357 | 197051ST REGIS PAPER MILL FLOW | l/s | WASTE |  | WASTE:E12357
19705 | #N/A | #N/A | #N/A | E12377 | 197051FLOW TO SBRS | l/s | WASTE |  | WASTE:E12377
19705 | #N/A | #N/A | #N/A | E12385 | 197051SBR SAS FLOW | l/s | WASTE |  | WASTE:E12385
19705 | #N/A | #N/A | #N/A | E12386 | 197051PLC1 SBR OUTLET FLOW | l/s | WASTE |  | WASTE:E12386
19705 | #N/A | #N/A | #N/A | E12351 | 197051EA249FLW TO TREATMENT | l/s | WASTE |  | WASTE:E12351
23267 | #N/A | #N/A | #N/A | E12462 | 232671FLOW TO SEWER | l/s | WASTE |  | WASTE:E12462
23267 | #N/A | #N/A | #N/A | E31666 | 232671POST DISCHARGE FLOW REAL VALUE | l/s | WASTE |  | WASTE:E31666
25104 | #N/A | #N/A | #N/A | E1752 | 251040INFLOW RATE | l/s | WASTE2 |  | WASTE2:E1752
30007 | #N/A | #N/A | #N/A | E5448 | 30007CSO FLOW | l/s | WASTE2 |  | WASTE2:E5448
50275 | #N/A | #N/A | #N/A | E38188 | 502750DISCHAGE FLOW | l/s | WASTE |  | WASTE:E38188
50417 | #N/A | #N/A | #N/A | E26647 | 504170EFFLUENT FLOW | l/s | WASTE |  | WASTE:E26647
50666 | #N/A | #N/A | #N/A | E25949 | 506660LEACHATE FLOW | l/s | WASTE |  | WASTE:E25949
51329 | #N/A | #N/A | #N/A | E3286 | 513290EFFLUENT FLOW | l/s | WASTE2 |  | WASTE2:E3286
51329 | #N/A | #N/A | #N/A | E10068 | 513291EFFLUENT FLOW | l/s | WASTE2 |  | WASTE2:E10068
51359 | #N/A | #N/A | #N/A | E3315 | 513590DISCHARGE FLOW | l/s | WASTE2 |  | WASTE2:E3315
14174 | BOX | MILL LANE | BOX MILL LANE | E8881 | 130290INLET FLOW 1 | l/s | WASTE | Y | WASTE:E8881

## All sites
SiteId | Site Name | Site Description | Division | Site Type | Status
10010 | SOMERTON | BEHIND BERRY | W | Private Sewage Pumping Station | INUSE
10011 | TROWBRIDGE | BOWYERS FACTORY CULVERT | N | Combined Sewer Overflow | INUSE
10019 | UPPER MINETY | TELLINGS ORCHARD | N | S105A Sewage Pumping Station | INUSE
10025 | VERWOOD | DUKES COURT | S | S105A Sewage Pumping Station | INUSE
10038 | SHAFTESBURY | BLEKE STREET | S | S105A Sewage Pumping Station | INUSE
10043 | CHILTON POLDEN | SMALLWAYS LANE | W | S105A Sewage Pumping Station | INUSE
10044 | SOPWORTH | SANDY FARM | N | Private Sewage Pumping Station | INUSE
10045 | BINEGAR | 2 DOUGLAS COURT | W | S105A Sewage Pumping Station | INUSE
10046 | CORFE MULLEN | CORFE VIEW ROAD | S | S105A Sewage Pumping Station | INUSE
10049 | BOURNEMOUTH | ALUMHURST ROAD | S | S105A Sewage Pumping Station | INUSE
10050 | WOTTON-UNDER-EDGE | CANONS COURT MEWS 2 | N | S105A Sewage Pumping Station | INUSE
10053 | CHEW MAGNA | LIMEBURN HILL | N | Sewage Pumping Station | INUSE
10061 | MATCHAMS | HURN ROAD NEW FOREST MOTEL | S | Private Sewage Pumping Station | INUSE
10063 | TROWBRIDGE | TOWN BRIDGE | N | Combined Sewer Overflow | Unknown
10064 | EAST HUNTSPILL | CROWN INN CHURCH ROAD | W | Sewage Pumping Station | INUSE
10066 | CASTLE COMBE | NEAR PREEDY COTTAGE | N | Sewage Pumping Station | INUSE
10067 | BRISTOL | KINGDOM VIEW FOUL 1 | N | Private Sewage Pumping Station | INUSE
10068 | BRISTOL | KINGDOM VIEW FOUL 2 | N | Private Sewage Pumping Station | INUSE
10069 | BRISTOL | KINGDOM VIEW SURFACE 1 | N | Private Sewage Pumping Station | INUSE
10073 | WEYMOUTH | LITTLESEA HOLIDAY PARK | S | Private Sewage Pumping Station | INUSE
10074 | DORCHESTER | MAX GATE | S | Private Sewage Pumping Station | INUSE
10075 | EAST KNOYLE | UPTON FARM | S | Private Sewage Pumping Station | INUSE
10076 | COLERNE | ST. JOHN THE BAPTIST CHURCH | N | Private Sewage Pumping Station | INUSE
10079 | TAUNTON | MOUNTFIELDS ROAD | W | Private Sewage Pumping Station | INUSE
10080 | KNOWLE | THE KNOWLE INN | W | S105A Sewage Pumping Station | INUSE
10083 | BATH | 22 DARLINGTON PLACE | N | Private Sewage Pumping Station | INUSE
10084 | BRISTOL | EASTMEAD LANE | N | Private Sewage Pumping Station | INUSE
10085 | HANHAM | CENTRAL AVENUE | N | Private Sewage Pumping Station | INUSE
10092 | CLEVEDON | STRODE COURT 1 | W | Private Sewage Pumping Station | INUSE
10093 | CLEVEDON | STRODE COURT 2 | W | Private Sewage Pumping Station | INUSE
10095 | BOURNEMOUTH | BOSCOMBE SPA ROAD | S | Private Sewage Pumping Station | INUSE
10098 | POOLE | ALMOND CLOSE | S | S105A Sewage Pumping Station | INUSE
10105 | WELLINGTON | HAM ROAD | S | Private Sewage Pumping Station | INUSE
10126 | WEYMOUTH | SPA ROAD | S | Private Sewage Pumping Station | INUSE
10127 | BRADFORD-ON-AVON | KINGSTON ROAD | N | Private Sewage Pumping Station | INUSE
10128 | BITTON | WALL TYNING GARDENS | N | S105A Sewage Pumping Station | INUSE
10129 | POOLE | CANFORD CLIFFS ROAD NO 150 | S | Private Sewage Pumping Station | INUSE
10131 | EYPE | 1 MOUNT COTTAGES | S | Private Sewage Pumping Station | INUSE
10132 | SEEND | THE STOCKS | N | Private Sewage Pumping Station | INUSE
10133 | SALISBURY | THE CLOSE | S | S105A Sewage Pumping Station | INUSE
10134 | LONG SUTTON | GOLF CLUB | W | Private Sewage Pumping Station | INUSE
10137 | MALMESBURY | SCHOOL | N | Private Sewage Pumping Station | INUSE
10139 | BATH | CRESCENT LANE | N | S105A Sewage Pumping Station | INUSE
10140 | NAILSEA | GREENFIELD CRESCENT | W | Private Sewage Pumping Station | INUSE
10141 | WARMINSTER | COPHEAP LANE | N | S105A Sewage Pumping Station | INUSE
10142 | SYNWELL | KNAPP ROAD | N | S105A Sewage Pumping Station | INUSE
10143 | WARMINSTER | FORAGE LANE | N | S105A Sewage Pumping Station | INUSE
10144 | YEOVIL | HATHERMEAD GARDENS | W | S105A Sewage Pumping Station | INUSE
10146 | CREWKERNE | BIRDS CLOSE | W | S105A Sewage Pumping Station | INUSE
10147 | SOMERTON | LEFFMAN COURT | W | S105A Sewage Pumping Station | INUSE
10148 | BRIDGWATER | CANAL SIDE | W | S105A Sewage Pumping Station | INUSE
10153 | EAST LULWORTH | SHAGGS | S | Private Sewage Pumping Station | INUSE
10155 | COOMBE KEYNES | NEWTOWN HILL | S | Private Sewage Pumping Station | INUSE
10156 | STEEPLE | BLACKMANSTON COTTAGES | S | Private Sewage Pumping Station | INUSE
10157 | POOLE | TILLINGBOURNE COURT | S | Private Sewage Pumping Station | INUSE
10159 | WEST MOORS | 12A HARDY CLOSE | S | Private Sewage Pumping Station | INUSE
10161 | HORTON | HAYTHORNE COMMON | S | Private Sewage Pumping Station | INUSE
10163 | WOODLANDS | HILLSIDE WALK | S | Private Sewage Pumping Station | INUSE
10164 | CLEVEDON | CHANNEL ROAD | W | S105A Sewage Pumping Station | INUSE
10165 | POOLE | RINGWOOD ROAD | S | S105A Sewage Pumping Station | INUSE
10166 | MILTON ABBAS | ST JAMES CHURCH | S | Private Sewage Pumping Station | INUSE
10167 | LONGBURTON | 4 WHISTLE WATER | W | Private Sewage Pumping Station | INUSE
10168 | LONGBURTON | 5 WHISTLE WATER | W | Private Sewage Pumping Station | INUSE
10172 | BOVINGTON | CAMP | S | Private Sewage Pumping Station | INUSE
10173 | CHARD | HOCKEN CLOSE | W | S105A Sewage Pumping Station | INUSE
10175 | WESTON-SUPER-MARE | 51A CLIFF ROAD | W | Private Sewage Pumping Station | INUSE
10176 | MARNHULL | LOVELLS PLACE | S | S105A Sewage Pumping Station | INUSE
10178 | GILLINGHAM | RIVER VIEW | S | S105A Sewage Pumping Station | INUSE
10179 | YATTON KEYNELL | CROWN INN | N | S105A Sewage Pumping Station | INUSE
10180 | WINTERBOURNE | LITTLE ACRE | N | S105A Sewage Pumping Station | INUSE
10181 | BRISTOL | THE HOLLIES | N | S105A Sewage Pumping Station | INUSE
10182 | TISBURY | WARDOUR | S | S105A Sewage Pumping Station | INUSE
10183 | BATHAMPTON | HARBUTTS | N | S105A Sewage Pumping Station | INUSE
10185 | WEST LYDFORD | OLD SCHOOL LANE | W | S105A Sewage Pumping Station | INUSE
10186 | PORTLAND | DELHI LANE | S | Private Sewage Pumping Station | INUSE
10188 | DOWNTON | WEST WICK | S | S105A Sewage Pumping Station | INUSE
10189 | TISBURY | PARSONAGE MEAD | S | S105A Sewage Pumping Station | INUSE
10190 | BROADSTONE | AIRETONS CLOSE | S | S105A Sewage Pumping Station | INUSE
10191 | TISBURY | CHURCH MEAD | S | S105A Sewage Pumping Station | INUSE
10192 | FERNDOWN | GLISSONS | S | Sewage Pumping Station | INUSE
10193 | BURTON | THE GREEN | S | Sewage Pumping Station | INUSE
10195 | FROME | WHITE GATES | W | Private Sewage Pumping Station | INUSE
10198 | CHARMOUTH | SEADOWN HOLIDAY PARK | S | Sewage Pumping Station | INUSE
10199 | BATHWICK | COMBE ROYAL CRESCENT | N | S105A Sewage Pumping Station | INUSE
10200 | ALDERHOLT | 10A ANTELLS WAY | S | S105A Sewage Pumping Station | INUSE
10201 | WEYMOUTH | 1A-1D BUXTON ROAD | S | S105A Sewage Pumping Station | INUSE
10203 | BOURNEMOUTH | MUSCLIFFE LANE | S | S105A Sewage Pumping Station | INUSE
10206 | LANGFORD | STOCK LANE | W | S105A Sewage Pumping Station | INUSE
10207 | PUDDLETOWN | PRINCES COURT | S | S105A Sewage Pumping Station | INUSE
10208 | BRISLINGTON | LONG FOX MANOR | N | S105A Sewage Pumping Station | INUSE
10209 | WELLS | THOMAS MEWS | W | S105A Sewage Pumping Station | INUSE
10210 | EAST HUNTSPILL | WEST HILL FARM CARAVAN PARK | W | Private Sewage Pumping Station | INUSE
10211 | CHILTON TRINITY | TECHNOLOGY COLLEGE | W | Private Sewage Pumping Station | INUSE
10214 | ILMINSTER | HORTS BRIDGE | W | S105A Sewage Pumping Station | INUSE
10215 | SALTFORD | RODNEY ROAD | N | Private Sewage Pumping Station | INUSE
10217 | YATE | OUTDOOR SPORTS FACILITY | N | Private Sewage Pumping Station | INUSE
10218 | BRIDPORT | NORTH MILLS TRADING ESTATE | S | S105A Sewage Pumping Station | INUSE
10219 | BRIDPORT | EDWARDS BUILDING | S | Private Sewage Pumping Station | INUSE
10221 | HORSEY | REGAL WALK | W | Sewage Pumping Station | INUSE
10222 | HORSEY | KINGS DOWN MAIN | W | Sewage Pumping Station | INUSE
10223 | HORSEY | KINGS ROAD | W | Sewage Pumping Station | INUSE
10224 | HIGHBRIDGE | PEPPERALL ROAD | W | S105A Sewage Pumping Station | INUSE
10225 | POOLE | PREMIER INN HOLES BAY | S | Private Sewage Pumping Station | INUSE
10226 | BREAN | MOTEL | W | Private Sewage Pumping Station | INUSE
10227 | ROOKSBRIDGE | ASH LAWNS | W | Private Sewage Pumping Station | INUSE
10230 | CHEDDAR | PERRYS CLOSE | W | S105A Sewage Pumping Station | INUSE
10231 | MILTON LILBOURNE | LOWER COTTAGE | N | S105A Sewage Pumping Station | INUSE
10232 | TETBURY | CIRENCESTER ROAD | N | S105A Sewage Pumping Station | INUSE
10233 | GREAT CHEVERELL | THE GREEN | N | S105A Sewage Pumping Station | INUSE
10234 | STURMINSTER MARSHALL | HENBURY HOUSE GARDENS | S | Sewage Pumping Station | INUSE
10235 | BISHOPS CAUNDLE | KALAMATA | S | S105A Sewage Pumping Station | INUSE
10236 | STOKE BISHOP | SHAPLANDS | N | S105A Sewage Pumping Station | INUSE
10237 | BRADFORD ON TONE | DEVONIA PARK | W | Private Sewage Pumping Station | INUSE
10238 | PORTISHEAD | THE SPINNEY | W | S105A Sewage Pumping Station | INUSE
10240 | MELKSHAM | HAMPTON PARK WEST | N | Private Sewage Pumping Station | INUSE
10242 | WIMBORNE | OAKWOOD | S | Private Sewage Pumping Station | INUSE
10243 | CHEDDAR | HELLIERS LANE | W | Sewage Pumping Station | INUSE
10244 | NORTH BRADLEY | SOUTHWICK ROAD SURFACE WATER | N | Private Sewage Pumping Station | INUSE
10245 | CHELSTON | MONUMENT VIEW | W | S105A Sewage Pumping Station | INUSE
10246 | BISHOPSTROW | HOTEL | N | Private Sewage Pumping Station | INUSE
10248 | BRANSGORE | HOLMSLEY CARAVAN PARK | S | Private Sewage Pumping Station | INUSE
10249 | COALPIT HEATH | BADMINTON ROAD | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
10250 | WORLEBURY | MILBURY GARDENS | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
10251 | SHEPTON MALLET | BLACKBERRY CLOSE | W | S105A Sewage Pumping Station | INUSE
10252 | STURMINSTER NEWTON | ORCHARD GARDENS | S | S105A Sewage Pumping Station | INUSE
10253 | ROWDE | LOWER FARM | N | Private Sewage Pumping Station | INUSE
10254 | BUTLEIGH | BUTLEIGH COURT | W | S105A Sewage Pumping Station | INUSE
10255 | BRADFORD-ON-AVON | FROME ROAD | N | Private Sewage Pumping Station | INUSE
10256 | BISHOPS HULL | MILLIGAN | W | Sewage Pumping Station | INUSE
10257 | BRISTOL | HANNOVER QUAY | N | Private Sewage Pumping Station | INUSE
10258 | WARMINSTER | DEVERILL ROAD | N | Private Sewage Pumping Station | INUSE
10259 | YEOVIL | DODHAM CRESCENT FRONT 11 | W | S105A Sewage Pumping Station | INUSE
10260 | YEOVIL | DODHAM CRESCENT ADJACENT 5 | W | S105A Sewage Pumping Station | INUSE
10261 | WEST WICK | GARDEN OF 5 WICK COURT | W | S105A Sewage Pumping Station | INUSE
10262 | LOCKING | ANSON ROAD EJECTOR STATION | W | S105A Sewage Pumping Station | INUSE
10263 | LOCKING | VARSITY WAY SURFACE WATER | W | Private Sewage Pumping Station | INUSE
10264 | HOLT | HILLTOP COTTAGE | S | Private Sewage Pumping Station | INUSE
10268 | MARSHFIELD | ASHWICKE HALL | N | Private Sewage Pumping Station | INUSE
10269 | BRIDPORT | RUSSET GARDENS | S | S105A Sewage Pumping Station | INUSE
10273 | MIDSOMER NORTON | 25A PARKWAY | N | S105A Sewage Pumping Station | INUSE
10274 | WIMBORNE | 141 LONNEN ROAD | S | S105A Sewage Pumping Station | INUSE
10275 | MARKET LAVINGTON | 41 THE SPRING | N | Private Sewage Pumping Station | INUSE
10276 | WESTBURY | BRIDGE COURT | N | S105A Sewage Pumping Station | INUSE
10277 | HEDDINGTON | AWDRY CLOSE | N | S105A Sewage Pumping Station | INUSE
10278 | HORTON CROSS | NURSING HOME SINGLE PROPERTY. | W | Private Sewage Pumping Station | INUSE
10279 | FONTMELL MAGNA | BLACKMORE COTTAGE | S | S105A Sewage Pumping Station | INUSE
10280 | ILMINSTER | WINTERHAY LANE 1 | W | S105A Sewage Pumping Station | INUSE
10281 | WINCANTON | 3 CARMEL VILLAS | W | Private Sewage Pumping Station | INUSE
10286 | FERNDOWN | LAKE FARM CLOSE | S | S105A Sewage Pumping Station | INUSE
10287 | BISHOPDOWN | WOLFERSTAN DRIVE | S | S105A Sewage Pumping Station | INUSE
10288 | BRISTOL | HARBURY ROAD | N | Combined Sewer Overflow | INUSE
10290 | POOLE | CANFORD CLIFFS ROAD | S | S105A Sewage Pumping Station | INUSE
10291 | MELKSHAM | SCOTLAND ROAD | N | Private Sewage Pumping Station | INUSE
10292 | FORDINGBRIDGE | DOWNWOOD CLOSE | S | S105A Sewage Pumping Station | INUSE
10293 | EAST CHINNOCK | PORTMAN COURT | W | S105A Sewage Pumping Station | INUSE
10294 | YATE | 57- 63 GOOSE GREEN | N | S105A Sewage Pumping Station | INUSE
10295 | YATE | 53-55 GOOSE GREEN | N | S105A Sewage Pumping Station | INUSE
10297 | HOLCOMBE | STOWELL CONCRETE SURFACE WATER | W | Private Sewage Pumping Station | INUSE
10298 | BLANDFORD | SANDBOURNE AVENUE | S | Sewage Pumping Station | INUSE
10302 | MINEHEAD | BLUE ANCHOR CHALETS | W | Sewage Pumping Station | INUSE
10303 | CHRISTCHURCH | MARINA VIEW | S | Sewage Pumping Station | INUSE
10304 | FERNDOWN | PINE WALK | S | S105A Sewage Pumping Station | INUSE
10308 | POOLE | CANFORD CLIFFS SURFACE WATER | S | Private Sewage Pumping Station | INUSE
10309 | CASTLE CARY | TRADING ESTATE TORBAY ROAD | W | Sewage Pumping Station | INUSE
10310 | WESTBURY | BROADWAY NORTH | N | Sewage Pumping Station | INUSE
10312 | IRON ACTON | HOOVERS LANE | N | Sewage Pumping Station | INUSE
10313 | WOOL | BINDON LANE | S | Private Sewage Pumping Station | INUSE
10314 | BRIDGWATER | HORSEPOND LANE FRIARN STREET | W | Private Sewage Pumping Station | INUSE
10315 | CHARLTON MARSHALL | PARVA COTTAGES | S | S105A Sewage Pumping Station | INUSE
10316 | GLASTONBURY | HORSEMANS MEWS | W | S105A Sewage Pumping Station | INUSE
10317 | SHAFTESBURY | VALE VIEW BIMPORT | S | S105A Sewage Pumping Station | INUSE
10318 | EAST LYNG | ROSE AND CROWN | W | Private Sewage Pumping Station | INUSE
10319 | TAUNTON | STONEGALLOWS 1 | W | Private Sewage Pumping Station | INUSE
10320 | TAUNTON | STONEGALLOWS 2 | W | Private Sewage Pumping Station | INUSE
10321 | BURNHAM-ON-SEA | BREAN DOWN ROAD 1 | W | Private Sewage Pumping Station | INUSE
10322 | BURNHAM-ON-SEA | BREAN DOWN ROAD 2 | W | Private Sewage Pumping Station | INUSE
10323 | BURNHAM-ON-SEA | BREAN DOWN ROAD 3 | W | Private Sewage Pumping Station | INUSE
10324 | BURNHAM-ON-SEA | BREAN DOWN ROAD 4 | W | Private Sewage Pumping Station | INUSE
10325 | BURLEY | COTT LANE | S | Private Sewage Pumping Station | INUSE
10327 | SPARKFORD | HAYNES MOTOR MUSEUM | W | Private Sewage Pumping Station | INUSE
10328 | POOLE | TWEMLOW AVENUE | S | Private Sewage Pumping Station | INUSE
10329 | POOLE | WELLLOW GARDENS | S | S105A Sewage Pumping Station | INUSE
10330 | POOLE | BARTER ROAD | S | Private Sewage Pumping Station | INUSE
10332 | HIGHCLIFFE | WHARNCLIFFE ROAD SURFACE WATER | S | Private Sewage Pumping Station | INUSE
10333 | BRADLEY STOKE | WILLOW BROOK CENTRE SURFACE WATER 1 | N | Private Sewage Pumping Station | INUSE
10334 | BRADLEY STOKE | WILLOW BROOK CENTRE SURFACE WATER 2 | N | Private Sewage Pumping Station | INUSE
10336 | PYMORE | THREAD MILL LANE SURFACE WATER | S | Private Sewage Pumping Station | INUSE
10337 | HOLCOMBE | LONGLEAT ROAD | W | S105A Sewage Pumping Station | INUSE
10340 | MERE | ADJACENT VICARAGE ANGEL LANE | N | Private Sewage Pumping Station | INUSE
10343 | PORTISHEAD | 256B DOWN ROAD | W | Private Sewage Pumping Station | INUSE
10344 | YEOVIL | GREAT MEAD | W | Sewage Pumping Station | INUSE
10345 | TETBURY | POLICE HOUSE PRIORY ROAD | N | S105A Sewage Pumping Station | INUSE
10346 | WELLS | GATE LANE | W | Private Sewage Pumping Station | INUSE
10354 | HORSEY | KINGS ROAD LIFT STATION | W | Sewage Pumping Station | INUSE
10355 | HORSEY | REGAL WALK LIFT STATION | W | Sewage Pumping Station | INUSE
10358 | SALISBURY | ST. CLEMENTS MEWS | S | S105A Sewage Pumping Station | INUSE
10359 | BRIDGWATER | 13 FRIARN STREET | W | Private Sewage Pumping Station | INUSE
10360 | BRIDGWATER | 11 FRIARN STREET | W | Private Sewage Pumping Station | INUSE
10362 | BISHOPS HULL | NETHERCLAY HOUSE | W | Private Sewage Pumping Station | INUSE
10363 | KEYNSHAM | ST CLEMENTS ROAD | N | Sewage Pumping Station | INUSE
10364 | BISHOPSWORTH | BISHOPS COVE STORM TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
10365 | HIGHBRIDGE | LAKESIDE BRISTOL ROAD | W | S105A Sewage Pumping Station | INUSE
10367 | BERKELEY | 43 LYNCH ROAD | N | Private Sewage Pumping Station | INUSE
10369 | WESTON-SUPER-MARE | COASTAL TOILET BLOCK | W | Private Sewage Pumping Station | INUSE
10370 | PORLOCK WEIR | QUAY | W | Sewage Pumping Station | INUSE
10372 | BATH | TOR VISTA | N | Private Sewage Pumping Station | INUSE
10374 | BERROW | UNITY FARM 1 | W | S105A Sewage Pumping Station | INUSE
10375 | SHERBORNE | JUNCTION HOUND STREET AND CHEAP STREET | S | Combined Sewer Overflow | INUSE
10376 | TEMPLECOMBE | EAST STREET | W | S105A Sewage Pumping Station | INUSE
10378 | STINCHCOMBE | TOWNSEND BARN | N | S105A Sewage Pumping Station | INUSE
10379 | WEYMOUTH | NOTTINGTON LANE | S | S105A Sewage Pumping Station | INUSE
10380 | WINTERBOURNE | MEADOW VIEW BARN | N | S105A Sewage Pumping Station | INUSE
10381 | ILMINSTER | WINTERHAY LANE 2 | W | S105A Sewage Pumping Station | INUSE
10382 | WINSCOMBE | SIDCOT DRIVE | W | S105A Sewage Pumping Station | INUSE
10383 | CORSHAM | BROOK DRIVE | N | S105A Sewage Pumping Station | INUSE
10384 | WESTBURY | 70 WESTBURY LEIGH | N | S105A Sewage Pumping Station | INUSE
10386 | WESTON-SUPER-MARE | SPRING COVE | W | S105A Sewage Pumping Station | INUSE
10387 | HASELBURY PLUCKNETT | HEATHFIELD ROW | W | Sewage Pumping Station | INUSE
10388 | DURDHAM PARK | HAREWOOD HOUSE | N | S105A Sewage Pumping Station | INUSE
10393 | BATH | LYTTON GARDENS | N | S105A Sewage Pumping Station | INUSE
10394 | SOPLEY | MILL | S | S105A Sewage Pumping Station | INUSE
10395 | TROWBRIDGE | LADYDOWN MILL | N | S105A Sewage Pumping Station | INUSE
10397 | ST GEORGES | THE COURTHOUSE | W | Private Sewage Pumping Station | INUSE
10398 | ALDERBURY | LIGHTS LANE | S | Private Sewage Pumping Station | INUSE
10400 | BATH | SPORTS CENTRE | N | Private Sewage Pumping Station | INUSE
10401 | MINEHEAD | 53 QUAY STREET | W | Private Sewage Pumping Station | INUSE
10402 | BATHAMPTON | ST GEORGE COTTAGE | N | Private Sewage Pumping Station | INUSE
10403 | BRISTOL | APPLEGATE | N | S105A Sewage Pumping Station | INUSE
10406 | BRISTOL | 6-8 SEA MILLS LANE | N | Single Property Pumping Station | INUSE
10407 | BRISTOL | 4 SEA MILLS LANE | N | Single Property Pumping Station | INUSE
10410 | OAKHILL | PRIMARY SCHOOL | W | Private Sewage Pumping Station | INUSE
10411 | WESTON-SUPER-MARE | WOODSPRING STADIUM | W | Private Sewage Pumping Station | INUSE
10412 | MALMESBURY | KINFIELD 1 | N | Private Sewage Pumping Station | INUSE
10413 | MALMESBURY | KINFIELD 2 | N | Private Sewage Pumping Station | INUSE
10414 | WESTON-SUPER-MARE | WILSON GARDENS | W | Sewage Pumping Station | INUSE
10415 | POOLE | 1A TO 1C GRANVILLE ROAD | S | S105A Sewage Pumping Station | INUSE
10416 | WEST PARLEY | 244A CHRISTCHURCH ROAD | S | Private Sewage Pumping Station | INUSE
10417 | WARMINSTER | TANGIER CLOSE | N | S105A Sewage Pumping Station | INUSE
10419 | OAKHILL | ZION HILL | W | S105A Sewage Pumping Station | INUSE
10421 | PRESTON | KEAST COURT HERON CLOSE | S | Private Sewage Pumping Station | INUSE
10422 | WINTERBORNE WHITECHURCH | OLD OAK WAY | S | Private Sewage Pumping Station | INUSE
10423 | STURMINSTER NEWTON | NEWTON GATE | S | S105A Sewage Pumping Station | INUSE
10424 | HOLT | 323 STATION ROAD | N | Private Sewage Pumping Station | INUSE
10425 | TROWBRIDGE | 31B HILPERTON ROAD | S | Private Sewage Pumping Station | INUSE
10426 | SALISBURY | LYWOOD CLOSE | S | Sewage Pumping Station | INUSE
10427 | CREWKERNE | RAMUS HOUSE | W | Private Sewage Pumping Station | INUSE
10429 | BOX | NORTHEY ARMS | N | Private Sewage Pumping Station | INUSE
10433 | NYNEHEAD | 6 BLACKDOWN VIEW | W | Private Sewage Pumping Station | INUSE
10434 | SALISBURY | SASSOON CLOSE | S | Sewage Pumping Station | INUSE
10435 | GLASTONBURY | GODNEY CLOSE | W | S105A Sewage Pumping Station | INUSE
10438 | SALISBURY | CASTLEGATE BUSINESS PARK | S | Sewage Pumping Station | INUSE
10441 | PORTISHEAD | VALLEY ROAD CIVIC AMENITY SITE | W | Private Sewage Pumping Station | INUSE
10442 | LEIGH DELAMERE | HAMLET | N | S105A Sewage Pumping Station | INUSE
10443 | ROYAL WOOTTON BASSETT | MIRANDA HOUSE NURSING HOME | N | Private Sewage Pumping Station | INUSE
10447 | BOURNEMOUTH | BLUE WATER 10-12 | S | Private Sewage Pumping Station | INUSE
10448 | SPARKFORD | HAZELGROVE SCHOOL | W | Private Sewage Pumping Station | INUSE
10450 | TICKENHAM | TICKENHAM HILL | W | Private Sewage Pumping Station | INUSE
10451 | AXBRIDGE | KNIGHTSTONE CLOSE | W | S105A Sewage Pumping Station | INUSE
10452 | WESTON-SUPER-MARE | LANSDOWN COURT | W | S105A Sewage Pumping Station | INUSE
10453 | SWANAGE | QUARRY CLOSE SURFACE WATER | S | Private Sewage Pumping Station | INUSE
10456 | FROME | WELSHMILL LANE | W | Private Sewage Pumping Station | INUSE
10458 | BOURNEMOUTH | BOURNE ACCADEMY 1 | S | Private Sewage Pumping Station | INUSE
10459 | BOURNEMOUTH | BOURNE ACCADEMY 2 | S | Private Sewage Pumping Station | INUSE
10460 | SALISBURY | HEATH VEW DRIVE | S | S105A Sewage Pumping Station | INUSE
10461 | SALISBURY | LONDON ROAD 1 | N | Private Sewage Pumping Station | INUSE
10462 | SALISBURY | LONDON ROAD 2 | N | Private Sewage Pumping Station | INUSE
10464 | WESTBURY | POND LEVELLING TANK | N | Private Sewage Pumping Station | INUSE
10465 | TROWBRIDGE | THE SPINNEY | N | Private Sewage Pumping Station | INUSE
10466 | FROME | OLD MANOR | N | Private Sewage Pumping Station | INUSE
10467 | MELKSHAM | AVON TECHNICAL PRODUCTS | N | Private Sewage Pumping Station | INUSE
10468 | RINGWOOD | OAK TREE PARK | S | Private Sewage Pumping Station | INUSE
10469 | BRADFORD-ON-AVON | ABBEY MILL RETIREMENT APARTMENTS | N | Private Sewage Pumping Station | INUSE
10470 | BATH | VILVEN | N | S105A Sewage Pumping Station | INUSE
10471 | BATH | SYDNEY HOUSE | N | S105A Sewage Pumping Station | INUSE
10472 | WEMBDON | WEMBDON ORCHARD SINGLE PROPERTY | W | Private Sewage Pumping Station | INUSE
10474 | TYTHERINGTON | THE NURSERIES | N | S105A Sewage Pumping Station | INUSE
10475 | STURMINSTER NEWTON | BUFFETTS CLOSE | S | S105A Sewage Pumping Station | INUSE
10476 | SWANAGE | MARSH WAY | S | S105A Sewage Pumping Station | INUSE
10477 | SALISBURY | SLEEPER AND SIDINGS | S | Private Sewage Pumping Station | INUSE
10478 | FERNDOWN | COACH HOUSE MEWS | S | Private Sewage Pumping Station | INUSE
10479 | IWERNE MINSTER | HOME FARM | S | Private Sewage Pumping Station | INUSE
10480 | CALNE | PENN COURT | N | Private Sewage Pumping Station | INUSE
10481 | BOURNEMOUTH | HOLDENHURST ROAD | S | Private Sewage Pumping Station | INUSE
10482 | BOURNEMOUTH | SEACOTE | S | S105A Sewage Pumping Station | INUSE
10483 | RINGWOOD | HERONS MEAD | S | Private Sewage Pumping Station | INUSE
10484 | BOURNEMOUTH | SOUTHBOURNE OVERCLIFF DRIVE | S | Private Sewage Pumping Station | INUSE
10485 | POOLE | THE DUNES | S | Private Sewage Pumping Station | INUSE
10486 | POOLE | HARRY PAYE CLOSE | S | Private Sewage Pumping Station | INUSE
10487 | SALISBURY | SARUM GARDENS | N | Private Sewage Pumping Station | INUSE
10488 | POOLE | MOUNT PLEASANT ROAD | S | Private Sewage Pumping Station | INUSE
10489 | WARMINSTER | PORTWAY | N | Private Sewage Pumping Station | INUSE
10490 | CALNE | ANCHOR ROAD 64-74 | N | Private Sewage Pumping Station | INUSE
10491 | BURTON BRADSTOCK | THE MONASTERY | S | Private Sewage Pumping Station | INUSE
10492 | ST. LEONARDS | CEDAR AVENUE SINGLE PROPERTY | S | Private Sewage Pumping Station | INUSE
10493 | STURMINSTER MARSHALL | BAILIE GATE INDUSTRIAL ESTATE 1 | S | Private Sewage Pumping Station | INUSE
10494 | POOLE | 4 LILLIPUT ROAD | S | Private Sewage Pumping Station | INUSE
10496 | HOLTON HEATH | ADMIRALTY PARK | S | Private Sewage Pumping Station | INUSE
10498 | CORFE MULLEN | FROUD WAY | S | Private Sewage Pumping Station | INUSE
10499 | ILMINSTER | HOME FARM PARK | W | Private Sewage Pumping Station | INUSE
10505 | LANGFORD | MEDICAL CENTRE SURFACE | W | Private Sewage Pumping Station | INUSE
10506 | YATTON | JONES BRIDGE SURFACE WATER | W | Private Sewage Pumping Station | INUSE
10508 | SOUTH PETHERTON | CHAPEL FIELD ROAD | W | Sewage Pumping Station | INUSE
10509 | WELLS | ALFRED COURT | W | Private Sewage Pumping Station | INUSE
10510 | BISHOPS LYDEARD | STATION GREEN | W | Sewage Pumping Station | INUSE
10513 | BRIDGWATER | ELM CROFT | W | Private Sewage Pumping Station | INUSE
10514 | PILL | THE WITHYS | W | S105A Sewage Pumping Station | INUSE
10515 | BRISTOL | ROCKLAND ROAD | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
10516 | MELKSHAM | ST. ANDREWS ROAD | N | Sewage Pumping Station | INUSE
10517 | CALNE | ABBERD LANE | N | Sewage Pumping Station | INUSE
10521 | BRADPOLE | HOMEWOOD WAY | S | Private Sewage Pumping Station | INUSE
10522 | YEOVIL | LYSANDER ROAD SURFACE WATER | S | Private Sewage Pumping Station | INUSE
10523 | MIDSOMER NORTON | WITHIES PARK | N | Sewage Pumping Station | INUSE
10524 | BURBAGE | SEYMOUR GRAFTON ROAD | N | Private Sewage Pumping Station | INUSE
10525 | COTFORD ST. LUKE | DENE ROAD | W | Private Sewage Pumping Station | INUSE
10526 | CREECH ST. MICHAEL | LEIGHTON DRIVE | W | S105A Sewage Pumping Station | INUSE
10528 | YATE | 400 BADMINTON ROAD | N | Private Sewage Pumping Station | INUSE
10529 | BATH | SUMMERLAYS COURT | N | S105A Sewage Pumping Station | INUSE
10530 | YETMINSTER | 11 SUSSEX FARM WAY | S | S105A Sewage Pumping Station | INUSE
10531 | MELCOMBE BINGHAM | CROSS LANES | S | Private Sewage Pumping Station | INUSE
10532 | BICKNOLLER | HONEYROW LANE THE PADDOCKS | W | Private Sewage Pumping Station | INUSE
10533 | SOUTH BARROW | CHAPEL LANE | W | S105A Sewage Pumping Station | INUSE
10534 | BRISTOL | STOKE PARK ROAD | N | S105A Sewage Pumping Station | INUSE
10535 | PORTISHEAD | DOWN ROAD | W | S105A Sewage Pumping Station | INUSE
10536 | WALKFORD | BROADLANDS CLOSE | S | S105A Sewage Pumping Station | INUSE
10537 | CLEVEDON | VICTORIA COURT | W | S105A Sewage Pumping Station | INUSE
10538 | TONEDALE | LOWMOOR INDUSTRIAL ESTATE | W | S105A Sewage Pumping Station | INUSE
10539 | KILVE | GREAT HANGER HOUSE | W | Private Sewage Pumping Station | INUSE
10541 | CALNE | IVY WALK | N | S105A Sewage Pumping Station | INUSE
10542 | TIMSBURY | LAUREL GARDENS | N | S105A Sewage Pumping Station | INUSE
10543 | BATH | THE ORCHARD HORSECOMBE VALE | N | Private Sewage Pumping Station | INUSE
10544 | MISTERTON | BROUGHTONS DRIVE | W | S105A Sewage Pumping Station | INUSE
10545 | MARSHFIELD | ST. MARTINS PARK | N | S105A Sewage Pumping Station | INUSE
10546 | HOLFORD | LITTLE QUANTOCK | W | Private Sewage Pumping Station | INUSE
10547 | CHEDDAR | OAK CLOSE STATION ROAD | W | S105A Sewage Pumping Station | INUSE
10548 | DOWNTON | PARKERS CLOSE | S | S105A Sewage Pumping Station | INUSE
10549 | WINTERBORNE WHITECHURCH | CHARLOTTE GARDENS | S | Private Sewage Pumping Station | INUSE
10550 | BOURNEMOUTH | 17 FOREST VIEW CLOSE | S | S105A Sewage Pumping Station | INUSE
10556 | WASHFORD | 22A CASTLE MEAD | W | Private Sewage Pumping Station | INUSE
10562 | CONHAM | EASTWOOD FARM LEACHATE | N | Private Sewage Pumping Station | INUSE
10563 | BATH | CULVERHAY NURSING HOME | N | Private Sewage Pumping Station | INUSE
10564 | COLDHARBOUR | SILENT WOMAN | S | Sewage Pumping Station | INUSE
10565 | NORTH TRIGON | NORTH TRIGON SEWAGE PUMPING STATION | S | Sewage Pumping Station | INUSE
10570 | KENN | WILLOW COTTAGE | W | Private Sewage Pumping Station | INUSE
10571 | WATCHET | LITTLE SILVER COURT | W | Private Sewage Pumping Station | INUSE
10572 | BRISTOL | ROSELAND GARDENS | N | S105A Sewage Pumping Station | INUSE
10574 | PARLEY | SUSTAINABLE SOLUTIONS | S | Private Sewage Pumping Station | INUSE
10575 | PARLEY | SUSTAINABLE SOLUTIONS LEACHATE | S | Private Sewage Pumping Station | INUSE
10576 | BATH | SOUTHLANDS | N | Private Sewage Pumping Station | INUSE
10578 | SHERSTON | SOPWORTH ROAD | N | Private Sewage Pumping Station | INUSE
10585 | SANDLEHEATH | SANDLE MANOR SCHOOL | S | Private Sewage Pumping Station | INUSE
10586 | POOLE | 1 SHORE ROAD | S | Private Sewage Pumping Station | INUSE
10589 | LOCKING | OAKTREE PARK | W | Private Sewage Pumping Station | INUSE
10590 | BERKELEY | PORLOCK HOUSE | N | Private Sewage Pumping Station | INUSE
10591 | DUNKERTON | SPLOTT FARM | N | Private Sewage Pumping Station | INUSE
10592 | PEWSEY | HOLLY TREE WALK | N | Private Sewage Pumping Station | INUSE
10593 | BRIDGWATER | 190 CHILTON STREET | W | Private Sewage Pumping Station | INUSE
10594 | BERROW | NO 3 MANOR CLOSE | W | Sewage Pumping Station | INUSE
10595 | YATE | MEADOWBANK GOOSE GREEN | N | S105A Sewage Pumping Station | INUSE
10596 | BOURNEMOUTH | GRACIE COURT | S | S105A Sewage Pumping Station | INUSE
10597 | BOURNEMOUTH | GRACIE MEWS STORM | S | S105A Sewage Pumping Station | INUSE
10598 | LONG ASHTON | 8 MINERS CLOSE | W | Private Sewage Pumping Station | INUSE
10599 | LONG ASHTON | 10 MINERS CLOSE | W | S105A Sewage Pumping Station | INUSE
10603 | BATH | GLASSHOUSE GARAGE | N | Private Sewage Pumping Station | INUSE
10604 | BOURNEMOUTH | ENCORE HOTEL | S | Private Sewage Pumping Station | INUSE
10605 | WRAXALL | LOWER CHARLTON FARM SURFACE | W | Private Sewage Pumping Station | INUSE
10607 | BRISTOL | CHANTRY ROAD | N | Private Sewage Pumping Station | INUSE
10608 | EMERSONS GREEN | FOLLY BROOK ROAD SURFACE | N | Private Sewage Pumping Station | INUSE
10609 | BATH | THE ORCHARD | N | Private Sewage Pumping Station | INUSE
10610 | GILLINGHAM | RIVERSMEET LEISURE CENTRE | S | Private Sewage Pumping Station | INUSE
10612 | MARK | ROWHEDGE THE CAUSEWAY | W | S105A Sewage Pumping Station | INUSE
10616 | CREWKERNE | RYDINGS | W | S105A Sewage Pumping Station | INUSE
10617 | BATH | GREAT STANHOPE STREET | N | Private Sewage Pumping Station | INUSE
10618 | BATH | INCHALLOCH | N | Private Sewage Pumping Station | INUSE
10619 | BATH | LOWER SHOCKERWICK | N | Private Sewage Pumping Station | INUSE
10620 | PITNEY | THISTLEDOWN | W | Single Property Pumping Station | INUSE
10622 | FROME | WESSEX FIELDS | N | Private Sewage Pumping Station | INUSE
10623 | MILVERTON | BURGAGE | W | Private Sewage Pumping Station | INUSE
10624 | WARMINSTER | GEORGE STREET | N | Private Sewage Pumping Station | INUSE
10625 | WESTBURY | HEALTH CENTRE | N | Private Sewage Pumping Station | INUSE
10626 | TROWBRIDGE | BYTHESEA ROAD | N | Private Sewage Pumping Station | INUSE
10627 | TROWBRIDGE | BRITISH ROW SURFACE | N | Private Sewage Pumping Station | INUSE
10628 | STREET | BARN CLOSE | W | Private Sewage Pumping Station | INUSE
10629 | BATH | HERSCHEL PLACE | N | Private Sewage Pumping Station | INUSE
10630 | CHILCOMPTON | THE ROOKERY | N | Private Sewage Pumping Station | INUSE
10631 | SHEPTON MALLET | CHARLTON ROAD | W | Private Sewage Pumping Station | INUSE
10632 | SHEPTON MALLET | PETROL STATION OLD TOWNSEND ROAD | W | Private Sewage Pumping Station | INUSE
10633 | SHEPTON MALLET | RETAIL PARK OLD TOWNSEND ROAD | W | Private Sewage Pumping Station | INUSE
10634 | WELLS | MONDYES COURT | W | Private Sewage Pumping Station | INUSE
10635 | SOUTH HORRINGTON | WEST COURT | N | Private Sewage Pumping Station | INUSE
10636 | BOURNEMOUTH | HIBBERD WAY | S | Private Sewage Pumping Station | INUSE
10637 | POOLE | BLAIR AVENUE | S | Private Sewage Pumping Station | INUSE
10638 | POOLE | 2 LILLIPUT ROAD | S | Private Sewage Pumping Station | INUSE
10639 | POOLE | 6 LILLIPUT ROAD | S | Private Sewage Pumping Station | INUSE
10641 | POOLE | STERTE CLOSE SURFACE | S | Private Sewage Pumping Station | INUSE
10642 | POOLE | OYSTER BAY APARTMENTS SURFACE | S | Private Sewage Pumping Station | INUSE
10643 | POOLE | POOLE PARK | S | Private Sewage Pumping Station | INUSE
10644 | POOLE | WESSEX GATE RETAIL PARK | S | Private Sewage Pumping Station | INUSE
10645 | POOLE | COBBS QUAY MARINA | S | Private Sewage Pumping Station | INUSE
10646 | POOLE | FLEETS CORNER | S | Private Sewage Pumping Station | INUSE
10647 | SWANAGE | DURLSTON CASTLE | S | Private Sewage Pumping Station | INUSE
10648 | WAREHAM | SCOTT CLOSE | S | S105A Sewage Pumping Station | INUSE
10649 | BERE REGIS | CYRIL WOOD COURT | S | Private Sewage Pumping Station | INUSE
10650 | WIMBORNE | COBHAM ROAD | S | Private Sewage Pumping Station | INUSE
10652 | BRISTOL | EVA TURNER CLOSE | N | S105A Sewage Pumping Station | INUSE
10654 | LONGHAM | HOTEL | S | Private Sewage Pumping Station | INUSE
10655 | FERNDOWN | ANGEL INN | S | Private Sewage Pumping Station | INUSE
10656 | CHRISTCHURCH | REID STREET DELIVERY OFFICE SINGLE PROPERTY. | S | Private Sewage Pumping Station | INUSE
10657 | RINGWOOD | KINGSBURYS LANE SURFACE | S | Private Sewage Pumping Station | INUSE
10658 | BOURNEMOUTH | WESTBOURNE HOUSE | S | Private Sewage Pumping Station | INUSE
10659 | BOURNEMOUTH | ST. ALBANS CRESCENT | S | Private Sewage Pumping Station | INUSE
10660 | BRISTOL | PRINCE STREET HOTEL | N | Private Sewage Pumping Station | INUSE
10661 | BRISTOL | GREYSTOKE AVENUE | N | Private Sewage Pumping Station | INUSE
10662 | BRISTOL | PACKGATE ROAD SURFACE | N | Private Sewage Pumping Station | INUSE
10664 | AVONMOUTH | KING ROAD AVENUE | N | Private Sewage Pumping Station | INUSE
10665 | BRISTOL | WEST MANOR | N | Private Sewage Pumping Station | INUSE
10666 | BRISTOL | WINTER WALK | N | S105A Sewage Pumping Station | INUSE
10667 | KINGSWOOD | SISTON CENTRE | N | Private Sewage Pumping Station | INUSE
10668 | BRISTOL | SPRINGLY COURT | N | Private Sewage Pumping Station | INUSE
10669 | STAPLETON | HEALTH HOUSE LANE | N | Private Sewage Pumping Station | INUSE
10670 | FISHPONDS | PEACOCK LODGE | N | Private Sewage Pumping Station | INUSE
10671 | BRISTOL | MORRISONS FISHPONDS ROAD | N | Private Sewage Pumping Station | INUSE
10672 | BRISTOL | TEEWELL COURT | N | S105A Sewage Pumping Station | INUSE
10674 | WESTON-SUPER-MARE | KNIGHTSTONE CAUSEWAY | W | Private Sewage Pumping Station | INUSE
10675 | WESTON-SUPER-MARE | BOURNVILLE PRIMARY SCHOOL | W | Private Sewage Pumping Station | INUSE
10677 | BRISTOL | BEDMINSTER TRADE PARK | N | Private Sewage Pumping Station | INUSE
10678 | KEYNSHAM | POOL BARTON | N | Private Sewage Pumping Station | INUSE
10679 | BRADLEY STOKE | BRISTOL DISTRIBUTION PARK | N | Private Sewage Pumping Station | INUSE
10680 | BRISTOL | CANBERRA GROVE | N | S105A Sewage Pumping Station | INUSE
10681 | STOKE GIFFORD | NEW ROAD | N | Private Sewage Pumping Station | INUSE
10682 | NAILSEA | PEGASUS COURT | W | Private Sewage Pumping Station | INUSE
10683 | CHIPPING SODBURY | RIVERSIDE COURT | N | Private Sewage Pumping Station | INUSE
10685 | CONGRESBURY | STONEWELL LANE | W | S105A Sewage Pumping Station | INUSE
10686 | BRISTOL | EASTGATE ROAD | N | Private Sewage Pumping Station | INUSE
10687 | BRISTOL | BEAUFORT HEIGHTS | N | S105A Sewage Pumping Station | INUSE
10688 | BRISTOL | ASH LEA COURT | N | Private Sewage Pumping Station | INUSE
10689 | BRISTOL | SUMMER COURT | N | Private Sewage Pumping Station | INUSE
10690 | BRISTOL | KNIGHTS CLOSE | N | S105A Sewage Pumping Station | INUSE
10691 | DORCHESTER | COBURG ROAD SPORTS CENTRE | S | Private Sewage Pumping Station | INUSE
10692 | BLANDFORD GRANGE CARE HOME | THE ORCHARD | S | Sewage Pumping Station | INUSE
10693 | MAIDEN NEWTON | 1 NEILS VIEW | S | S105A Sewage Pumping Station | INUSE
10694 | CHARLTON DOWN | WALNUT COURT | S | S105A Sewage Pumping Station | INUSE
10695 | WEYMOUTH | GRANBY INDUSTRIAL ESTATE | S | Private Sewage Pumping Station | INUSE
10696 | MOSTERTON | WHITES MEADOW | S | Private Sewage Pumping Station | INUSE
10697 | SHERBORNE | LUDBOURNE ROAD SUPERMARKET SINGLE PROPERTY. | S | Private Sewage Pumping Station | INUSE
10698 | CALNE | ST MARYS SCHOOL | N | Private Sewage Pumping Station | INUSE
10700 | MELKSHAM | ASHVILLE CENTRE | N | Private Sewage Pumping Station | INUSE
10702 | YATTON KEYNELL | 12 FARRELLS FIELD | N | Private Sewage Pumping Station | INUSE
10703 | COLERNE | LUCKNAM PARK HOTEL | N | Private Sewage Pumping Station | INUSE
10704 | SALISBURY | LOWER ROAD | N | Private Sewage Pumping Station | INUSE
10705 | SALISBURY | CRANE STREET SURFACE | N | Private Sewage Pumping Station | INUSE
10706 | TILSHEAD | AWES EXCON | N | Private Sewage Pumping Station | INUSE
10707 | AMESBURY | SPORTS PAVILLION | N | Private Sewage Pumping Station | INUSE
10708 | MARTOCK | 2 HORSE SHOE COTTAGES | W | S105A Sewage Pumping Station | INUSE
10709 | DOWNTON | LODE HILL | S | Private Sewage Pumping Station | INUSE
10710 | GILLINGHAM | THORNE GROVE CENTRE | S | Private Sewage Pumping Station | INUSE
10711 | GILLINGHAM | PEACEMARSH FARM CLOSE | S | S105A Sewage Pumping Station | INUSE
10712 | GILLINGHAM | WYKE HALL | S | S105A Sewage Pumping Station | INUSE
10713 | ROUGHMOOR | SILKMILLS ROAD | W | Private Sewage Pumping Station | INUSE
10714 | LANGPORT | SOMERTON HILL | W | Private Sewage Pumping Station | INUSE
10715 | LANGPORT | LANGPORT SURGERY SINGLE PROPERTY. | W | Private Sewage Pumping Station | INUSE
10716 | BARTON ST. DAVID | ORCHARD HOUSE | W | S105A Sewage Pumping Station | INUSE
10717 | BARRINGTON | BARRINGTON COURT COTTAGES | W | Private Sewage Pumping Station | INUSE
10718 | NORTON FITZWARREN | CROSS KEYS CLOSE | W | Private Sewage Pumping Station | INUSE
10719 | WINSHAM | BALSOM CLOSE | W | Private Sewage Pumping Station | INUSE
10720 | BERROW | HOLIDAY PARK | W | Private Sewage Pumping Station | INUSE
10721 | BERROW | HOLIDAY PARK | W | Private Sewage Pumping Station | INUSE
10722 | BRENT KNOLL | SOMERSET COURT | W | Private Sewage Pumping Station | INUSE
10723 | MARK | MARK COLLEGE | W | Private Sewage Pumping Station | INUSE
10724 | STOURTON | STOURHEAD | S | Private Sewage Pumping Station | INUSE
10725 | SALISBURY | WINTERBOURNE CARE HOME | S | Private Sewage Pumping Station | INUSE
10726 | BOVINGTON | CUNNINGHAM CLOSE | S | Private Sewage Pumping Station | INUSE
10727 | FLAX BOURTON | STANCOMBE QUARRY | W | Private Sewage Pumping Station | INUSE
10728 | BURLEY | BURLEY GOLF CLUB | S | Single Property Pumping Station | INUSE
10729 | SHERSTON | HOLMFIELD | N | S105A Sewage Pumping Station | INUSE
10730 | BRISTOL | LANGCLIFFE COURT SURFACE | N | Private Sewage Pumping Station | INUSE
10731 | BRIDGWATER | 62 SUNNYMEADE | W | S105A Sewage Pumping Station | INUSE
10733 | RINGWOOD | ASHLEY HEATH | S | S105A Sewage Pumping Station | INUSE
10736 | BRYANSTON | BRYANSTON SCHOOL | S | Sewage Pumping Station | INUSE
10738 | POOLE | 73 CHADDESLEY GLEN | S | Private Sewage Pumping Station | INUSE
10741 | TROWBRIDGE | THE LODGE | N | Private Sewage Pumping Station | INUSE
10742 | BRISTOL | TEMPORARY CAR WASH | W | Private Sewage Pumping Station | INUSE
10743 | BLANDFORD FORUM | THE BLANDFORD SCHOOL | S | Private Sewage Pumping Station | INUSE
10745 | PODIMORE | LITTLE CHEF | W | Private Sewage Pumping Station | INUSE
10746 | BRISTOL | CAPRICORN PLACE | N | Private Sewage Pumping Station | INUSE
10747 | WINTERBOURNE | FLAXPITS HOUSE | N | Private Sewage Pumping Station | INUSE
10749 | GILLINGHAM | HAWTHORN AVENUE 1 | S | S105A Sewage Pumping Station | INUSE
10750 | EDINGTON | HARDINGS BARTON | W | Single Property Pumping Station | INUSE
10751 | CHIPPENHAM | VICTORIAS PLACE | N | S105A Sewage Pumping Station | INUSE
10753 | WELLS | ROWDENS ROAD | W | Private Sewage Pumping Station | INUSE
10755 | BRENT KNOLL | BRENT STREET NURSING HOME | W | Private Sewage Pumping Station | INUSE
10759 | YATE | CHAPEL ORCHARD | N | S105A Sewage Pumping Station | INUSE
10760 | FROME | PROVIDENCE COURT | W | S105A Sewage Pumping Station | INUSE
10763 | BOURNEMOUTH | KNIGHTON HEATH GOLF CLUB | S | Private Sewage Pumping Station | INUSE
10764 | WEST HUNTSPILL | 78 CHURCH ROAD | W | Private Sewage Pumping Station | INUSE
10766 | BOVINGTON | VICTORIA CLOSE | S | Private Sewage Pumping Station | INUSE
10767 | TROWBRIDGE | LEISLER GARDENS | N | Sewage Pumping Station | INUSE
10768 | SIXPENNY HANDLEY | TOWN FARM HOUSE | S | Sewage Pumping Station | INUSE
10769 | WESTBURY-ON-TRYM | TOWN FARM HOUSE | N | Private Sewage Pumping Station | INUSE
10770 | BRADFORD-ON-AVON | GREENLAND VIEW | N | S105A Sewage Pumping Station | INUSE
10771 | WESTON-SUPER-MARE | MARTINDALE COURT | W | Private Sewage Pumping Station | INUSE
10772 | BEAMINSTER | 5 SHORTS LANE | S | Private Sewage Pumping Station | INUSE
10773 | TROWBRIDGE | 45 FRANCIS STREET | N | S105A Sewage Pumping Station | INUSE
10774 | BATH | RINGSWELL GARDENS | N | S105A Sewage Pumping Station | INUSE
10775 | DEVIZES | VICTORIA ROAD | N | Sewage Pumping Station | INUSE
10776 | WEYMOUTH | 5 TEELING ROAD | S | Single Property Pumping Station | INUSE
10777 | RADSTOCK | FORTESCUE ROAD | N | Sewage Pumping Station | INUSE
10779 | WELLS | 12A ASH LANE | W | Private Sewage Pumping Station | INUSE
10780 | SWANAGE | ULWELL ROAD | S | Private Sewage Pumping Station | INUSE
10781 | PORTISHEAD | ESPLANADE TENNIS COURTS | W | Private Sewage Pumping Station | INUSE
10783 | BOURNEMOUTH | 98 HAREWOOD AVENUE | S | Private Sewage Pumping Station | INUSE
10785 | WESTON-SUPER-MARE | SPRING HILL | W | Sewage Pumping Station | INUSE
10792 | WESTBURY | WARMINSTER ROAD | N | S105A Sewage Pumping Station | INUSE
10794 | BRIDGWATER | ACORN PARK | W | Private Sewage Pumping Station | INUSE
10795 | HAMBROOK | QUARRY BARTON | N | Combined Sewer Overflow | INUSE
10796 | GASTARD | GOODS HILL | N | Private Sewage Pumping Station | INUSE
10799 | PEWSHAM | PEWSHAM HOUSE | N | S105A Sewage Pumping Station | INUSE
10800 | TIMSBURY | CROCOMBE | N | S105A Sewage Pumping Station | INUSE
10801 | SHEPTON MALLET | YORK MEWS | W | S105A Sewage Pumping Station | INUSE
10802 | PORTLAND | OSPREY QUAY | S | Private Sewage Pumping Station | INUSE
10808 | COMBE DOWN | BEECHWOOD LODGE | N | S105A Sewage Pumping Station | INUSE
10810 | BRISTOL | BEDMINSTER DOWN ROAD | N | Private Sewage Pumping Station | INUSE
10811 | WEST MOORS | BOND AVENUE MOD | S | Private Sewage Pumping Station | INUSE
10812 | AMESBURY | BOSCOMBE DOWN 2 MOD | S | Private Sewage Pumping Station | INUSE
10813 | AMESBURY | BOSCOMBE DOWN 3 MOD | S | Private Sewage Pumping Station | INUSE
10814 | WEST MOORS | PETROLEUM CENTRE SPS 1 MOD | S | Private Sewage Pumping Station | INUSE
10815 | WEST MOORS | PETROLEUM CENTRE SPS 2 MOD | S | Private Sewage Pumping Station | INUSE
10816 | BOVINGTON | CAPPER ROAD EAST MOD | S | Private Sewage Pumping Station | INUSE
10817 | CHARD | SHEPHERDS LANE | W | S105A Sewage Pumping Station | INUSE
10818 | BOURNEMOUTH | STOUR GARDENS | S | S105A Sewage Pumping Station | INUSE
10819 | CALNE | MEADOW VIEW | N | S105A Sewage Pumping Station | INUSE
10820 | LOCKING | HELICOPTER MUSEUM | W | Private Sewage Pumping Station | INUSE
10821 | CREWKERNE | MILL COTTAGES | W | S105A Sewage Pumping Station | INUSE
10822 | BRISTOL | THE SIDINGS | N | S105A Sewage Pumping Station | INUSE
10823 | WARMINSTER | PERRIWINKLE CLOSE | N | S105A Sewage Pumping Station | INUSE
10824 | KEYNSHAM | TEMPLE STREET | N | Private Sewage Pumping Station | INUSE
10825 | BATH | BAILBROOK COTTAGES | N | Sewage Pumping Station | INUSE
10826 | POOLE | UPPLEBY ROAD ATTENUATION | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
10827 | CHRISTCHURCH | PEPPERCORN CLOSE | S | S105A Sewage Pumping Station | INUSE
10828 | POOLE | BRIXEY CLOSE | S | S105A Sewage Pumping Station | INUSE
10830 | SHAPWICK | THE COURTYARD | W | S105A Sewage Pumping Station | INUSE
10833 | STURMINSTER MARSHALL | BAILIE GATE INDUSTRIAL ESTATE 2 | S | Private Sewage Pumping Station | INUSE
10834 | STURMINSTER MARSHALL | BAILIE GATE INDUSTRIAL ESTATE 3 | S | Private Sewage Pumping Station | INUSE
10836 | SALWAYASH | 2 ASH FARM BUNGALOW | S | Private Sewage Pumping Station | INUSE
10837 | SALWAYASH | 1 ASH FARM BUNGALOW | S | Private Sewage Pumping Station | INUSE
10838 | POOLE | COBBS QUAY MARINA 2 | S | S105A Sewage Pumping Station | INUSE
10839 | CHIPPENHAM | ABBEYFIELD SCHOOL | N | Private Sewage Pumping Station | INUSE
10840 | WEYMOUTH | ABBOTSBURY ROAD FOUL AND SURFACE | S | S105A Sewage Pumping Station | INUSE
10841 | BRISTOL | CANONS WAY | N | Private Sewage Pumping Station | INUSE
10845 | LANGTON MATRAVERS | ISLAND VIEW | S | Private Sewage Pumping Station | INUSE
10846 | ALMONDSBURY | 3 OLD AUST ROAD | N | Private Sewage Pumping Station | INUSE
10847 | BATH | THE PODIUM | N | Sewage Pumping Station | INUSE
10850 | ILTON | CHUBBARDS CROSS CARAVAN SITE | W | Private Sewage Pumping Station | INUSE
10851 | CHIPPING SODBURY | 1 COTSWOLD ROAD | N | Private Sewage Pumping Station | INUSE
10852 | CHARMOUTH | HIGHLANDS | S | Private Sewage Pumping Station | INUSE
10854 | PEN ELM | WYVALE GARDEN CENTRE | W | Private Sewage Pumping Station | INUSE
10856 | CHIDEOCK | MILL LANE | S | S105A Sewage Pumping Station | INUSE
10861 | PORTISHEAD | LAKESIDE TEAM ROOMS | W | Private Sewage Pumping Station | INUSE
10863 | TAUNTON | FROBISHER WAY | W | Private Sewage Pumping Station | INUSE
10864 | BRISTOL | BISHOPTHORPE ROAD | N | Sewage Pumping Station | INUSE
10868 | BANWELL | CHARLTON | W | S105A Sewage Pumping Station | INUSE
10874 | MINEHEAD | BEECHFIELD HOUSE FOUL | W | Private Sewage Pumping Station | INUSE
10875 | MINEHEAD | BEECHFIELD HOUSE SURFACE | W | Private Sewage Pumping Station | INUSE
10876 | NEWTON ST. LOE | NEWTON MILL CARAVAN PARK | N | Private Sewage Pumping Station | INUSE
10877 | TROWBRIDGE | MCDONALDS RESTAURANT | N | Private Sewage Pumping Station | INUSE
10880 | KILMERSDON | 4 MANOR CLOSE | W | Private Sewage Pumping Station | INUSE
10882 | TAUNTON | ELLISFIELDS COURT | W | Private Sewage Pumping Station | INUSE
10890 | POOLE | PARKSTONE BAY MARINA | S | Private Sewage Pumping Station | INUSE
10891 | WRINGTON | ADJACENT CINDERFORD COTTAGE | N | Private Sewage Pumping Station | INUSE
10892 | PORTISHEAD | WETLANDS LANE | W | S105A Sewage Pumping Station | INUSE
10897 | BRISTOL | ANCHOR ROAD | N | Private Sewage Pumping Station | INUSE
10902 | ILMINSTER | HOLWAY HOUSE PARK | W | Private Sewage Pumping Station | INUSE
10903 | WOTTON-UNDER-EDGE | LISLE COTTAGE | N | Private Sewage Pumping Station | INUSE
10904 | BRISTOL | SHARLAND CLOSE | N | S105A Sewage Pumping Station | INUSE
10905 | POOLE | COBBS QUAY MARINA 2 | S | Private Sewage Pumping Station | INUSE
10906 | HIGHBRIDGE | OLDWAY PLACE | W | Sewage Pumping Station | INUSE
10907 | WOTTON-UNDER-EDGE | COLOUR TECH DYERS BROOK | N | Private Sewage Pumping Station | INUSE
10908 | WESTON-SUPER-MARE | AISECOME WAY SURFACE WATER | W | Sewage Pumping Station | INUSE
10910 | GILLINGHAM | BARLEY COTTAGE | S | S105A Sewage Pumping Station | INUSE
10911 | LANGFORD | STOCK LANE FARM | N | Private Sewage Pumping Station | INUSE
10912 | WESTON-SUPER-MARE | ARUNDELL COURT | W | S105A Sewage Pumping Station | INUSE
10913 | BRISTOL | MERLIN COURT | N | Private Sewage Pumping Station | INUSE
10916 | WARMINSTER | 14 ROBIN CLOSE | N | Private Sewage Pumping Station | INUSE
10919 | FRENCHAY | STONELEIGH | N | Private Sewage Pumping Station | INUSE
10920 | KINGSTON | GRENESTEDE | S | S105A Sewage Pumping Station | INUSE
10922 | POOLE | 36 BLAKE HILL CRESCENT | S | Private Sewage Pumping Station | INUSE
10923 | STAPLETON | OAK BARN | W | S105A Sewage Pumping Station | INUSE
10929 | LYNEHAM | CHURCH LANE | N | S105A Sewage Pumping Station | INUSE
10930 | LANGFORD BUDVILLE | 7 COURTLANDS | W | S105A Sewage Pumping Station | INUSE
10942 | BATH | IVY AVENUE SURFACE WATER | N | Combined Sewer Overflow | INUSE
10944 | BRISTOL | 74 BIFIELD ROAD SURFACE WATER | N | Combined Sewer Overflow | INUSE
10946 | BRISTOL | JUNCTION FORTFIELD AND BRIERYLEAZE ROAD SURFACE WATER | N | Combined Sewer Overflow | INUSE
10947 | BRISTOL | OS 25 MONK ROAD SURFACE WATER | N | Combined Sewer Overflow | INUSE
10949 | BRISTOL | SALTMARSH DRIVE SURFACE WATER | N | Combined Sewer Overflow | INUSE
10950 | MILTON | JUNCTION GROVE ROAD AND UPPER BRISTOL ROAD | W | Combined Sewer Overflow | INUSE
10952 | CHARD | HOLBEAR GRANGE | W | S105A Sewage Pumping Station | INUSE
10953 | BOURNEMOUTH | 982C RINGWOOD ROAD | S | S105A Sewage Pumping Station | INUSE
10954 | SOUTH PETHERTON | HELE COTTAGES | W | Sewage Pumping Station | INUSE
10955 | NAILSEA | ARGENTUM LODGE | W | Private Sewage Pumping Station | INUSE
10956 | BRISTOL | QUEENS SQUARE | N | Private Sewage Pumping Station | INUSE
10957 | WARMLEY | MATROW COURT | N | Private Sewage Pumping Station | INUSE
10962 | WEYMOUTH | CHANDLER CLOSE | S | Private Sewage Pumping Station | INUSE
10963 | BARROW GURNEY | WILD COUNTRY LANE | N | Private Sewage Pumping Station | INUSE
10964 | BARROW GURNEY | OLD SCHOOL LODGE | N | Private Sewage Pumping Station | INUSE
10965 | BURCOTT | BURCOTT MILL | W | Private Sewage Pumping Station | INUSE
10966 | BURCOTT | PENNYBATCH LANE | W | Private Sewage Pumping Station | INUSE
10967 | BURNHAM-ON-SEA | LANDFILL LEACHATE | W | Private Sewage Pumping Station | INUSE
10973 | SEVERN BEACH | CHURCHSIDE | N | Private Sewage Pumping Station | INUSE
10974 | RUISHTON | PREMIER INN | W | Private Sewage Pumping Station | INUSE
10975 | RODE | FIVE GABLES | W | Private Sewage Pumping Station | INUSE
10977 | YEOVIL | HENDFORD HILL | W | Private Sewage Pumping Station | INUSE
10979 | BATH | PRIVATE LANE REAR 50 BECKHAMPTON ROAD | N | Combined Sewer Overflow | INUSE
10980 | LYTCHETT MATRAVERS | CASTLE FARM ROAD | S | S105A Sewage Pumping Station | INUSE
10981 | PUDDLETOWN | MEADOW COTTAGE | S | Private Sewage Pumping Station | INUSE
10982 | BINEGAR | GARDEN OF OAKHILL HOUSE | W | S105A Sewage Pumping Station | INUSE
10983 | WESTPORT | THE NOOK (PUMPED NRV) | W | Single Property Pumping Station | INUSE
10984 | WESTPORT | 1 SUNNYSIDE (PUMPED NRV) | W | Single Property Pumping Station | INUSE
10985 | BATH | RIVER HOUSE (PUMPED NRV) | N | Single Property Pumping Station | INUSE
10986 | BATH | PHOENIX HOUSE (PUMPED NRV) | N | Single Property Pumping Station | INUSE
10988 | FORDINGTON | 1-4 MALTHOUSE COTTAGES (PUMPED NRV) | S | Single Property Pumping Station | INUSE
10989 | FORDINGTON | FLATS AT THE MALTHOUSE (PUMPED NRV) | S | Single Property Pumping Station | INUSE
10990 | WESTHAY | TAYPORT MAIN ROAD (PUMPED NRV) | W | Single Property Pumping Station | INUSE
10992 | YARLEY CROSS | RIVERSIDE HOUSE | W | Single Property Pumping Station | INUSE
10993 | CHEW MAGNA | MANOR COTTAGE | N | Single Property Pumping Station | INUSE
10994 | GUYS MARSH | MYRTLE FARM | S | S105A Sewage Pumping Station | INUSE
10995 | BITTON | HARRINGTON CLOSE | N | S105A Sewage Pumping Station | INUSE
10996 | GREAT SOMERFORD | PADDOCK CLOSE | N | Private Sewage Pumping Station | INUSE
11097 | FAILAND | AUDLEY RETIREMENT VILLAGE | W | Private Sewage Pumping Station | INUSE
11107 | BROADSTONE | DUNYEATS ROAD | S | Private Sewage Pumping Station | INUSE
11132 | STURMINSTER NEWTON | THE OLD COTTAGE | S | Private Sewage Pumping Station | INUSE
11155 | ANSFORD | THE NURSERIES | W | Private Sewage Pumping Station | INUSE
11166 | THREE LEGGED CROSS | RINGWOOD ROAD | S | S105A Sewage Pumping Station | INUSE
11189 | STOURPAINE | MANOR ROAD | S | Private Sewage Pumping Station | INUSE
11275 | SALISBURY | LONDON ROAD OFFICE PARK | S | S105A Sewage Pumping Station | INUSE
11280 | BRIDGWATER | WOODLANDS COURT | W | Sewage Pumping Station | INUSE
11307 | WINSLEY | WINSLEY ROAD | N | Private Sewage Pumping Station | INUSE
11343 | TROWBRIDGE | 35 HILPERTON ROAD | N | Private Sewage Pumping Station | INUSE
11345 | NORTH PETHERTON | 37 BROADLANDS AVENUE | W | S105A Sewage Pumping Station | INUSE
11357 | PIDDLETRENTHIDE | WHITE LACKINGTON | S | Private Sewage Pumping Station | INUSE
11363 | BOURNEMOUTH | SHAPLAND AVENUE | S | Private Sewage Pumping Station | INUSE
11393 | WIMBORNE | BEAUCROFT LANE | S | S105A Sewage Pumping Station | INUSE
11398 | JUMPERS COMBE | . | W | S105A Sewage Pumping Station | INUSE
11404 | UPTON | WATERY LANE | S | Private Sewage Pumping Station | INUSE
11426 | WELLINGTON | PYLES THORNE ROAD | W | Private Sewage Pumping Station | INUSE
11446 | RINGWOOD | POPPY OAKDENE FOREST PARK | S | Private Sewage Pumping Station | INUSE
11450 | RINGWOOD | FOXGLOVE OAKDENE FOREST PARK | S | Private Sewage Pumping Station | INUSE
11452 | RINGWOOD | MARIGOLD OAKDENE FOREST PARK | S | Private Sewage Pumping Station | INUSE
11454 | RINGWOOD | AZALEA OAKDENE FOREST PARK | S | Private Sewage Pumping Station | INUSE
11456 | RINGWOOD | SALES OAKDENE FOREST PARK | S | Private Sewage Pumping Station | INUSE
11457 | TROWBRIDGE | HOLBROOK LANE | N | Private Sewage Pumping Station | INUSE
11458 | TROWBRIDGE | HOLBROOK LANE 1 | N | Private Sewage Pumping Station | INUSE
11460 | TRULL | BARTON GREEN | W | S105A Sewage Pumping Station | INUSE
11470 | SPARKFORD | AINSTEY DRIVE | W | Single Property Pumping Station | INUSE
11487 | MELKSHAM | EVANS BUSINESS CENTRE | N | Private Sewage Pumping Station | INUSE
11488 | MELKSHAM | HAMPTON PARK WEST 2 | N | Private Sewage Pumping Station | INUSE
11489 | TAUNTON | GARDEN CLOSE | W | Private Sewage Pumping Station | INUSE
11490 | TAUNTON | GARDEN CLOSE 1 | W | Private Sewage Pumping Station | INUSE
11492 | BERKELEY | GLOUCESTERSHIRE SCIENCE AND TECHNOLOGY PARK | N | Sewage Pumping Station | INUSE
11517 | KINGSBURY EPISCOPI | THORNEY ROAD | W | Private Sewage Pumping Station | INUSE
11519 | BATH | LAWRENCE HOUSE | N | Private Sewage Pumping Station | INUSE
11525 | WIMBORNE | BEAUCROFT LANE 2 | S | S105A Sewage Pumping Station | INUSE
11528 | WIMBORNE | MERLEY LANE | S | Sewage Pumping Station | INUSE
11529 | WEYMOUTH | AUSTRALIA ROAD | S | S105A Sewage Pumping Station | INUSE
11536 | PORTLAND | CHISWELL | S | Private Sewage Pumping Station | INUSE
11537 | BATH | SOUTHSTOKE ROAD 1 | N | Private Sewage Pumping Station | INUSE
11544 | BRISTOL | LONGMOOR COURT | N | S105A Sewage Pumping Station | INUSE
11553 | BURTON BRADSTOCK | CLIFF ROAD | S | Private Sewage Pumping Station | INUSE
11554 | BRISTOL | ST TERESAS COURT | N | Private Sewage Pumping Station | INUSE
11556 | CURRY RIVEL | HOLDENS WAY | W | Private Sewage Pumping Station | INUSE
11559 | TAUNTON | MOUNTSFIELD ROAD | W | Sewage Pumping Station | INUSE
11574 | STREET | DURSTON CLOSE | W | Private Sewage Pumping Station | INUSE
11579 | BISHOPS CAUNDLE | CROFT BARTON | S | S105A Sewage Pumping Station | INUSE
11584 | EASTER COMPTON | WASHINGPOOL FARM | N | Private Sewage Pumping Station | INUSE
11585 | BIBSTONE | PULLINS PLACE | N | Private Sewage Pumping Station | INUSE
11586 | MALMESBURY | GLOUCESTER ROAD 1 | N | Private Sewage Pumping Station | INUSE
11591 | WESTON-SUPER-MARE | TIGER MOTH ROAD | W | Sewage Pumping Station | UPADOPTED
11593 | SALISBURY | SOUTHAMPTON ROAD | S | Private Sewage Pumping Station | INUSE
11595 | NETHER STOWEY | INWOOD FARM | W | Private Sewage Pumping Station | INUSE
11601 | BATH | ENGLISHCOMBE LANE 3 | N | Private Sewage Pumping Station | INUSE
11625 | MIDSOMER NORTON | RADSTOCK ROAD 1 | N | Private Sewage Pumping Station | INUSE
11634 | TROWBRIDGE | OUTMARSH | N | Private Sewage Pumping Station | INUSE
11635 | TROWBRIDGE | OUTMARSH SURFACE | N | Private Sewage Pumping Station | INUSE
11649 | HIGHCLIFFE | ROTHESAY DRIVE | S | Private Sewage Pumping Station | INUSE
11666 | BOURNEMOUTH | MURLEY ROAD | S | S105A Sewage Pumping Station | INUSE
11667 | FROME | MARSTON PARK ESTATE | N | Private Sewage Pumping Station | INUSE
11674 | CHRISTCHURCH | MAY GARDENS SURFACE WATER | S | S105A Sewage Pumping Station | INUSE
11682 | BRISTOL | ST. STEPHENS AVENUE | N | Private Sewage Pumping Station | INUSE
11683 | CURRY RIVEL | HOLDENS WAY 1 | W | Private Sewage Pumping Station | INUSE
11689 | WEST CHINNOCK | BREECH FARM | W | Private Sewage Pumping Station | INUSE
11692 | SALISBURY | GLENMORE BUSINESS PARK | N | Private Sewage Pumping Station | INUSE
11695 | NORTON ST. PHILIP | TOWN BARTON | N | Private Sewage Pumping Station | INUSE
11700 | BRISTOL | WHITTUCKS ROAD 1 | N | Private Sewage Pumping Station | INUSE
11703 | BRISTOL | WHITTUCKS ROAD 2 | N | Private Sewage Pumping Station | INUSE
11718 | MALMESBURY | GLOUCESTER ROAD | N | Private Sewage Pumping Station | INUSE
11722 | TROWBRIDGE | CASTLE HEDINGHAM | N | Sewage Pumping Station | INUSE
11728 | WELLS | CHAMBERLAIN STREET | W | Private Sewage Pumping Station | INUSE
11732 | BRIDPORT | LEE LANE 2 | S | Private Sewage Pumping Station | INUSE
11733 | CHRISTCHURCH | STONY LANE | S | Private Sewage Pumping Station | INUSE
11741 | CHRISTCHURCH | BRIDGE STREET | S | Private Sewage Pumping Station | INUSE
11743 | SALISBURY | TOWN PATH | N | Private Sewage Pumping Station | INUSE
11745 | WELLINGTON | FOXDOWN HILL | W | Private Sewage Pumping Station | INUSE
11749 | BRISTOL | CONHAM VIEW | N | Private Sewage Pumping Station | INUSE
11751 | BATH | WESTON PARK 1 | N | Private Sewage Pumping Station | INUSE
11752 | BATH | WESTON PARK 2 | N | Private Sewage Pumping Station | INUSE
11754 | BOURNEMOUTH | IFORD LANE | S | Combined Sewer Overflow | INUSE
11790 | BRISTOL | GLASS WHARF | N | Private Sewage Pumping Station | INUSE
11792 | BRISTOL | MORRISONS FISHPONDS ROAD 2 | N | Private Sewage Pumping Station | INUSE
11801 | STURMINSTER NEWTON | BACK LANE | S | S105A Sewage Pumping Station | INUSE
11803 | BRISTOL | NORTHWAY | N | Private Sewage Pumping Station | INUSE
11805 | POOLE | STEPNELL REACH | S | Private Sewage Pumping Station | INUSE
11809 | CHICKERELL | BROWNS CRESCENT | S | Private Sewage Pumping Station | INUSE
11810 | HIGHCLIFFE | MONTAGU ROAD | S | Private Sewage Pumping Station | INUSE
11811 | HIGHCLIFFE | LYMINGTON ROAD SURFACE | S | Private Sewage Pumping Station | INUSE
11813 | VERWOOD | SANDY LANE | S | Private Sewage Pumping Station | INUSE
11818 | ASHCOTT | STATION ROAD | W | Private Sewage Pumping Station | INUSE
11819 | CHRISTCHURCH | HURN WAY | S | Private Sewage Pumping Station | INUSE
11820 | WANSTROW | KILN CLOSE | W | Private Sewage Pumping Station | INUSE
11821 | BRISTOL | DOWNMAN ROAD SURFACE | N | Private Sewage Pumping Station | INUSE
11825 | FROME | CRITCH HILL | W | Private Sewage Pumping Station | INUSE
11828 | BISHOPSTONE | BUTT LANE | N | Private Sewage Pumping Station | INUSE
11829 | SHERSTON | OLD SILK MILL | N | Private Sewage Pumping Station | INUSE
11873 | WESTON-SUPER-MARE | WESTON COLLEGE SOUTH WEST SKILLS CAMPUS | W | Private Sewage Pumping Station | INUSE
11874 | HULLAVINGTON | 15 BELFRY DRIVE | N | Private Sewage Pumping Station | INUSE
11875 | WINTERBOURNE GUNNER | THE PORTWAY | S | Private Sewage Pumping Station | INUSE
11876 | FALFIELD | EASTWOOD PARK | N | Sewage Pumping Station | INUSE
11877 | CORFE MULLEN | 15 THE HIDEAWAY | S | Private Sewage Pumping Station | INUSE
11879 | STREET | FARM LANE | W | Sewage Pumping Station | INUSE
11882 | BOURNEMOUTH | 4 RIVER PARK IFORD LANE | S | Private Sewage Pumping Station | INUSE
11885 | BATH | WHITEWAY ROAD | N | Private Sewage Pumping Station | INUSE
11886 | WELLS | THOMPSON ROAD | W | Sewage Pumping Station | INUSE
11887 | NAILSEA | 15 HEATH ROAD | W | Private Sewage Pumping Station | INUSE
11888 | FRAMPTON COTTERELL | 2 FRAMPTON END ROAD | N | S105A Sewage Pumping Station | INUSE
11891 | HAYWOOD VILLAGE | COBHAM PARADE | W | Private Sewage Pumping Station | INUSE
11892 | WESTBURY | 80A WARMINSTER ROAD | N | S105A Sewage Pumping Station | INUSE
11894 | KEYNSHAM | LIMEKILNS CLOSE | N | S105A Sewage Pumping Station | INUSE
11897 | RINGWOOD | KINGS ARMS LANE | S | Private Sewage Pumping Station | INUSE
11898 | BRIDGWATER | WILLOW DOWN PRIMARY ACADEMY | W | Sewage Pumping Station | INUSE
11899 | WATCHET | SEA VIEW TERRACE | W | Private Sewage Pumping Station | INUSE
11900 | FERNDOWN | PREMIER INN FOUL AND SURFACE | S | Private Sewage Pumping Station | INUSE
11901 | BRIDGWATER | THE BOWER INN PUBLIC HOUSE | W | Private Sewage Pumping Station | INUSE
11902 | FISHPONDS | MANOR ROAD | N | Private Sewage Pumping Station | INUSE
11903 | TISBURY | KNAPP HOLLOW | S | Private Sewage Pumping Station | INUSE
11904 | NORTON SUB HAMDON | STABLES RECTORY LANE | W | Single Property Pumping Station | INUSE
11905 | STOKE BISHOP | THE DELL CHURCH ROAD | N | Private Sewage Pumping Station | INUSE
11908 | ASH PRIORS | COURT HOUSE BARN | W | S105A Sewage Pumping Station | INUSE
11909 | CORFE MULLEN | OLIVIA CLOSE | S | Private Sewage Pumping Station | INUSE
11910 | BOURNEMOUTH | BOSCOMBE OVERCLIFF DRIVE SURFACE WATER | S | Private Sewage Pumping Station | INUSE
11911 | POOLE | TATNAM ROAD | S | S105A Sewage Pumping Station | INUSE
11912 | MANNINGFORD BRUCE | MILL ROAD | N | Private Sewage Pumping Station | INUSE
11916 | CHRISTIAN MALFORD | THE HAWTHORNS | N | S105A Sewage Pumping Station | INUSE
11920 | POOLE | RNLI COVENTINA | S | Private Sewage Pumping Station | INUSE
11921 | BRISTOL | HAMPTON ROAD | N | Sewage Pumping Station | INUSE
11922 | BOURNEMOUTH | MAXWELL ROAD | S | Combined Sewer Overflow | INUSE
11924 | SHIREHAMPTON | STATION ROAD O/S 50 | N | Combined Sewer Overflow | INUSE
11925 | SWANAGE | PEVERIL POINT ROAD O/S 27 | S | S105A Sewage Pumping Station | INUSE
11926 | DOWNTON | BRIAN WHITEHEAD SPORTS CENTRE WICK LANE | S | Private Sewage Pumping Station | INUSE
11927 | WEST WICK | ST ANNES SCHOOL | W | Private Sewage Pumping Station | INUSE
11932 | ROYAL WOOTTON BASSETT | 36 NEW ROAD | N | Private Sewage Pumping Station | INUSE
11938 | CLEVEDON | HAND EQUESTRIAN CENTRE | W | Private Sewage Pumping Station | INUSE
11939 | SHAFTESBURY | ABBEYFIELD HOUSE BLEKE STREET | S | Private Sewage Pumping Station | INUSE
11940 | LYTCHETT MATRAVERS | ADAMS PRACTICE HIGH STREET | S | Private Sewage Pumping Station | INUSE
11941 | HALLEN | MOORHOUSE CARAVANS | N | Private Sewage Pumping Station | INUSE
11942 | ALMONDSBURY | GLOUCESTER ROAD | N | Private Sewage Pumping Station | INUSE
11944 | COMBE DOWN | THE BATH CLINIC | N | Private Sewage Pumping Station | INUSE
11945 | BRIDGWATER | BRIDGEWATER WAREHOUSING CO LTD | W | Private Sewage Pumping Station | INUSE
11946 | CANNINGTON | BRYMORE ACADEMY | W | Private Sewage Pumping Station | INUSE
11947 | WOTTON-UNDER-EDGE | SYMN LANE CLINIC | N | Private Sewage Pumping Station | INUSE
11950 | HAMBROOK | THE LAURELS MILL LANE | N | Private Sewage Pumping Station | INUSE
11951 | HAMBROOK | MARIGOLD COURT MILL LANE | N | S105A Sewage Pumping Station | INUSE
11952 | TROWBRIDGE | HILPERTON ROAD | N | S105A Sewage Pumping Station | INUSE
11953 | CHEDDAR | SHARPHAM ROAD | W | Private Sewage Pumping Station | INUSE
11955 | BATH | BEECHWOOD ROAD | N | Private Sewage Pumping Station | INUSE
11958 | BATH | FOREFIELDS | N | Private Sewage Pumping Station | INUSE
11959 | BRISTOL | COLSTON COLLEGIATE SCHOOL | N | Private Sewage Pumping Station | INUSE
11960 | KEYNSHAM | THE CO-OPERATIVE GROUP | N | Private Sewage Pumping Station | INUSE
11961 | BOURNEMOUTH | CORPUS CHRISTI CENTRE 1 | S | Private Sewage Pumping Station | INUSE
11962 | BOURNEMOUTH | CORPUS CHRISTI CENTRE 2 | S | Private Sewage Pumping Station | INUSE
11963 | CORFE MULLEN | COVENTRY ARMS | S | S105A Sewage Pumping Station | INUSE
11964 | WEST LAVINGTON | DAUNTSEYS SCHOOL | N | Private Sewage Pumping Station | INUSE
11966 | LONGWELL GREEN | ALDI | N | Private Sewage Pumping Station | INUSE
11967 | POOLE | ST MARGARETS ROAD | S | Private Sewage Pumping Station | INUSE
11968 | TOCKINGTON | STONELEIGH DOWN | N | Private Sewage Pumping Station | INUSE
11969 | BRIDPORT | WEST BAY ROAD | S | Private Sewage Pumping Station | INUSE
11971 | SHERBORNE | SHERBORNE LIBRARY | S | Private Sewage Pumping Station | INUSE
11972 | YEOVIL | HENDFORD LODGE SURGERY | W | Private Sewage Pumping Station | INUSE
11973 | FERNDOWN | FAIRLAWNS REST HOME | S | Private Sewage Pumping Station | INUSE
11974 | RINGWOOD | FISH INN | S | Private Sewage Pumping Station | INUSE
11975 | POOLE | FLEETSPOINT BUSINESS CENTRE | S | Private Sewage Pumping Station | INUSE
11976 | POOLE | THE LAURELS & PINE LODGE FOXHOLES ROAD | S | Private Sewage Pumping Station | INUSE
11977 | TROWBRIDGE | BRADLEY ROAD | N | Private Sewage Pumping Station | INUSE
11978 | FERNDOWN | GLADELANDS PARK | S | Private Sewage Pumping Station | INUSE
11979 | FERNDOWN | GLADELANDS PARK | S | Private Sewage Pumping Station | INUSE
11980 | WHATLEY | HANSON AGGREGATES | W | Private Sewage Pumping Station | INUSE
11981 | POOLE | HARBOUR PROSPECT | S | Private Sewage Pumping Station | INUSE
11982 | HIGHCLIFFE | HIGHCLIFFE CASTLE | S | Private Sewage Pumping Station | INUSE
11983 | CHRISTCHURCH | IFORD BRIDGE BOWLING CLUB | S | Private Sewage Pumping Station | INUSE
11984 | ALMONDSBURY | INTEGRAL | N | Private Sewage Pumping Station | INUSE
11985 | DEVIZES | LATCHWAYS PLC | N | Private Sewage Pumping Station | INUSE
11986 | BRISTOL | FEEDER ROAD | N | Private Sewage Pumping Station | INUSE
11987 | FROME | MANOR FURLONG | W | Private Sewage Pumping Station | INUSE
11988 | WESTBURY | MATRAVERS SCHOOL | N | Private Sewage Pumping Station | INUSE
11989 | MELKSHAM | HAMPTON PARK WEST | N | Private Sewage Pumping Station | INUSE
11991 | HATCH BEAUCHAMP | ROSE COTTAGE | W | Private Sewage Pumping Station | INUSE
11992 | POOLE | MITRE COURT | S | Private Sewage Pumping Station | INUSE
11993 | BRIDGWATER | MOLE VALLY FEEDS SOLUTIONS | W | Private Sewage Pumping Station | INUSE
11994 | BATH | GAY STREET | N | Private Sewage Pumping Station | INUSE
11996 | WESTBURY-ON-TRYM | SOUTHMEAD HOSPITAL | N | Private Sewage Pumping Station | INUSE
11997 | BREAN | NORTHAM FARM CAMPING & CARAVAN PARK | W | Private Sewage Pumping Station | INUSE
11998 | BOURNEMOUTH | OCEAN BREEZE | S | Private Sewage Pumping Station | INUSE
11999 | POOLE | PARKSTONE GRAMMAR SCHOOL FOR GIRLS | S | Private Sewage Pumping Station | INUSE
12000 | PORTLAND | OSPREY QUAY | S | Private Sewage Pumping Station | INUSE
12151 | FRAMPTON COTTERELL | PERRINPIT ROAD | N | S105A Sewage Pumping Station | INUSE
12152 | BRADFORD-ON-AVON | ST. MARGARETS STREET 2 | N | Private Sewage Pumping Station | INUSE
12157 | SALISBURY | SHAFTESBURY DROVE | S | Private Sewage Pumping Station | INUSE
12161 | STOKE GIFFORD | CURTIS LANE 1 | N | Private Sewage Pumping Station | INUSE
12162 | STOKE GIFFORD | CURTIS LANE 2 | N | Private Sewage Pumping Station | INUSE
12163 | STOKE GIFFORD | CURTIS LANE 3 | N | Private Sewage Pumping Station | INUSE
12164 | SEVERN BEACH | COLLINS DRIVE | N | Private Sewage Pumping Station | INUSE
12166 | WEYMOUTH | WYKE ROAD 2 | S | Private Sewage Pumping Station | INUSE
12168 | RADSTOCK | FROME ROAD | N | Combined Sewer Overflow | INUSE
12170 | BUCKHORN WESTON | SHEPHERDS HILL | S | S105A Sewage Pumping Station | INUSE
12172 | POOLE | POINT SOUTH | S | Private Sewage Pumping Station | INUSE
12175 | SWYRE | TOPPE COTTAGE | S | Private Sewage Pumping Station | INUSE
12177 | BRIDPORT | WEST BAY ROAD 2 | S | Private Sewage Pumping Station | INUSE
12178 | WEYMOUTH | PRESTON BEACH ROAD | S | Private Sewage Pumping Station | INUSE
12179 | HORTON | POTTERY ROAD | W | S105A Sewage Pumping Station | INUSE
12181 | CHRISTCHURCH | AMBASSADOR INDUSTRIAL ESTATE AIRFIELD ROAD | S | Private Sewage Pumping Station | INUSE
12182 | ACTON TURVILLE | SODBURY ROAD | N | Private Sewage Pumping Station | INUSE
12187 | SHAW | LOWDEN GARDEN NURSERIES | N | Private Sewage Pumping Station | INUSE
12189 | TETBURY | QUERCUS ROAD 2 | N | Private Sewage Pumping Station | INUSE
12190 | POOLE | 61 BANKS ROAD | S | Private Sewage Pumping Station | INUSE
12194 | TROWBRIDGE | TROWBRIDGE OAKS CARE HOME | N | Private Sewage Pumping Station | INUSE
12199 | POOLE | THE QUAY SCHOOL | S | Private Sewage Pumping Station | INUSE
12200 | SWANAGE | HOLM OAKS | S | Private Sewage Pumping Station | INUSE
12201 | PIDDLETRENTHIDE | LACKINGTON MILL | S | Private Sewage Pumping Station | INUSE
12202 | NAILSEA | SILVER STREET | W | Private Sewage Pumping Station | INUSE
12203 | CHARLTON MUSGROVE | PEAR TREE COTTAGE | W | Private Sewage Pumping Station | INUSE
12204 | CHURCHILL | DINGHURST ROAD | W | Private Sewage Pumping Station | INUSE
12205 | GLASTONBURY | HALSALL | W | Private Sewage Pumping Station | INUSE
12206 | UPPER MINETY | FLISTRIDGE FARM | N | Private Sewage Pumping Station | INUSE
12207 | CHRISTCHURCH | AVON LODGE | S | Private Sewage Pumping Station | INUSE
12208 | BATH | MUTHAIGA | N | Private Sewage Pumping Station | INUSE
12209 | WOODFALLS | FERNBANK | S | Private Sewage Pumping Station | INUSE
12210 | BATH | WILDWOOD | N | Private Sewage Pumping Station | INUSE
12211 | BATH | ALTA | N | Private Sewage Pumping Station | INUSE
12212 | BRISTOL | THE QUAYS | N | Private Sewage Pumping Station | INUSE
12213 | KINGSBURY EPISCOPI | KINGSBURY HOUSE | W | Private Sewage Pumping Station | INUSE
12214 | CHRISTCHURCH | REGENT CENTRE | S | Private Sewage Pumping Station | INUSE
12215 | POOLE | R N L I | S | Private Sewage Pumping Station | INUSE
12216 | BERE REGIS | ROBINSWOOD FARM | S | Private Sewage Pumping Station | INUSE
12217 | MEARE | RSPB CAR PARK | W | Private Sewage Pumping Station | INUSE
12218 | BATH | THE AIKMAN EVENTIDE HOME | N | Private Sewage Pumping Station | INUSE
12219 | OWERMOIGNE | SANDYHOLME CARAVAN PARK | S | Private Sewage Pumping Station | INUSE
12220 | BOURNEMOUTH | SEABREEZE | S | Private Sewage Pumping Station | INUSE
12221 | FYFIELD | FYFIELD HOUSE | N | Private Sewage Pumping Station | INUSE
12222 | TAUNTON | SOMERSET COLLEGE OF ARTS & TECHNOLOGY | W | Private Sewage Pumping Station | INUSE
12223 | TAUNTON | SOMERSET COLLEGE OF ARTS & TECHNOLOGY | W | Private Sewage Pumping Station | INUSE
12224 | MIDSOMER NORTON | ST. BENEDICTS RC PRIMARY SCHOOL | W | Private Sewage Pumping Station | INUSE
12225 | POOLE | ST. MARYS RC SCHOOL | S | Private Sewage Pumping Station | INUSE
12226 | BOX | BRENTOR | N | Private Sewage Pumping Station | INUSE
12227 | SWANAGE | 3 VICTORIA ROAD | S | Private Sewage Pumping Station | INUSE
12228 | TAUNTON | SOMERSET PARTNERSHIP NHS FOUNDATION TRUST | W | Private Sewage Pumping Station | INUSE
12230 | SALISBURY | ELIZABETH COURT | S | Private Sewage Pumping Station | INUSE
12231 | FROME | THE ROBINS | W | S105A Sewage Pumping Station | INUSE
12232 | MINEHEAD | WEST SOMERSET COMMUNITY COLLEGE | W | Private Sewage Pumping Station | INUSE
12233 | CORSHAM | CORSHAM COMMERCIAL CENTRE | N | Private Sewage Pumping Station | INUSE
12234 | WELLS | TRAVIS PERKINS TRADING CO LTD | W | Private Sewage Pumping Station | INUSE
12235 | BRIDGWATER | TRAVIS PERKINS TRADING CO LTD | W | Private Sewage Pumping Station | INUSE
12237 | WATCHET | WARREN BAY CARAVAN PARK | W | Private Sewage Pumping Station | INUSE
12238 | BREAN | WARREN FARM HOLIDAY CENTRE | W | Private Sewage Pumping Station | INUSE
12239 | ROOKSBRIDGE | SEDGEMOOR SERVICES | W | Private Sewage Pumping Station | INUSE
12240 | DORCHESTER | WELDMAR HOSPICECARE TRUST | S | Private Sewage Pumping Station | INUSE
12241 | KEYNSHAM | T A CENTRE | N | Private Sewage Pumping Station | INUSE
12242 | WEYMOUTH | WEYMOUTH COLLEGE | S | Private Sewage Pumping Station | INUSE
12243 | BURNHAM-ON-SEA | LAKESIDE HOLIDAY PARK | W | Private Sewage Pumping Station | INUSE
12244 | BURNHAM-ON-SEA | LAKESIDE HOLIDAY PARK 2 | W | Private Sewage Pumping Station | INUSE
12245 | DRAYCOT CERNE | DRAYCOT | N | Private Sewage Pumping Station | INUSE
12246 | BURNHAM-ON-SEA | SHELLEY CLOSE | W | Sewage Pumping Station | INUSE
12247 | WORLE | FUSSELLS COURT | W | Private Sewage Pumping Station | INUSE
12248 | BRIDGWATER | CROSSWAYS ROAD | W | Private Sewage Pumping Station | INUSE
12249 | SHAFTESBURY | COLES TRACTORS | S | Private Sewage Pumping Station | INUSE
12250 | WALFORD CROSS | WALFORD HOUSE | W | Private Sewage Pumping Station | INUSE
12251 | BRISTOL | TALBOT ROAD | N | Private Sewage Pumping Station | INUSE
12253 | TIDWORTH | BAYEUX MEWS | S | Private Sewage Pumping Station | INUSE
12254 | CONGRESBURY | CONGRESBURY SERVICE STATION | W | S105A Sewage Pumping Station | INUSE
12255 | POOLE | 29A LAKESIDE ROAD SURFACE | S | Private Sewage Pumping Station | INUSE
12256 | POOLE | 29 LAKESIDE ROAD SURFACE | S | Private Sewage Pumping Station | INUSE
12257 | DURRINGTON | IVORS COURT | S | Private Sewage Pumping Station | INUSE
12260 | BRISTOL | R/O 3 WILLIS ROAD | N | Combined Sewer Overflow | INUSE
12263 | MINEHEAD | A SMITH MEMORIALS | W | Private Sewage Pumping Station | INUSE
12264 | RINGWOOD | MCDONALDS | S | Private Sewage Pumping Station | INUSE
12265 | YETMINSTER | THORNFORD ROAD | S | Private Sewage Pumping Station | INUSE
12266 | EVERCREECH | KINGFISHER ROAD | W | Sewage Pumping Station | INUSE
12267 | PORTISHEAD | AVON AND SOMERSET POLICE | W | Private Sewage Pumping Station | INUSE
12268 | MARNHULL | GODDARDS LANE | S | Private Sewage Pumping Station | INUSE
12273 | PORTLAND | THUMB LANE | S | Private Sewage Pumping Station | INUSE
12274 | TAUNTON | SHERLAND HEIGHTS | W | Private Sewage Pumping Station | INUSE
12275 | BROADSTONE | HARRABY GREEN | S | Private Sewage Pumping Station | INUSE
12279 | CHRISTCHURCH | PREMIER INN (EXISTING) | S | Private Sewage Pumping Station | INUSE
12280 | CHRISTCHURCH | PREMIER INN (NEW) | S | Private Sewage Pumping Station | INUSE
12281 | BATHEASTON | LOWER NORTHEND | N | Private Sewage Pumping Station | INUSE
12282 | BERROW | NO 4 MANOR CLOSE | W | Sewage Pumping Station | INUSE
12283 | BERROW | NO 3 MANOR DRIVE | W | Sewage Pumping Station | INUSE
12288 | RINGWOOD | MANOR ROAD | S | S105A Sewage Pumping Station | INUSE
12290 | LYTCHETT MATRAVERS | ELDONS DROVE | S | S105A Sewage Pumping Station | INUSE
12291 | BATHPOOL | TAUNTON RUGBY FOOTBALL CLUB | W | Private Sewage Pumping Station | INUSE
12292 | CHIDEOCK | RIDWOOD ESTATE SURFACE WATER | S | Private Sewage Pumping Station | INUSE
12294 | BRISTOL | PERCIVAL ROAD SURFACE SINGLE PROPERTY | N | Private Sewage Pumping Station | INUSE
12298 | FROME | 11A STYLES AVENUE | W | Private Sewage Pumping Station | INUSE
12303 | ILFORD | THE LODGE | W | Private Sewage Pumping Station | INUSE
12304 | UPPER MINETY | ORCHARD COTTAGE | N | Private Sewage Pumping Station | INUSE
12306 | TAUNTON | TAUNTON PRIVATE SEWAGE PUMPING STATION | W | Private Sewage Pumping Station | INUSE
12307 | BEAMINSTER | BANKSIDE VIEW | S | Private Sewage Pumping Station | INUSE
12308 | DUNBALL | ADMIRALS TABLE | W | Private Sewage Pumping Station | INUSE
12309 | DUNBALL | ADMIRALS TABLE SW | W | Private Sewage Pumping Station | INUSE
12312 | WEYMOUTH | WYKE ROAD | S | Private Sewage Pumping Station | INUSE
12313 | BRISTOL | DEAN ROAD | N | S105A Sewage Pumping Station | INUSE
12314 | PORTISHEAD | THE SALTINGS | W | S105A Sewage Pumping Station | INUSE
12315 | BRIDPORT | GROVE NURSERIES | S | Private Sewage Pumping Station | INUSE
12316 | CHILD OKEFORD | COOPER GARDENS | S | Private Sewage Pumping Station | INUSE
12317 | MARNHULL | BUTTS CLOSE | S | S105A Sewage Pumping Station | INUSE
12318 | BLANDFORD FORUM | RUSSELL COURT | S | S105A Sewage Pumping Station | INUSE
12319 | IWERNE MINSTER | MILES FIELD | S | S105A Sewage Pumping Station | INUSE
12320 | WEYMOUTH | KIRTLETON AVENUE | S | Private Sewage Pumping Station | INUSE
12321 | BOURNEMOUTH | TALBOT AVENUE | S | S105A Sewage Pumping Station | INUSE
12322 | HINTON | HINTON ADMIRAL MEWS | S | Private Sewage Pumping Station | INUSE
12323 | WESTON-SUPER-MARE | WATERS EDGE | W | Private Sewage Pumping Station | INUSE
12326 | NEW ROAD | FERNDOWN | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
12327 | BOURNEMOUTH | PELHAMS PARK | S | Private Sewage Pumping Station | INUSE
12329 | BURNHAM-ON-SEA | GOLF LINKS ROAD | W | Private Sewage Pumping Station | INUSE
12332 | CURRY RIVEL | BREACH COTTAGE | W | Private Sewage Pumping Station | INUSE
12333 | CURRY RIVEL | 1 CURRYWOODS WAY | W | Private Sewage Pumping Station | INUSE
12334 | CURRY RIVEL | 2 CURRYWOODS WAY | W | Private Sewage Pumping Station | INUSE
12335 | BRIDGWATER | DURLEIGH ROAD | W | Private Sewage Pumping Station | INUSE
12336 | BERROW | JESAMA HURN LANE | W | Private Sewage Pumping Station | INUSE
12337 | STAPLE HILL | PAMELA HOUSE | N | Private Sewage Pumping Station | INUSE
12341 | HIGHCLIFFE | 35 WHARNCLIFFE ROAD SURFACE WATER | S | Private Sewage Pumping Station | INUSE
12342 | BOURNEMOUTH | J/O MAXWELL ROAD AND LINWOOD ROAD | S | Combined Sewer Overflow | INUSE
12343 | GLASTONBURY | 59C THE ROMAN WAY | W | Private Sewage Pumping Station | INUSE
12344 | KNOWLE | THE SQUARE | N | Combined Sewer Overflow | INUSE
12345 | BATH | NEWBRIDGE ROAD PARK AND RIDE | N | Private Sewage Pumping Station | INUSE
12346 | RINGWOOD | 42B BROADSHARD LANE | S | S105A Sewage Pumping Station | INUSE
12347 | MONKTON COMBE | BRASSKNOCKER HILL | N | Private Sewage Pumping Station | INUSE
12348 | CLEVEDON | PRINCES ROAD | W | S105A Sewage Pumping Station | INUSE
12349 | GLASTONBURY | MOORVIEW | W | Private Sewage Pumping Station | INUSE
12353 | BURNHAM-ON-SEA | FRENSHAM THE DRIVE | W | Private Sewage Pumping Station | INUSE
12354 | BURNHAM-ON-SEA | FRENSHAM THE DRIVE | W | Private Sewage Pumping Station | INUSE
12356 | STOKE GIFFORD | BRISTOL TECHNOLOGY AND ENGINEERING ACADEMY | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
12357 | NESTON | FOXSTONE HOUSE | N | Private Sewage Pumping Station | INUSE
12360 | MERRIOTT | GLEBE PLACE | W | Private Sewage Pumping Station | INUSE
12361 | BRISTOL | WILLOW CLOSE | N | Private Sewage Pumping Station | INUSE
12362 | GOMELDON | THE PADDOCK | S | S105A Sewage Pumping Station | INUSE
12363 | BRISTOL | GLEN VIEW | N | S105A Sewage Pumping Station | INUSE
12364 | WESTON-SUPER-MARE | APPLE FARM LANE | W | S105A Sewage Pumping Station | INUSE
12365 | BRIDPORT | HOMEBREDY HOUSE SURFACE | S | Private Sewage Pumping Station | INUSE
12366 | POOLE | LAKESIDE ROAD | S | S105A Sewage Pumping Station | INUSE
12367 | BRIDGWATER | HAYWATER AVENUE | W | Sewage Pumping Station | INUSE
12368 | BRISTOL | OVERNDALE ROAD | N | Private Sewage Pumping Station | INUSE
12369 | HORTON | LANGWORTHY ORCHARD | W | Sewage Pumping Station | INUSE
12371 | WESTON-SUPER-MARE | EBDON ROAD | W | S105A Sewage Pumping Station | INUSE
12372 | FRAMPTON COTTERELL | WATERMORE CLOSE | N | S105A Sewage Pumping Station | INUSE
12373 | STURMINSTER NEWTON | WESTERLEY | S | S105A Sewage Pumping Station | INUSE
12374 | BROADWAY | TICINO | W | S105A Sewage Pumping Station | INUSE
12375 | LANGTON MATRAVERS | MALTHOUSE COTTAGE | S | S105A Sewage Pumping Station | INUSE
12376 | BRIDGWATER | THE GEORGE WILLIAMS CENTRE | W | Private Sewage Pumping Station | INUSE
12377 | HANHAM | 136 MEMORIAL ROAD | N | Private Sewage Pumping Station | INUSE
12380 | GILLINGHAM | BABERTON | S | Private Sewage Pumping Station | INUSE
12381 | CHALBURY | EBONY COTTAGE | S | Private Sewage Pumping Station | INUSE
12384 | BRISTOL | BELOE ROAD | N | Private Sewage Pumping Station | INUSE
12385 | SALISBURY | ROLLESTONE STREET | S | Private Sewage Pumping Station | INUSE
12386 | CODFORD | BROADLEAZE | N | Private Sewage Pumping Station | INUSE
12387 | BRIDGWATER | BRIDGWATER COLLEGE SURFACE | W | Private Sewage Pumping Station | INUSE
12388 | BRIDGWATER | BRIDGWATER COLLEGE FOUL | W | Private Sewage Pumping Station | INUSE
12389 | TIDWORTH | TIDWORTH SERVICE STATION | N | Private Sewage Pumping Station | INUSE
12390 | WILTON | RUSSELL STREET | S | S105A Sewage Pumping Station | INUSE
12391 | POOLE | MORICONIUM QUAY 1 | S | S105A Sewage Pumping Station | INUSE
12392 | POOLE | MORICONIUM QUAY 2 | S | S105A Sewage Pumping Station | INUSE
12393 | POOLE | MORICONIUM QUAY 3 | S | S105A Sewage Pumping Station | INUSE
12394 | WIMBORNE ST. GILES | ASH LEAH COTTAGES | S | Private Sewage Pumping Station | INUSE
12395 | BOURNEMOUTH | WIMBORNE HOUSE | S | Private Sewage Pumping Station | INUSE
12397 | NYNEHEAD | 8 BLACKDOWN VIEW | W | Private Sewage Pumping Station | INUSE
12398 | WOTTON-UNDER-EDGE | SYMN LANE | N | Private Sewage Pumping Station | INUSE
12399 | HIGHCLIFFE | WILLIAM COURT | S | Private Sewage Pumping Station | INUSE
12401 | CHRISTCHURCH | DOUGLAS COURT | S | Private Sewage Pumping Station | INUSE
12402 | POOLE | DAISY CLOSE | S | S105A Sewage Pumping Station | INUSE
12403 | POOLE | BOND ROAD | S | S105A Sewage Pumping Station | INUSE
12404 | POOLE | LATIMER COURT | S | Private Sewage Pumping Station | INUSE
12405 | WESTBURY-ON-TRYM | ROBIN CLOSE | N | Private Sewage Pumping Station | INUSE
12406 | GILLINGHAM | GILLINGHAM GRANGE | S | Private Sewage Pumping Station | INUSE
12407 | NAILSEA | QUARRY WAY | W | Private Sewage Pumping Station | INUSE
12409 | POOLE | 21A GUEST AVENUE | S | Private Sewage Pumping Station | INUSE
12410 | BOURNEMOUTH | BAY VIEW GARDENS | S | Private Sewage Pumping Station | INUSE
12411 | POOLE | DELPHINA CHASE | S | Private Sewage Pumping Station | INUSE
12412 | POOLE | FALCON HEIGHTS | S | Private Sewage Pumping Station | INUSE
12413 | BOURNEMOUTH | HAMILTON COURT | S | Private Sewage Pumping Station | INUSE
12414 | POOLE | HARBOUR REACH | S | Private Sewage Pumping Station | INUSE
12415 | BRISTOL | SEAWALLS | N | S105A Sewage Pumping Station | INUSE
12416 | EASTVILLE | MAYTREES | N | Private Sewage Pumping Station | INUSE
12417 | ST. ANNES PARK | THE PUMP HOUSE | N | Private Sewage Pumping Station | INUSE
12418 | MAIDEN BRADLEY | CHESTNUT CLOSE | N | S105A Sewage Pumping Station | INUSE
12422 | WELLS | KEWARD MILL TRADING ESTATE | W | S105A Sewage Pumping Station | INUSE
12424 | BLAGDON | DIPLAND GROVE FARM | W | S105A Sewage Pumping Station | INUSE
12425 | EYPE | 2 MOUNT COTTAGES | S | Private Sewage Pumping Station | INUSE
12426 | MIDSOMER NORTON | RADSTOCK ROAD | N | S105A Sewage Pumping Station | INUSE
12427 | NURSTEED | NURSTEED MEADOWS | N | S105A Sewage Pumping Station | INUSE
12428 | EVERCREECH | LEIGHTON LANE INDUSTRIAL ESTATE | W | S105A Sewage Pumping Station | INUSE
12429 | DEVIZES | THE NURSERY | N | Private Sewage Pumping Station | INUSE
12431 | LOCKING | 90 ELM TREE ROAD (PUMPED NRV) | W | Single Property Pumping Station | INUSE
12432 | PORTBURY | GORDANO HOUSE MARSH LANE | W | S105A Sewage Pumping Station | INUSE
12433 | BRISTOL | 3 CLEEVE COURT | N | Private Sewage Pumping Station | INUSE
12436 | CONGRESBURY | BLACKBERRY BARN | W | S105A Sewage Pumping Station | INUSE
12437 | NORTH TRIGON | WAREHAM FOREST TOURIST PARK 1 | S | Private Sewage Pumping Station | INUSE
12438 | NORTH TRIGON | WAREHAM FOREST TOURIST PARK 2 | S | Private Sewage Pumping Station | INUSE
12439 | TAUNTON | DOWELL CLOSE | W | S105A Sewage Pumping Station | INUSE
12440 | FILTON | AIRBUS | N | Private Sewage Pumping Station | INUSE
12441 | BATH | APPLE LOFT | N | S105A Sewage Pumping Station | INUSE
12443 | BEAMINSTER | SOUTHGATE | S | S105A Sewage Pumping Station | INUSE
12444 | WARMINSTER | 2 COPHEAP LANE | N | S105A Sewage Pumping Station | INUSE
12445 | NORTON FITZWARREN | THE HAYLOFT | W | S105A Sewage Pumping Station | INUSE
12446 | MATCHAMS | MATCHAMS CLOSE | S | Private Sewage Pumping Station | INUSE
12447 | WEDMORE | FERN COTTAGE | W | Private Sewage Pumping Station | INUSE
12448 | BISHOPDOWN | THE HAMPTON INN FOUL | S | Private Sewage Pumping Station | INUSE
12449 | BISHOPDOWN | THE HAMPTON INN SURFACE | S | Private Sewage Pumping Station | INUSE
12452 | EAST COKER | CHALFONT HOUSE | W | Private Sewage Pumping Station | INUSE
12453 | WALKFORD | CHEWTON WAY | S | Private Sewage Pumping Station | INUSE
12454 | WEYMOUTH | PRESTON ROAD | S | Private Sewage Pumping Station | INUSE
12455 | HENLADE | STOKE ROAD | W | Private Sewage Pumping Station | INUSE
12456 | CHIPPENHAM | ROWDEN LANE | N | S105A Sewage Pumping Station | INUSE
12457 | BOURNEMOUTH | ST. CATHERINES ROAD | S | Private Sewage Pumping Station | INUSE
12460 | BISHOP'S CANNINGS | LYNES YARD | N | S105A Sewage Pumping Station | INUSE
12461 | BAGBOROUGH | HEATHFIELD | W | Private Sewage Pumping Station | INUSE
12462 | LANGTON MATRAVERS | PURBECK RIDGE | S | S105A Sewage Pumping Station | INUSE
12464 | BRISTOL | MAPLE DRIVE | N | Private Sewage Pumping Station | INUSE
12465 | STREET | PORTWAY CRESCENT | W | Private Sewage Pumping Station | INUSE
12466 | STREET | 28 BULLMEAD CLOSE | W | Private Sewage Pumping Station | INUSE
12467 | RINGWOOD | 63 CHRISTCHURCH ROAD | S | Private Sewage Pumping Station | INUSE
12468 | CORSHAM | THE CRESCENT | N | S105A Sewage Pumping Station | INUSE
12469 | MARSHFIELD | TORMARTON ROAD | N | S105A Sewage Pumping Station | INUSE
12470 | MELKSHAM | LONGLEAZE LANE | N | S105A Sewage Pumping Station | INUSE
12471 | ROWDE | FERRIS CLOSE | N | S105A Sewage Pumping Station | INUSE
12473 | MAIDEN NEWTON | ST MARYS CHURCH | S | Private Sewage Pumping Station | INUSE
12474 | CHEDDAR | VALLEY LINE INDUSTRIAL PARK | W | S105A Sewage Pumping Station | INUSE
12475 | BISHOPSWORTH | ORCHARD DRIVE | N | S105A Sewage Pumping Station | INUSE
12478 | BRISTOL | BLACKHORSE LANE | N | S105A Sewage Pumping Station | INUSE
12479 | BRIDGWATER | DURLEIGH ROAD | W | S105A Sewage Pumping Station | INUSE
12480 | TIMSBURY | BRAMBLES | N | S105A Sewage Pumping Station | INUSE
12481 | TIMSBURY | CROCOMBE LODGE | N | S105A Sewage Pumping Station | INUSE
12482 | YATE | THE LAWNS | N | Private Sewage Pumping Station | INUSE
12486 | TISBURY | PARSONAGE MEAD SURFACE | S | Private Sewage Pumping Station | INUSE
12487 | NYNEHEAD | HORNSHAY FARM | W | Private Sewage Pumping Station | INUSE
12489 | WESTBURY | OLDFIELD ROAD | N | S105A Sewage Pumping Station | INUSE
12491 | CHILCOMPTON | SPRING GROVE | W | S105A Sewage Pumping Station | INUSE
12492 | EASTON-IN-GORDANO | ST. GEORGES CHURCH HALL | W | S105A Sewage Pumping Station | INUSE
12495 | ALDERBURY | SPIDERS ISLAND | S | S105A Sewage Pumping Station | INUSE
12496 | FOVANT | MILL COTTAGE | S | Private Sewage Pumping Station | INUSE
12498 | BRENT KNOLL | BRENT KNOLL PRIMARY SCHOOL | W | Sewage Pumping Station | INUSE
12499 | POOLE | IMBRECOURT | S | Private Sewage Pumping Station | INUSE
12515 | CALNE | ATWELL WILSON MOTOR MUSEUM | N | Private Sewage Pumping Station | INUSE
12516 | CONGRESBURY | BRISTOL ROAD 1 | W | Private Sewage Pumping Station | INUSE
12520 | WEYMOUTH | CURTIS WAY | S | Sewage Pumping Station | CONSTRUCT
12522 | POOLE | HARKWOOD DRIVE 1 | S | Combined Sewer Overflow | INUSE
12539 | TETBURY | CATTLE LANE | N | Private Sewage Pumping Station | INUSE
12553 | WICK | TRACEY PARK | N | Private Sewage Pumping Station | INUSE
12556 | WESTERLEIGH | OAKLEY GREEN FARM ABATTOIR | N | Private Sewage Pumping Station | INUSE
12560 | CHRISTIAN MALFORD | APPLEWOOD | N | S105A Sewage Pumping Station | INUSE
12561 | WEYMOUTH | THE DAIRY HOUSE 1 | S | Private Sewage Pumping Station | INUSE
12562 | WEYMOUTH | THE DAIRY HOUSE 2 | S | Private Sewage Pumping Station | INUSE
12563 | CHILTON TRINITY | TRINITY BARNS | W | S105A Sewage Pumping Station | INUSE
12565 | POOLE | SANDBANKS ROAD | S | Private Sewage Pumping Station | INUSE
12566 | BRISTOL | PREMIER INN HILL HOUSE | N | Private Sewage Pumping Station | INUSE
12569 | POOLE | NATASHA GARDENS | S | S105A Sewage Pumping Station | INUSE
12570 | DEVIZES | ANSTIE COURT | N | Private Sewage Pumping Station | INUSE
12573 | BRIMSMORE | BRIMSMORE COURT | W | S105A Sewage Pumping Station | INUSE
12574 | SHAFTESBURY | BLACKMORE VALE FARM | S | Private Sewage Pumping Station | INUSE
12575 | FARLEIGH WICK | INWOODS BARN | N | Private Sewage Pumping Station | INUSE
12576 | FROME | MASONS ARMS | W | Private Sewage Pumping Station | INUSE
12577 | COMBE DOWN | ROCKERY PARK | N | Private Sewage Pumping Station | INUSE
12580 | SHAFTESBURY | THE VALLEY HOUSE HIGHER BLANDFORD ROAD | S | S105A Sewage Pumping Station | INUSE
12581 | BRISTOL | HULSE ROAD | N | Combined Sewer Overflow | INUSE
12582 | BROAD TOWN | PYE LANE | N | S105A Sewage Pumping Station | INUSE
12583 | WESTBURY | CHEMICAL ROAD | N | Private Sewage Pumping Station | INUSE
12584 | MALMESBURY | ABBOTS GARDEN | N | S105A Sewage Pumping Station | INUSE
12585 | UPPER SEAGRY | THE COURTYARD | N | S105A Sewage Pumping Station | INUSE
12591 | MELKSHAM | LONGFORD ROAD | N | Private Sewage Pumping Station | INUSE
12592 | WESTBURY | RAILWAY CLOSE | N | S105A Sewage Pumping Station | INUSE
12596 | CHEDDAR | PETRUTH PADDOCKS CAMPSITE | W | Private Sewage Pumping Station | INUSE
12597 | LYTCHETT MATRAVERS | SANDPIPERS | S | S105A Sewage Pumping Station | INUSE
12598 | BRIDPORT | WOODHOUSE COURT | S | S105A Sewage Pumping Station | INUSE
12601 | YEOVIL | WEST HENDFORD | W | Private Sewage Pumping Station | INUSE
12602 | STARTLEY | WOODMANS WELL | N | S105A Sewage Pumping Station | INUSE
12605 | SEEND | THE STOCKS 2 | N | S105A Sewage Pumping Station | INUSE
12611 | STREET | STRODE COLLEGE SPORTS CENTRE | W | Private Sewage Pumping Station | INUSE
12612 | STREET | STRODE COLLEGE J BLOCK | W | S105A Sewage Pumping Station | INUSE
12613 | BRADLEY GREEN | CANONS COURT MEWS | N | S105A Sewage Pumping Station | INUSE
12614 | NAILSEA | 16 CHANCEL CLOSE | W | Private Sewage Pumping Station | INUSE
12615 | NAILSEA | 14 CHANCEL CLOSE | W | Private Sewage Pumping Station | INUSE
12616 | BRISTOL | CHAPEL COURT | N | Private Sewage Pumping Station | INUSE
12617 | CLIFTON | MORTIMER MEWS | N | Private Sewage Pumping Station | INUSE
12618 | POOLE | ALDER HEIGHTS | S | S105A Sewage Pumping Station | INUSE
12619 | THORNFORD | GRANGE PARK | S | S105A Sewage Pumping Station | INUSE
12621 | WEYMOUTH | BUXTON ROAD | S | S105A Sewage Pumping Station | INUSE
12622 | PORTLAND | WESTON ROAD | S | Private Sewage Pumping Station | INUSE
12624 | POOLE | 3A CRICHEL MOUNT ROAD | S | Private Sewage Pumping Station | INUSE
12625 | POOLE | 3 CRICHEL MOUNT ROAD | S | Private Sewage Pumping Station | INUSE
12627 | AMESBURY | AMESBURY INDUSTRIAL ESTATE | S | S105A Sewage Pumping Station | INUSE
12633 | BRISTOL | ALMOND WALK | N | S105A Sewage Pumping Station | INUSE
12634 | BRISTOL | CAMPBELL COURT | N | S105A Sewage Pumping Station | INUSE
12636 | BRISTOL | HANHAM MILLS | N | S105A Sewage Pumping Station | INUSE
12637 | CURLAND | CHAPEL COTTAGE | W | Private Sewage Pumping Station | INUSE
12639 | STREET | SAINSBURYS SUPERMARKETS FOUL | W | Private Sewage Pumping Station | INUSE
12640 | STREET | SAINSBURYS SUPERMARKETS SURFACE | W | Private Sewage Pumping Station | INUSE
12641 | CHEW STOKE | CHEW VALLEY LAKE TEAROOMS | N | Private Sewage Pumping Station | INUSE
12642 | CHEW STOKE | CHEW VALLEY LAKE PUBLIC TOILETS | N | Private Sewage Pumping Station | INUSE
12643 | CHEW STOKE | CHEW VALLEY LAKE SAILING CLUB | N | Private Sewage Pumping Station | INUSE
12644 | BRISTOL | LEDBURY WALK | N | Private Sewage Pumping Station | INUSE
12645 | SALISBURY | THE CLOSE | S | Combined Sewer Overflow | INUSE
12646 | STAPLE HILL | BROAD STREET | N | Private Sewage Pumping Station | INUSE
12647 | STAPLE HILL | CHRISTCHURCH ROAD | S | Private Sewage Pumping Station | INUSE
12648 | STAPLE HILL | THE BREWERY | S | Private Sewage Pumping Station | INUSE
12649 | ATWORTH | BRADFORD ROAD | N | S105A Sewage Pumping Station | INUSE
12650 | WEDMORE | WESTWALL HOUSE | W | Private Sewage Pumping Station | INUSE
12651 | BLAGDON | STATION ROAD | W | Private Sewage Pumping Station | INUSE
12652 | UBLEY | CLEEVE HILL | N | Private Sewage Pumping Station | INUSE
12653 | RINGWOOD | MANSFIELD ROAD | S | S105A Sewage Pumping Station | INUSE
12654 | RINGWOOD | HIGHTOWN ROAD | S | Private Sewage Pumping Station | INUSE
12659 | WEST LYDFORD | MARDI'S LANE | W | Private Sewage Pumping Station | INUSE
12661 | CHRISTCHURCH | NEWLANDS ROAD | S | Private Sewage Pumping Station | INUSE
12662 | HULLAVINGTON | 16 BELFRY DRIVE | N | Private Sewage Pumping Station | INUSE
12664 | CHARD | GABLES END | W | S105A Sewage Pumping Station | INUSE
12665 | ILMINSTER | TRAVELODGE | W | S105A Sewage Pumping Station | INUSE
12667 | EMERSONS GREEN | BROOK OFFICE PARK UNIT 3 | N | S105A Sewage Pumping Station | INUSE
12668 | GLASTONBURY | SHARPHAM ROAD NO 3 | W | Private Sewage Pumping Station | INUSE
12669 | LYTCHETT MATRAVERS | THE CHEQUERS INN | S | Private Sewage Pumping Station | INUSE
12671 | BOURNEMOUTH | WICK LANE | S | Private Sewage Pumping Station | INUSE
12672 | SALISBURY | FOWLERS HILL | S | Private Sewage Pumping Station | INUSE
12673 | NESTON | NESTON GOSPEL HALL | N | Private Sewage Pumping Station | INUSE
12674 | HORSINGTON | ROOKES HOUSE | W | Private Sewage Pumping Station | INUSE
12676 | MELKSHAM | SPA ROAD | N | Private Sewage Pumping Station | INUSE
12677 | FERNHILL | FERNHILL COURT | N | Private Sewage Pumping Station | INUSE
12678 | WAREHAM | PRIDE PLACE | S | Private Sewage Pumping Station | INUSE
12679 | WARMLEY | STANLEY ROAD | N | Private Sewage Pumping Station | INUSE
12680 | MELKSHAM | MELKSHAM FOOTBALL AND RUGBY CLUB | N | Private Sewage Pumping Station | INUSE
12681 | BOURNEMOUTH | PADDINGTON GROVE SURFACE | S | Private Sewage Pumping Station | INUSE
12682 | BOURNEMOUTH | PADDINGTON GROVE FOUL | S | Private Sewage Pumping Station | INUSE
12683 | BURLEY | BURLEY LAWN | S | Private Sewage Pumping Station | INUSE
12684 | EMERSONS GREEN | BROOK OFFICE PARK UNIT 4 | N | S105A Sewage Pumping Station | INUSE
12685 | EMERSONS GREEN | BROOK OFFICE PARK UNIT 10 | N | S105A Sewage Pumping Station | INUSE
12686 | WESTON SUPER MARE | HERCULES ROAD | W | Private Sewage Pumping Station | INUSE
12687 | WHADDON | WHADDON BUSINESS PARK | S | Private Sewage Pumping Station | INUSE
12691 | WELLS | WELLS COLD STORE | W | S105A Sewage Pumping Station | INUSE
12692 | POOLE | UPPLEBY ROAD | S | S105A Sewage Pumping Station | INUSE
12693 | BRISTOL | KINGS COURT | N | Private Sewage Pumping Station | INUSE
12698 | WELLINGTON | CADES FARM | W | Sewage Pumping Station | INUSE
12699 | BRISTOL | THE BOAT HOUSE | N | Private Sewage Pumping Station | INUSE
12700 | BURNHAM-ON-SEA | STANMOORE | W | Private Sewage Pumping Station | INUSE
12704 | WIMBORNE | MERRIFIELD HEIGHTS | S | S105A Sewage Pumping Station | INUSE
12706 | RADSTOCK | NELSON WARD DRIVE | N | Sewage Pumping Station | INUSE
12707 | NORTH PETHERTON | BAYMEAD LANE | W | Private Sewage Pumping Station | INUSE
12708 | NORTH PETHERTON | BAYMEAD LANE | W | Private Sewage Pumping Station | INUSE
12709 | MINEHEAD | PREMIER INN | W | Private Sewage Pumping Station | INUSE
12711 | RINGWOOD | CHAPEL RISE | S | S105A Sewage Pumping Station | INUSE
12712 | WARMINSTER | ASPECT HOUSE | N | S105A Sewage Pumping Station | INUSE
12713 | EAST COKER | NAISH BARTON | W | S105A Sewage Pumping Station | INUSE
12716 | WEYMOUTH | HIGHLAND ROAD | S | Private Sewage Pumping Station | INUSE
12717 | BOURNEMOUTH | PORTMAN CRESCENT | S | Private Sewage Pumping Station | INUSE
12719 | MARK | POPLAR LANE | W | Sewage Pumping Station | INUSE
12722 | BRIDGWATER | DURLEIGH ROAD (PUMPED NRV) | W | Single Property Pumping Station | INUSE
12724 | YEOVIL | LUFTON | W | Sewage Pumping Station | INUSE
12726 | BEAMINSTER | HAMS MILL | S | Private Sewage Pumping Station | INUSE
12727 | MERRIOTT | TAIL MILL LANE | W | Private Sewage Pumping Station | INUSE
12729 | BOURNEMOUTH | MEADOW COURT CLOSE | S | Private Sewage Pumping Station | INUSE
12733 | PORTISHEAD | CHARLTON VIEW | W | S105A Sewage Pumping Station | INUSE
12737 | BOURNEMOUTH | SOUTHBOURNE OVERCLIFF DRIVE 1 | S | Private Sewage Pumping Station | INUSE
12740 | WARMINSTER | MILL ISLAND | N | Private Sewage Pumping Station | INUSE
12742 | WESTBURY | THE HAM | N | Private Sewage Pumping Station | INUSE
12743 | SEVERN BEACH | CENTRAL AVENUE | N | Private Sewage Pumping Station | INUSE
12744 | BRISTOL | 10 CHURCH ROAD | N | Private Sewage Pumping Station | INUSE
12746 | BATH | NORTH ROAD | N | Private Sewage Pumping Station | INUSE
12748 | COMBE ST NICHOLAS | COMBE WOOD | W | Private Sewage Pumping Station | INUSE
12749 | BRIDGWATER | BRIDGEWATER WAREHOUSING CO LTD (SURFACE)2 | W | Private Sewage Pumping Station | INUSE
12750 | BLANDFORD FORUM | PEARMAIN HOUSE | S | Private Sewage Pumping Station | INUSE
12751 | IWERNE MINSTER | BLENHEIM HOUSE | S | Private Sewage Pumping Station | INUSE
12752 | IWERNE MINSTER | RUSSET HOUSE | S | Private Sewage Pumping Station | INUSE
12753 | IWERNE MINSTER | JAZZ HOUSE | S | Private Sewage Pumping Station | INUSE
12754 | FERNDOWN | ANGEL LANE 1 | S | Private Sewage Pumping Station | INUSE
12755 | FERNDOWN | ANGEL LANE 2 | S | Private Sewage Pumping Station | INUSE
12756 | FERNDOWN | ANGEL LANE 3 | S | Private Sewage Pumping Station | INUSE
12757 | BOURNEMOUTH | GILLETT ROAD | S | Private Sewage Pumping Station | INUSE
12758 | OWERMOIGNE | MORETON ROAD | S | Private Sewage Pumping Station | INUSE
12764 | SALISBURY | LONG HEDGE FARM | S | Sewage Pumping Station | INUSE
12771 | POOLE | ALLENS ROAD | S | Private Sewage Pumping Station | INUSE
12772 | TROWBRIDGE | WICKER HILL O/S MANE EVENT HAIRDRESSERS | N | Combined Sewer Overflow | INUSE
12773 | TROWBRIDGE | ROSECROFT POLEBARN ROAD | N | Combined Sewer Overflow | INUSE
12781 | CALNE | STOCKLEY LANE | N | S105A Sewage Pumping Station | INUSE
12782 | LACOCK | WHITEHALL GARDEN CENTRE | N | Private Sewage Pumping Station | INUSE
12787 | NEWTON ST. LOE | GLOBE INN | N | Private Sewage Pumping Station | INUSE
12789 | LEIGH DELAMERE | SERVICES EASTBOUND | N | Private Sewage Pumping Station | INUSE
12790 | LEIGH DELAMERE | SERVICES WESTBOUND | N | Private Sewage Pumping Station | INUSE
12847 | BRISTOL | NAPIER ROAD | N | Private Sewage Pumping Station | INUSE
12848 | POOLE | DORNIE ROAD 1 | S | Private Sewage Pumping Station | INUSE
12849 | POOLE | DORNIE ROAD 2 | S | Private Sewage Pumping Station | INUSE
12854 | POOLE | CHADDESLEY GLEN 1 | S | Private Sewage Pumping Station | INUSE
12855 | DONIFORD | DONIFORD BAY HOLIDAY PARK | W | Private Sewage Pumping Station | INUSE
12856 | CHRISTCHURCH | AVON RUN CLOSE | S | Private Sewage Pumping Station | INUSE
12857 | FORDINGBRIDGE | FLAXFIELDS END | S | Private Sewage Pumping Station | INUSE
12860 | ALMONDSBURY | GLOUCESTER ROAD 1 | N | Private Sewage Pumping Station | INUSE
12861 | ALMONDSBURY | GLOUCESTER ROAD 2 | N | Private Sewage Pumping Station | INUSE
12862 | ALMONDSBURY | GLOUCESTER ROAD 3 | N | Private Sewage Pumping Station | INUSE
12863 | POOLE | CANFORD CLIFFS AVENUE | S | Private Sewage Pumping Station | INUSE
12865 | BRIDGWATER | OLD TAUNTON ROAD | W | Sewage Pumping Station | INUSE
12869 | CONGRESBURY | SERVICE STATION 1 | W | S105A Sewage Pumping Station | INUSE
12883 | CALNE | BEVERSBROOK ROAD 1 | N | Private Sewage Pumping Station | INUSE
12890 | WINSCOMBE | ILEX LANE | W | Private Sewage Pumping Station | INUSE
12891 | HULLAVINGTON | HULLAVINGTON AIRFIELD 1 | N | Private Sewage Pumping Station | INUSE
12892 | PEWSEY | STATION MEWS SURFACE | N | Private Sewage Pumping Station | INUSE
12893 | CHARLTON ADAM | HIGH STREET | W | Private Sewage Pumping Station | INUSE
12895 | POOLE | STERTE ROAD UNIT 9 | S | Private Sewage Pumping Station | INUSE
12896 | POOLE | STERTE ROAD UNIT 8 | S | Private Sewage Pumping Station | INUSE
12906 | BRISTOL | CABOT MEWS | N | Private Sewage Pumping Station | INUSE
12909 | BATH | LOWER BRISTOL ROAD SURFACE | N | Private Sewage Pumping Station | INUSE
12911 | CHILCOMPTON | WELLS ROAD | W | Private Sewage Pumping Station | INUSE
12918 | TEMPLECOMBE | THROOP ROAD | W | Private Sewage Pumping Station | INUSE
12922 | BOURNEMOUTH | WATER LANE FARM | S | S105A Sewage Pumping Station | INUSE
12923 | CHRISTCHURCH | HURN ROAD | S | S105A Sewage Pumping Station | INUSE
12933 | BRIDPORT | ALEXANDRA ROAD | S | Private Sewage Pumping Station | INUSE
12936 | BURNHAM-ON-SEA | THE ORCHIDS | W | S105A Sewage Pumping Station | INUSE
12938 | BRISTOL | O/S 168 STATION ROAD | N | Combined Sewer Overflow | INUSE
12974 | ROYAL WOOTTON BASSETT | HIGH STREET | N | Private Sewage Pumping Station | INUSE
13014 | AXBRIDGE | OLD STW SITE | W | Sewage Pumping Station | INUSE
13033 | BRADFORD PEVERELL | GILES CROSS | S | Sewage Pumping Station | INUSE
13074 | COMBWICH | QUAY ROAD | W | Sewage Pumping Station | INUSE
13089 | CREWKERNE | OPPOSITE 2 REDGATE PARK | W | Combined Sewer Overflow | INUSE
13093 | DONIFORD | . | W | Sewage Pumping Station | INUSE
13126 | FONTMELL MAGNA | COLLYERS RISE (FONTMELL MAGNA 1) | S | Sewage Pumping Station | INUSE
13138 | GRITTLETON | WOODMANS LODGE | N | Sewage Pumping Station | INUSE
13153 | HOLTON HEATH | HOLTON HEATH SEWAGE PUMPING STATION | S | Sewage Pumping Station | INUSE
13189 | LYMPSHAM | WORTHY CRESCENT | W | Sewage Pumping Station | INUSE
13197 | MARK | . | W | Sewage Pumping Station | INUSE
13216 | MONKTON DEVERILL | HIGH STREET | N | Sewage Pumping Station | INUSE
13240 | TAUNTON | PRIORY STORM | W | Combined Sewer Overflow | INUSE
13261 | SANDYLANDS | . | W | Sewage Pumping Station | INUSE
13265 | SHAPWICK | SOMERSET | W | Sewage Pumping Station | INUSE
13273 | SHIPTON GORGE | OFF MARKETS LANE | S | Sewage Pumping Station | INUSE
13283 | SPAXTON | . | W | Sewage Pumping Station | INUSE
13284 | ST GEORGES | NO 1 | W | Sewage Pumping Station | INUSE
13326 | WARMWELL | CROSSWAYS OF B3390 | S | Sewage Pumping Station | INUSE
13334 | BRIDPORT | WEST BAY | S | Sewage Pumping Station | INUSE
13337 | WEST LULWORTH | HAMBURY FARM | S | Sewage Pumping Station | INUSE
13340 | WESTON-SUPER-MARE | BLACK ROCK WINDWHISTLE ROAD | W | Sewage Pumping Station | INUSE
13373 | PORLOCK | PORLOCK WEIR | W | Sewage Pumping Station | INUSE
13375 | LYNEHAM | PRESTON LANE | N | Sewage Pumping Station | INUSE
13389 | BOSSINGTON | . | W | Sewage Pumping Station | INUSE
13425 | BRIDPORT | SEA ROAD NORTH | S | Private Sewage Pumping Station | INUSE
13461 | ALMONDSBURY | 17 OLD AUST ROAD | N | Private Sewage Pumping Station | INUSE
13462 | SOUTH PETHERTON | LOPENHEAD BUSINESS PARK | W | Private Sewage Pumping Station | INUSE
13467 | GILLINGHAM | BARNABY MEAD 1 | S | Private Sewage Pumping Station | INUSE
13468 | WEYMOUTH | PRINCESS GARDENS SURFACE | S | Private Sewage Pumping Station | INUSE
13523 | LYNEHAM | D SITE (OLD SMALL STW) | N | Sewage Pumping Station | INUSE
13561 | FROME | FROME GARAGES | W | Private Sewage Pumping Station | INUSE
13563 | BRISTOL | WAPPING WHARF | N | Private Sewage Pumping Station | INUSE
13565 | WOOL | WATER MEADOW LANE | S | Private Sewage Pumping Station | INUSE
13570 | CHRISTCHURCH | RIVER GLADE | S | S105A Sewage Pumping Station | INUSE
13571 | WESTON-SUPER-MARE | OVERCOMBE HOUSE | W | Private Sewage Pumping Station | INUSE
13572 | CONGRESBURY | SOUTHLANDS WAY | W | S105A Sewage Pumping Station | INUSE
13575 | BRADFORD-ON-AVON | WESTBURY HOUSE | N | Private Sewage Pumping Station | INUSE
13576 | STAVERTON | ST PAULS CHURCH | N | Private Sewage Pumping Station | INUSE
13582 | WEYMOUTH | MONMOUTH AVENUE | S | Private Sewage Pumping Station | INUSE
13584 | URCHFONT | PEPPERCOMBE LANE | N | Private Sewage Pumping Station | INUSE
13590 | WATERROW | THE MANOR MILL | W | Private Sewage Pumping Station | INUSE
13602 | WEDMORE | WEDMORE FIRST SCHOOL | W | Private Sewage Pumping Station | INUSE
13603 | BATHAMPTON | STATION ROAD | N | Private Sewage Pumping Station | INUSE
13604 | DORCHESTER | ST GEORGES ROAD | S | Private Sewage Pumping Station | INUSE
13605 | WESTBURY | 75 WARMINSTER ROAD (PUMPED NRV) | N | Single Property Pumping Station | INUSE
13607 | BOURNEMOUTH | MILLHAMS RECYCLING CENTRE | S | Private Sewage Pumping Station | INUSE
13608 | BURTON BRADSTOCK | MILL COTTAGE | S | Private Sewage Pumping Station | INUSE
13609 | SOUTH PETHERTON | LOGGE FARM | W | Private Sewage Pumping Station | INUSE
13610 | POOLE | PEARCE AVENUE (SURFACE) | S | Private Sewage Pumping Station | INUSE
13614 | BOURNEMOUTH INTERNATIONAL AIRPORT | INTERNATIONAL AIRPORT ENTERPRISE WAY | S | Private Sewage Pumping Station | INUSE
13615 | POOLE | THE DRIVE | S | Private Sewage Pumping Station | INUSE
13616 | POOLE | WOODSIDE | S | Private Sewage Pumping Station | INUSE
13617 | POOLE | THE DRIVE | S | Private Sewage Pumping Station | INUSE
13620 | MEARE | ST MARYS ROAD | W | Private Sewage Pumping Station | INUSE
13624 | CHRISTCHURCH | CLIFF DRIVE (FOUL AND SURFACE) | S | Private Sewage Pumping Station | INUSE
13633 | COLERNE | BATH ROAD | N | Private Sewage Pumping Station | INUSE
13634 | WARMINSTER | 63 BARLEY CLOSE | N | Private Sewage Pumping Station | INUSE
13635 | WARMINSTER | 65 BARLEY CLOSE | N | Private Sewage Pumping Station | INUSE
13636 | WESTON-SUPER-MARE | GROVE ROAD | W | S105A Sewage Pumping Station | INUSE
13637 | BOURNEMOUTH | KIRBY WAY | S | S105A Sewage Pumping Station | INUSE
13638 | COSSINGTON | COSSINGTON LANE | W | Private Sewage Pumping Station | INUSE
13639 | DURLEIGH | ENMORE ROAD 1 | W | Sewage Pumping Station | INUSE
13640 | WELLS | SINGLETON COURT | W | S105A Sewage Pumping Station | INUSE
13641 | WIMBORNE | PILFORD HEATH ROAD 1 | S | S105A Sewage Pumping Station | INUSE
13642 | WINCANTON | SOUTHGATE ROAD | W | Private Sewage Pumping Station | INUSE
13644 | BRISTOL | KELLAWAY AVENUE | N | Private Sewage Pumping Station | INUSE
13651 | EASTON | MANOR FARM HOUSE | W | Private Sewage Pumping Station | INUSE
13653 | OAKE | TE ANAU PROPERTY | W | Private Sewage Pumping Station | INUSE
13654 | NORTH BRADLEY | WESTBURY ROAD | N | Private Sewage Pumping Station | INUSE
13655 | BATH | EDEN PARK DRIVE 1 | N | Private Sewage Pumping Station | INUSE
13656 | BATH | EDEN PARK DRIVE 2 | N | Private Sewage Pumping Station | INUSE
13660 | POOLE | HERBERT AVENUE | S | Private Sewage Pumping Station | INUSE
13662 | POOLE | OLD WAREHAM ROAD 1 | S | Private Sewage Pumping Station | INUSE
13663 | POOLE | OLD WAREHAM ROAD 2 | S | Private Sewage Pumping Station | INUSE
13666 | WESTHAY | SHAPWICK ROAD | W | Private Sewage Pumping Station | INUSE
13668 | DORCHESTER | POUNDBURY ROAD | S | Sewage Pumping Station | INUSE
13669 | HENSTRIDGE | SHAFTESBURY ROAD | W | Private Sewage Pumping Station | INUSE
13670 | BATH | TEDDINGTON CLOSE | N | Private Sewage Pumping Station | INUSE
13672 | IWERNE MINSTER | BLANDFORD ROAD | S | Private Sewage Pumping Station | INUSE
13673 | SALISBURY | MILFORD MILL ROAD | S | Private Sewage Pumping Station | INUSE
13679 | LARKHILL | MOD SITE SPS | N | Private Sewage Pumping Station | INUSE
13683 | WEYMOUTH | THE QUAY STATION | S | Private Sewage Pumping Station | INUSE
13684 | WEYMOUTH | WEYMOUTH TOWER | S | Private Sewage Pumping Station | INUSE
13685 | BRISTOL | LEICESTER SQUARE | N | Private Sewage Pumping Station | INUSE
13686 | BLEADON | PURN HOLIDAY PARK | W | Private Sewage Pumping Station | INUSE
13687 | WARMINSTER | COPHEAP LANE | N | Private Sewage Pumping Station | INUSE
13689 | BRISTOL AIRPORT | FOUL PUMPED HOLDING TANK | W | Private Sewage Pumping Station | INUSE
13690 | BRISTOL AIRPORT | SOUTH SIDE | W | Private Sewage Pumping Station | INUSE
13691 | BRISTOL AIRPORT | FIRE STATION | W | Private Sewage Pumping Station | INUSE
13695 | BRIDGWATER | BATH ROAD 1 SURFACE | W | Private Sewage Pumping Station | INUSE
13696 | BLEADON | 4 CORONATION ROAD | W | Private Sewage Pumping Station | INUSE
13705 | CERNE ABBAS | ACREMAN STREET (SURFACE) | S | Private Sewage Pumping Station | INUSE
13707 | BRISTOL | WHITCHURCH MEWS | N | Private Sewage Pumping Station | INUSE
13709 | WEYMOUTH | LAKESIDE WALK | S | Private Sewage Pumping Station | INUSE
13710 | WEYMOUTH | RADIPOLE PARK DRIVE | S | Private Sewage Pumping Station | INUSE
13711 | SHERBORNE | NETHERCOOMBE LANE | S | Private Sewage Pumping Station | INUSE
13719 | CHARMINSTER | NORTH STREET | S | Private Sewage Pumping Station | INUSE
13722 | CORSHAM | THE CLEEVE 1 | N | Sewage Pumping Station | Emergency
13723 | SWANAGE | THE SWANAGE SCHOOL | S | Private Sewage Pumping Station | INUSE
13725 | CLEVEDON | WILD ORCHARD | W | Private Sewage Pumping Station | INUSE
13726 | BOURNEMOUTH | CHARMINSTER ROAD NEAR 286-290 | S | Combined Sewer Overflow | INUSE
13746 | BRIDGWATER | PATRICIA MEWS SURFACE | W | Private Sewage Pumping Station | INUSE
13747 | BRISTOL | SEA WALLS ROAD 1 | N | Private Sewage Pumping Station | INUSE
13748 | BRISTOL | SEA WALLS ROAD 2 | N | Private Sewage Pumping Station | INUSE
13750 | BRISTOL | FARRIERS COURT | N | Private Sewage Pumping Station | INUSE
13752 | BRISTOL | COURT ROAD | N | Private Sewage Pumping Station | INUSE
13753 | BRISTOL | EASTFIELD ROAD | N | Private Sewage Pumping Station | INUSE
13764 | CHARD | FIELD BARS HOUSE | W | Private Sewage Pumping Station | INUSE
13770 | CREECH ST. MICHAEL | HUSK FARM | W | Private Sewage Pumping Station | INUSE
13771 | CONGRESBURY | ST ANDREWS SCHOOL | N | Private Sewage Pumping Station | INUSE
13773 | MARTOCK | HURST 1 | W | Private Sewage Pumping Station | INUSE
13774 | FORDINGBRIDGE | STATION ROAD 1 | S | Private Sewage Pumping Station | INUSE
13776 | WINFORD | OLD COACH STATION SURFACE | W | Private Sewage Pumping Station | INUSE
13777 | POOLE | DORSET LAKE AVENUE | S | Private Sewage Pumping Station | INUSE
13783 | WINCANTON | SOUTHGATE ROAD 1 | W | S105A Sewage Pumping Station | INUSE
13797 | WEYMOUTH | PRESTON FISHERBRIDGE ROAD SURFACE | S | Private Sewage Pumping Station | INUSE
13800 | MELKSHAM | 137 QUEENSWAY | N | Private Sewage Pumping Station | INUSE
13801 | RADSTOCK | MILL ROAD | N | Private Sewage Pumping Station | INUSE
13802 | SHEPTON MALLET | DOMUS DRIVE | W | S105A Sewage Pumping Station | INUSE
13804 | ABBOTS LEIGH | THE EVERGREENS | N | Private Sewage Pumping Station | INUSE
13806 | ROWDE | NURSING HOME | N | Private Sewage Pumping Station | INUSE
13807 | LOCKING | BANWELL ROAD | W | Private Sewage Pumping Station | INUSE
13808 | KENN | STONEHOUSE FARM | W | S105A Sewage Pumping Station | INUSE
13814 | HUNTWORTH | THE FORGE BARN | W | Private Sewage Pumping Station | INUSE
13815 | BOX | BOX HOUSE BATH ROAD | N | Private Sewage Pumping Station | INUSE
13816 | BRENT KNOLL | BRENT STREET 1 | W | Private Sewage Pumping Station | INUSE
13817 | CHIPPENHAM | 22 LONG CLOSE | N | Combined Sewer Overflow | INUSE
13818 | BEAMINSTER | KNAPP HOUSE | S | Private Sewage Pumping Station | INUSE
13820 | WILLESLEY | BEAUFORT HOUSE | N | Private Sewage Pumping Station | INUSE
13821 | POOLE | MARTELLO ROAD SOUTH | S | Private Sewage Pumping Station | INUSE
13825 | STOKE-SUB-HAMDON | MATTS LANE | W | Private Sewage Pumping Station | INUSE
13826 | EAST LAMBROOK | WATER STREET | W | Private Sewage Pumping Station | INUSE
13828 | CONGRESBURY | CADBURY GARDEN LEISURE | W | Private Sewage Pumping Station | INUSE
14000 | TAUNTON | RIVERSIDE | W | Sewage Pumping Station | INUSE
14001 | BATH | SOUTHSTOKE ROAD | N | Sewage Pumping Station | INUSE
14002 | BATH | MIDLAND ROAD TWERTON | N | Sewage Pumping Station | INUSE
14003 | BATH | NEWBRIDGE CARAVAN SITE | N | Sewage Pumping Station | INUSE
14004 | BATH | VAN DIEMENS LANE | N | Sewage Pumping Station | INUSE
14005 | BATH | ENGLISHCOMBE RISE (PREVIOUSLY WHITEWAY AVENUE) | N | Sewage Pumping Station | INUSE
14006 | BATH | BUCKLANDS LODGE | N | Sewage Pumping Station | INUSE
14007 | BATH | DARLINGTON ROAD | N | Sewage Pumping Station | INUSE
14008 | BATH | STONEHOUSE CLOSE | N | Sewage Pumping Station | INUSE
14009 | NORTON FITZWARREN | WASSAIL VIEW (MANOR FARM) | W | Sewage Pumping Station | INUSE
14013 | CLIFTON | LOW LEVEL | N | Sewage Pumping Station | INUSE
14014 | BRISTOL | KINGS WALK | N | Sewage Pumping Station | INUSE
14015 | BRISTOL | BEDMINSTER DOWN | N | Sewage Pumping Station | INUSE
14016 | BRISTOL | ASHTON AVENUE | N | Sewage Pumping Station | INUSE
14017 | BRISTOL | BLACK ROCKS PORTWAY | N | Combined Sewer Overflow | INUSE
14019 | BRISTOL | ROSERY CLOSE | N | Sewage Pumping Station | INUSE
14020 | LOWER STANTON DREW | . | N | Sewage Pumping Station | INUSE
14021 | BRISTOL | BROADMEAD | N | Sewage Pumping Station | INUSE
14022 | BRISTOL | HEDGEMEAD VIEW | N | Sewage Pumping Station | INUSE
14023 | BRISTOL | IRONMOULD LANE | N | Sewage Pumping Station | INUSE
14024 | BRISTOL | ATWOOD DRIVE | N | Sewage Pumping Station | INUSE
14025 | FILTON | CHARLTON GARDENS | N | Sewage Pumping Station | INUSE
14028 | BRISTOL | BROOMHILL ROAD | N | Sewage Pumping Station | INUSE
14033 | CHRISTCHURCH | PUREWELL | S | Sewage Pumping Station | INUSE
14034 | HURN | MOORS CLOSE | S | Sewage Pumping Station | INUSE
14035 | CHRISTCHURCH | SOMERFORD BRIDGE | S | Sewage Pumping Station | INUSE
14036 | CHRISTCHURCH | SCOTTS HILL LANE | S | Sewage Pumping Station | INUSE
14039 | SHIPTON MOYNE | . | N | Sewage Pumping Station | INUSE
14040 | LEIGHTERTON | . | N | Sewage Pumping Station | INUSE
14041 | SIXPENNY HANDLEY | . | S | Sewage Pumping Station | INUSE
14042 | CRANBORNE | ALDERHOLT RD HIGHER HOLWELL | S | Sewage Pumping Station | INUSE
14044 | STANTON ST BERNARD | CHURCH FARM | N | Sewage Pumping Station | INUSE
14045 | EVERLEIGH | EVERLEIGH MANOR | N | Sewage Pumping Station | INUSE
14046 | PEWSEY | SWAN | N | Sewage Pumping Station | INUSE
14047 | COATE | SPANIELS BRIDGE | N | Sewage Pumping Station | INUSE
14048 | BEECHINGSTOKE | . | N | Sewage Pumping Station | INUSE
14049 | PEWSEY | WILCOT LODGE | N | Sewage Pumping Station | INUSE
14050 | COLLINGBOURNE DUCIS | . | N | Sewage Pumping Station | INUSE
14051 | UPAVON | ANDOVER ROAD | N | Sewage Pumping Station | INUSE
14052 | STANTON ST BERNARD | CANAL COTTAGES | N | Sewage Pumping Station | INUSE
14053 | ERLESTOKE | ERLESTOKE PARK | N | Sewage Pumping Station | INUSE
14054 | PEWSEY | JUBILEE | N | Sewage Pumping Station | INUSE
14055 | MARDEN | HIGH STREET | N | Sewage Pumping Station | INUSE
14056 | WEST LAVINGTON | DUCK STREET | N | Sewage Pumping Station | INUSE
14057 | GREAT CHEVERELL | CHEVERELL GREEN | N | Sewage Pumping Station | INUSE
14058 | HORTON | HORTON FARM | N | Sewage Pumping Station | INUSE
14059 | ROWDE | TOWER VIEW | N | Sewage Pumping Station | INUSE
14061 | BRISTOL | MARSHFIELD PARK | N | Sewage Pumping Station | INUSE
14062 | BRISTOL | CROWN GARDENS | N | Sewage Pumping Station | INUSE
14063 | KINGSWOOD | SWINEFORD | N | Sewage Pumping Station | INUSE
14064 | KINGSWOOD | WILLSBRIDGE | N | Sewage Pumping Station | INUSE
14065 | KINGSWOOD | PARKWALL ROAD | N | Sewage Pumping Station | INUSE
14066 | HANHAM | SALLY ON THE BARN | N | Sewage Pumping Station | INUSE
14067 | BITTON | . | N | Sewage Pumping Station | INUSE
14068 | GLASTONBURY | BUSHYCOMBE | W | Sewage Pumping Station | INUSE
14069 | STREET | HOUNDWOOD DROVE | W | Sewage Pumping Station | INUSE
14070 | GODNEY | . | W | Sewage Pumping Station | INUSE
14071 | MEARE | OXENPILL | W | Sewage Pumping Station | INUSE
14072 | BLEADNEY | BLEADNEY MILL | W | Sewage Pumping Station | INUSE
14073 | STREET | THE MEAD | W | Sewage Pumping Station | INUSE
14074 | SHEPTON MALLET | FOSSE LANE CHARLTON | W | Sewage Pumping Station | INUSE
14075 | GLASTONBURY | NORTH LOAD BRIDGE | W | Sewage Pumping Station | INUSE
14076 | EVERCREECH | STONEY STRATTON | W | Sewage Pumping Station | INUSE
14077 | STREET | STRODE ROAD | W | Sewage Pumping Station | INUSE
14078 | WELLS | HAYBRIDGE | W | Sewage Pumping Station | INUSE
14079 | MEARE | TURNBRIDGE | W | Sewage Pumping Station | INUSE
14080 | HENTON | FORD LANE | W | Sewage Pumping Station | INUSE
14082 | STREET | MAIN | W | Sewage Pumping Station | INUSE
14083 | WEST PENNARD | HAVYATT | W | Sewage Pumping Station | INUSE
14084 | GLASTONBURY | ACTIS | W | Sewage Pumping Station | INUSE
14085 | COXLEY | COXLEY RIPPLE | W | Sewage Pumping Station | INUSE
14086 | MEARE | HOMEWAY CORNER | W | Sewage Pumping Station | INUSE
14087 | WEST LYDFORD | . | W | Sewage Pumping Station | INUSE
14088 | BALTONSBOROUGH | CHURCH LANE | W | Sewage Pumping Station | INUSE
14089 | WESTHAY | . | W | Sewage Pumping Station | INUSE
14090 | BUTLEIGH WOOTTON | . | W | Sewage Pumping Station | INUSE
14092 | GLASTONBURY | WELLS ROAD | W | Sewage Pumping Station | INUSE
14093 | WEST PENNARD | PAGE LANE | W | Sewage Pumping Station | INUSE
14094 | GLASTONBURY | THORNDUN | W | Sewage Pumping Station | INUSE
14095 | GLASTONBURY | PORCHESTALL | W | Sewage Pumping Station | INUSE
14096 | COXLEY | MILL LANE | W | Sewage Pumping Station | INUSE
14097 | BALTONSBOROUGH | BALTONSBOROUGH MAIN | W | Sewage Pumping Station | INUSE
14098 | EAST LYDFORD | . | W | Sewage Pumping Station | INUSE
14099 | STREET | WALTON GLOBE | W | Sewage Pumping Station | INUSE
14100 | GLASTONBURY | TOR VIEW | W | Sewage Pumping Station | INUSE
14101 | WESTBURY SUB MENDIP | EASTON | W | Sewage Pumping Station | INUSE
14102 | KILMERSDON | . | W | Sewage Pumping Station | INUSE
14103 | COLEFORD | UPPER MERRYFIELD | W | Sewage Pumping Station | INUSE
14104 | FROME | SPRING GARDENS | W | Sewage Pumping Station | INUSE
14105 | CHILCOMPTON | BENNEL | W | Sewage Pumping Station | INUSE
14106 | NORTON ST PHILIP | TELLISFORD LANE | W | Sewage Pumping Station | INUSE
14107 | WITHAM FRIARY | . | W | Sewage Pumping Station | INUSE
14108 | MELLS | . | W | Sewage Pumping Station | INUSE
14109 | OAKHILL | FOSSE ROAD | W | Sewage Pumping Station | INUSE
14110 | STOKE ST MICHAEL | STOKE HILL | W | Sewage Pumping Station | INUSE
14111 | OAKHILL | ASHWICK GROVE | W | Sewage Pumping Station | INUSE
14112 | WANSTROW | . | W | Sewage Pumping Station | INUSE
14113 | TRUDOXHILL | . | W | Sewage Pumping Station | INUSE
14114 | GLASTONBURY | EDGARLEY MILLFIELD SCHOOL | W | Sewage Pumping Station | INUSE
14115 | FROME | LEONARDS MILL | W | Sewage Pumping Station | INUSE
14116 | GURNEY SLADE | . | W | Sewage Pumping Station | INUSE
14117 | STREET | PETVINE CLOSE PORTWAY ALSO S0118 | W | Sewage Pumping Station | INUSE
14119 | WELLS | KEWARD AVENUE (BISHOPS LEA CLOSE) | W | Sewage Pumping Station | INUSE
14120 | STREET | MIDDLE BROOKS ROAD | W | Sewage Pumping Station | INUSE
14121 | STUBHAMPTON | MAIN STREET | S | Sewage Pumping Station | INUSE
14122 | SPETISBURY | NO 3 | S | Sewage Pumping Station | INUSE
14123 | CHARMOUTH | CATHERSTONE | S | Sewage Pumping Station | INUSE
14124 | STOURPAINE | . | S | Sewage Pumping Station | INUSE
14125 | GILLINGHAM | BUCKINGHAM ROAD | S | Sewage Pumping Station | INUSE
14126 | SHROTON | . | S | Sewage Pumping Station | INUSE
14127 | GILLINGHAM | BRICKYARD LANE | S | Sewage Pumping Station | INUSE
14128 | BURLEY | ESDAILE LANE | S | Sewage Pumping Station | INUSE
14129 | RINGWOOD | NAGS HEAD | S | Sewage Pumping Station | INUSE
14130 | RINGWOOD | HIGHTOWN CROW LANE | S | Sewage Pumping Station | INUSE
14131 | RINGWOOD | MOORTOWN | S | Sewage Pumping Station | INUSE
14132 | BRANSGORE | WILTSHIRE GARDENS | S | Sewage Pumping Station | INUSE
14133 | RINGWOOD | BICKERLEY | S | Sewage Pumping Station | INUSE
14134 | WHITSBURY | LOWER GROVE | S | Sewage Pumping Station | INUSE
14135 | HULLAVINGTON | PARKLANDS | N | Sewage Pumping Station | INUSE
14136 | LEA | CRESSWELL LANE | N | Sewage Pumping Station | INUSE
14137 | GREAT SOMERFORD | HOLLOW STREET | N | Sewage Pumping Station | INUSE
14138 | COLERNE | THICKWOOD | N | Sewage Pumping Station | INUSE
14139 | CHRISTIAN MALFORD | SWALLETTS GATE | N | Sewage Pumping Station | INUSE
14140 | HULLAVINGTON | BRADFIELD | N | Sewage Pumping Station | INUSE
14141 | HILMARTON | SNOW HILL | N | Sewage Pumping Station | INUSE
14142 | MINETY | STATION ROAD | N | Sewage Pumping Station | INUSE
14143 | GREAT SOMERFORD | WEST STREET | N | Sewage Pumping Station | INUSE
14144 | MALMESBURY | PERRY GREEN | N | Sewage Pumping Station | INUSE
14145 | MALMESBURY | TANNERS BRIDGE | N | Sewage Pumping Station | INUSE
14146 | LYNEHAM | POUND CLOSE | N | Sewage Pumping Station | INUSE
14147 | CHIPPENHAM | WESTMEAD | N | Sewage Pumping Station | INUSE
14148 | MALMESBURY | HOLLOWAY HILL | N | Sewage Pumping Station | INUSE
14149 | CHIPPENHAM | FIELD VIEW | N | Sewage Pumping Station | INUSE
14150 | GREAT SOMERFORD | DAUNTSEY ROAD | N | Sewage Pumping Station | INUSE
14151 | DAUNTSEY | THE GREEN | N | Sewage Pumping Station | INUSE
14152 | BROADS GREEN | . | N | Sewage Pumping Station | INUSE
14153 | BROADTOWN | COTMARSH FARM | N | Sewage Pumping Station | INUSE
14154 | SHERSTON | GASTON LANE | N | Sewage Pumping Station | INUSE
14155 | GASTARD | COPPERSHELL | N | Sewage Pumping Station | INUSE
14156 | YATTON KEYNELL | TIDDLY WINK | N | Sewage Pumping Station | INUSE
14157 | CALNE | ROUGH LEAZE | N | Sewage Pumping Station | INUSE
14158 | HULLAVINGTON | RAF STATION | N | Sewage Pumping Station | INUSE
14159 | DAUNTSEY | ST JAMES | N | Sewage Pumping Station | INUSE
14160 | SHERSTON | THE TARTERS | N | Sewage Pumping Station | INUSE
14161 | COMPTON BASSETT | THE POND | N | Sewage Pumping Station | INUSE
14162 | MALMESBURY | BURTON HILL | N | Sewage Pumping Station | INUSE
14163 | EAST TYTHERTON | BARNS BRIDGE | N | Sewage Pumping Station | INUSE
14164 | FOXHAM | WEST END | N | Sewage Pumping Station | INUSE
14166 | MINETY | LOWER MOOR | N | Sewage Pumping Station | INUSE
14167 | LACOCK | CORSHAM ROAD | N | Sewage Pumping Station | INUSE
14168 | LOWER SEAGRY | . | N | Sewage Pumping Station | INUSE
14169 | GRITTLETON | FOSCOTE | N | Sewage Pumping Station | INUSE
14170 | BRINKWORTH | CALLOW HILL | N | Sewage Pumping Station | INUSE
14171 | CHIPPENHAM | HARDENHUISH | N | Sewage Pumping Station | INUSE
14173 | CASTLE COMBE | . | N | Sewage Pumping Station | INUSE
14174 | BOX | MILL LANE | N | Sewage Pumping Station | INUSE
14175 | EASTCOURT | OATRIDGE FARM | N | Sewage Pumping Station | INUSE
14176 | KINGTON LANGLEY | . | N | Sewage Pumping Station | INUSE
14177 | CALSTONE WELLINGTON | . | N | Sewage Pumping Station | INUSE
14178 | GREAT SOMERFORD | FROG LANE | N | Sewage Pumping Station | INUSE
14179 | BIDDESTONE | MANOR COTTAGES | N | Sewage Pumping Station | INUSE
14181 | ROYAL WOOTTON BASSETT | HOOK DIANMER CLOSE | N | Sewage Pumping Station | INUSE
14182 | HEDDINGTON | BEACON HILL | N | Sewage Pumping Station | INUSE
14183 | BOX | MIDDLE HILL | N | Sewage Pumping Station | INUSE
14184 | ROYAL WOOTTON BASSETT | GREEN PARK | N | Sewage Pumping Station | INUSE
14185 | MALMESBURY | ST JOHNS STREET | N | Sewage Pumping Station | INUSE
14186 | ROYAL WOOTTON BASSETT | GOLDBOROUGH | N | Sewage Pumping Station | INUSE
14187 | LITTLE SOMERFORD | MANOR FARM | N | Sewage Pumping Station | INUSE
14188 | LOWER STANTON ST QUINTIN | . | N | Sewage Pumping Station | INUSE
14189 | YATESBURY | NOLANDS FARM | N | Sewage Pumping Station | INUSE
14190 | EAST TYTHERTON | CLOVELLY COTTAGE | N | Sewage Pumping Station | INUSE
14192 | UPPER SEAGRY | UPPER SEAGRY | N | Sewage Pumping Station | INUSE
14193 | SHERSTON | SANDPITS LANE | N | Sewage Pumping Station | INUSE
14194 | COMPTON BASSETT | BREACH FARM | N | Sewage Pumping Station | INUSE
14195 | STARTLEY | . | N | Sewage Pumping Station | INUSE
14196 | MALMESBURY | NOAHS ARK | N | Sewage Pumping Station | INUSE
14197 | MALMESBURY | CORSTON | N | Sewage Pumping Station | INUSE
14198 | CALNE | COLEMANS FARM | N | Sewage Pumping Station | INUSE
14199 | UPPER MINETY | FLISTERIDGE | N | Sewage Pumping Station | INUSE
14200 | LEA | LEA NORTH | N | Sewage Pumping Station | INUSE
14201 | MALMESBURY | STATION YARD | N | Sewage Pumping Station | INUSE
14202 | HANKERTON | HANKERTON BRIDGE | N | Sewage Pumping Station | INUSE
14203 | BROADTOWN | THORNHILL | N | Sewage Pumping Station | INUSE
14204 | CALNE | STUDLEY | N | Sewage Pumping Station | INUSE
14205 | MALMESBURY | FLYING MONK | N | Sewage Pumping Station | INUSE
14206 | HANKERTON | HANKERTON EAST | N | Sewage Pumping Station | INUSE
14207 | CHELWORTH | OAKSEY | N | Sewage Pumping Station | INUSE
14209 | CALNE | CASTLE STREET | N | Sewage Pumping Station | INUSE
14210 | PEWSHAM | LONDON ROAD ALSO S0191 | N | Sewage Pumping Station | INUSE
14211 | ROYAL WOOTTON BASSETT | WESTBURY PARK | N | Sewage Pumping Station | INUSE
14212 | BURTON | . | N | Sewage Pumping Station | INUSE
14213 | CRUDWELL | THE RIDGEWAY | N | Sewage Pumping Station | INUSE
14214 | LEA | CRAB MILL LANE | N | Sewage Pumping Station | INUSE
14215 | BOVINGTON | EAST WING | S | Sewage Pumping Station | INUSE
14216 | STOBOROUGH | KINGS ARMS | S | Sewage Pumping Station | INUSE
14217 | UPTON | HIBBS CLOSE | S | Sewage Pumping Station | INUSE
14218 | BOVINGTON | A T D U | S | Sewage Pumping Station | INUSE
14219 | UPTON | SANDY LANE | S | Sewage Pumping Station | INUSE
14220 | LYTCHETT MATRAVERS | BULBURY LANE | S | Sewage Pumping Station | INUSE
14221 | UPTON | FRENCHS FARM | S | Sewage Pumping Station | INUSE
14222 | EAST KNIGHTON | BLACKNOLL | S | Sewage Pumping Station | INUSE
14224 | LYTCHETT MATRAVERS | WIMBORNE ROAD | S | Sewage Pumping Station | INUSE
14226 | CHURCH KNOWLE | GLEBE FARM | S | Sewage Pumping Station | INUSE
14227 | STUDLAND | WADMORE LANE | S | Sewage Pumping Station | INUSE
14228 | BOVINGTON | RHINE ROAD | S | Sewage Pumping Station | INUSE
14229 | WAREHAM | WEST MILL CRESCENT | S | Sewage Pumping Station | INUSE
14230 | BOVINGTON | CRANES MOOR | S | Sewage Pumping Station | INUSE
14232 | CHURCH KNOWLE | ANIMAL SANCTUARY | S | Sewage Pumping Station | INUSE
14234 | BOVINGTON | STANLEY BARRACKS | S | Sewage Pumping Station | INUSE
14235 | BOVINGTON | DUNCAN CRESCENT | S | Sewage Pumping Station | INUSE
14236 | UPTON | GORSE LANE | S | Sewage Pumping Station | INUSE
14237 | WINFRITH NEWBURGH | WINFRITH CHURCH | S | Sewage Pumping Station | INUSE
14238 | SANDFORD | HEATH COTTAGES | S | Sewage Pumping Station | INUSE
14239 | WAREHAM | SANDFORD LANE INDUSTRIAL ESTATE | S | Sewage Pumping Station | INUSE
14240 | BOVINGTON | MORRIS ROAD | S | Sewage Pumping Station | INUSE
14241 | SANDFORD | MORDEN ROAD | S | Sewage Pumping Station | INUSE
14242 | MORDEN | HECTORS CORNER | S | Sewage Pumping Station | INUSE
14243 | MORDEN | COCK AND BOTTLE | S | Sewage Pumping Station | INUSE
14244 | SWANAGE | DURLSTON ROAD | S | Sewage Pumping Station | INUSE
14245 | UPTON | SHORE LANE | S | Sewage Pumping Station | INUSE
14246 | SWANAGE | LIFE BOAT STATION COMMINUTOR | S | Sewage Pumping Station | INUSE
14247 | LYTCHETT MATRAVERS | FLOWERS DROVE | S | Sewage Pumping Station | INUSE
14248 | EAST BURTON | CROSS ROADS | S | Sewage Pumping Station | INUSE
14249 | BLOXWORTH | FOX POUND | S | Sewage Pumping Station | INUSE
14250 | LYTCHETT MATRAVERS | HOPMANS CLOSE | S | Sewage Pumping Station | INUSE
14251 | UPTON | TREE HAMLETS | S | Sewage Pumping Station | INUSE
14252 | STUDLAND | COOMBE | S | Sewage Pumping Station | INUSE
14254 | WAREHAM | BESTWALL | S | Sewage Pumping Station | INUSE
14255 | STOBOROUGH | RIDGE | S | Sewage Pumping Station | INUSE
14256 | AFFPUDDLE | . | S | Sewage Pumping Station | INUSE
14257 | STOBOROUGH | TUCKERS MILL CLOSE | S | Sewage Pumping Station | INUSE
14258 | BERE REGIS | ELDER ROAD | S | Sewage Pumping Station | INUSE
14259 | WAREHAM | SOUTH EAST | S | Sewage Pumping Station | INUSE
14260 | LYTCHETT MATRAVERS | GLEBE ROAD | S | Sewage Pumping Station | INUSE
14261 | STUDLAND | WATERY LANE | S | Sewage Pumping Station | INUSE
14262 | BERE REGIS | SITTERTON | S | Sewage Pumping Station | INUSE
14263 | CORFE CASTLE | RED LANE | S | Sewage Pumping Station | INUSE
14264 | EAST KNIGHTON | . | S | Sewage Pumping Station | INUSE
14265 | UPTON | MOORLANDS WAY | S | Sewage Pumping Station | INUSE
14266 | WAREHAM | SANDFORD LANE | S | Sewage Pumping Station | INUSE
14268 | WAREHAM | NORTH BRIDGE | S | Sewage Pumping Station | INUSE
14269 | BERE REGIS | COURT FARM SOUTHBROOK | S | Sewage Pumping Station | INUSE
14270 | BOVINGTON | TERMINAL | S | Sewage Pumping Station | INUSE
14271 | WAREHAM | DRAX AVENUE | S | Sewage Pumping Station | INUSE
14272 | BRIANTSPUDDLE | . | S | Sewage Pumping Station | INUSE
14273 | WOOL | RAILWAY COTTAGES | S | Sewage Pumping Station | INUSE
14274 | EAST CHALDON | . | S | Sewage Pumping Station | INUSE
14275 | CORFE CASTLE | HALVES COTTAGES | S | Sewage Pumping Station | INUSE
14276 | CORFE CASTLE | STUDLAND ROAD | S | Sewage Pumping Station | INUSE
14277 | WOOL | BINDON LANE | S | Sewage Pumping Station | INUSE
14278 | BERE REGIS | RYE HILL CLOSE | S | Sewage Pumping Station | INUSE
14279 | STUDLAND | BEACH CAFE | S | Sewage Pumping Station | INUSE
14280 | LYTCHETT MINSTER | SLOUGH LANE | S | Sewage Pumping Station | INUSE
14281 | LYTCHETT MINSTER | BAKERS ARMS | S | Sewage Pumping Station | INUSE
14282 | STUDLAND | HARDY ROAD | S | Sewage Pumping Station | INUSE
14283 | BARTON ST DAVID | . | W | Sewage Pumping Station | INUSE
14284 | HARDINGTON MANDEVILLE | BENDFORD BRIDGE | W | Sewage Pumping Station | INUSE
14285 | MISTERTON | . | W | Sewage Pumping Station | INUSE
14286 | LOPEN | . | W | Sewage Pumping Station | INUSE
14287 | HINTON ST GEORGE | . | W | Sewage Pumping Station | INUSE
14288 | MARSTON MAGNA | CHURCH LANE | W | Sewage Pumping Station | INUSE
14289 | ILCHESTER | ILCHESTER MAIN | W | Sewage Pumping Station | INUSE
14290 | LANGPORT | WESTOVER | W | Sewage Pumping Station | INUSE
14291 | WEST CAMEL | . | W | Sewage Pumping Station | INUSE
14292 | ILCHESTER | ILCHESTER MEAD | W | Sewage Pumping Station | INUSE
14293 | QUEEN CAMEL | ENGLANDS MEAD GREEN LANE | W | Sewage Pumping Station | INUSE
14294 | DONYATT | . | W | Sewage Pumping Station | INUSE
14295 | YEOVILTON | WEIR | W | Sewage Pumping Station | INUSE
14296 | PODIMORE | . | W | Sewage Pumping Station | INUSE
14297 | CHARD | BEECHINGS CLOSE | W | Sewage Pumping Station | INUSE
14298 | CHILTON CANTELO | SCHOOL | W | Sewage Pumping Station | INUSE
14299 | NORTH CHERITON | GROVE LANE | W | Sewage Pumping Station | INUSE
14300 | YEOVIL | PEN MILL BANBURY | W | Sewage Pumping Station | INUSE
14301 | STALBRIDGE | . | S | Sewage Pumping Station | INUSE
14302 | IDMISTON | . | S | Sewage Pumping Station | INUSE
14303 | BERWICK ST JOHN | . | S | Sewage Pumping Station | INUSE
14304 | ALLINGTON | OLD INN | S | Sewage Pumping Station | INUSE
14305 | SALISBURY | OLD SARUM AIRFIELD (PARTRIDGE WAY) | S | Sewage Pumping Station | INUSE
14306 | BOSCOMBE DOWN | A & AEE | S | Private Sewage Pumping Station | INUSE
14307 | CHILMARK | RAF STATION | S | Private Sewage Pumping Station | INUSE
14309 | DONHEAD ST ANDREW | . | S | Sewage Pumping Station | INUSE
14310 | NETHERAVON | SUPPORT WEAPONS WING | S | Sewage Pumping Station | INUSE
14311 | TILSHEAD | CAMP ROAD | S | Sewage Pumping Station | INUSE
14312 | SHREWTON | HOMANTON | S | Sewage Pumping Station | INUSE
14313 | STAPLEFORD | OVERSTREET | S | Sewage Pumping Station | INUSE
14314 | AMESBURY | SOUTH MILL LANE | S | Sewage Pumping Station | INUSE
14315 | AMESBURY | GLEESONS ESTATE | S | Sewage Pumping Station | INUSE
14316 | EAST KNOYLE | UNDERHILL | S | Sewage Pumping Station | INUSE
14317 | HURDCOTT | . | S | Sewage Pumping Station | INUSE
14318 | DOWNTON | MESH PONDS | S | Sewage Pumping Station | INUSE
14319 | AMESBURY | EJECTOR | S | Sewage Pumping Station | INUSE
14320 | STAPLEFORD | PELICAN INN | S | Sewage Pumping Station | INUSE
14321 | DOWNTON | WATERSIDE | S | Sewage Pumping Station | INUSE
14322 | DINTON | BRATCH LANE | S | Sewage Pumping Station | INUSE
14323 | AMESBURY | FLOWER LANE | S | Sewage Pumping Station | INUSE
14324 | WYLYE | CHEQUERS COTTAGES | S | Sewage Pumping Station | INUSE
14325 | DOWNTON | WICK ESTATE | S | Sewage Pumping Station | INUSE
14326 | STOFORD | . | S | Sewage Pumping Station | INUSE
14327 | LAVERSTOCK | ROSS WARMAFOAM | S | Sewage Pumping Station | INUSE
14328 | HANGING LANGFORD | . | S | Sewage Pumping Station | INUSE
14329 | SALISBURY | PETERSFINGER | S | Sewage Pumping Station | INUSE
14330 | LITTLE LANGFORD | . | S | Sewage Pumping Station | INUSE
14331 | SALISBURY | LONGFORD CASTLE | S | Sewage Pumping Station | INUSE
14332 | WYLYE | CORN MILL | S | Sewage Pumping Station | INUSE
14333 | EAST KNOYLE | SHAFTESBURY ROAD | S | Sewage Pumping Station | INUSE
14334 | DOWNTON | AVON DYKE | S | Sewage Pumping Station | INUSE
14335 | NETHERHAMPTON | MANOR HOUSE | S | Sewage Pumping Station | INUSE
14336 | BERWICK ST JAMES | . | S | Sewage Pumping Station | INUSE
14337 | ALDERBURY | HOME FARM | S | Sewage Pumping Station | INUSE
14338 | NETHERAVON | CAMP ROAD | S | Sewage Pumping Station | INUSE
14339 | DOWNTON | MOOT CLOSE/ MOOT GARDENS | S | Sewage Pumping Station | INUSE
14340 | FOVANT | CHURCH LANE | S | Sewage Pumping Station | INUSE
14341 | ALDERBURY | JUNCTION ROAD | S | Sewage Pumping Station | INUSE
14342 | TEFFONT EVIAS | . | S | Sewage Pumping Station | INUSE
14343 | GREAT WISHFORD | COBBS MILL | S | Sewage Pumping Station | INUSE
14344 | NETHERHAMPTON | WALDRONS FARM | S | Sewage Pumping Station | INUSE
14345 | WOODFALLS | LITTLE WOODFALLS DRIVE | S | Sewage Pumping Station | INUSE
14346 | HINDON | THE DENE | S | Sewage Pumping Station | INUSE
14347 | NETHERHAMPTON | FLOWERLAND | S | Sewage Pumping Station | INUSE
14348 | WOODFALLS | LODGE DROVE | S | Sewage Pumping Station | INUSE
14349 | SALISBURY | STRATFORD SUB CASTLE | S | Sewage Pumping Station | INUSE
14350 | LAVERSTOCK | WHITEBRIDGE ROAD | S | Sewage Pumping Station | INUSE
14351 | TISBURY | UNION ROAD | S | Sewage Pumping Station | INUSE
14352 | LAVERSTOCK | DRAKES STORE | S | Sewage Pumping Station | INUSE
14353 | DOWNTON | SOUTH LANE | S | Sewage Pumping Station | INUSE
14354 | BARFORD ST MARTIN | . | S | Sewage Pumping Station | INUSE
14355 | AMESBURY | COUNTESS ROAD | S | Sewage Pumping Station | INUSE
14356 | WILTON | BULBRIDGE (BURCOMBE ROAD) | S | Sewage Pumping Station | INUSE
14358 | SOUTH NEWTON | BELL INN | S | Sewage Pumping Station | INUSE
14359 | NEWTON TONEY | VILLAGE HALL CAR PARK | S | Sewage Pumping Station | INUSE
14360 | ALDERBURY | GRIMSTEAD ROAD | S | Sewage Pumping Station | INUSE
14361 | EAST KNOYLE | WARMINSTER ROAD | S | Sewage Pumping Station | INUSE
14362 | CHILMARK | . | S | Sewage Pumping Station | INUSE
14363 | DURRINGTON | NAGS HEAD | S | Sewage Pumping Station | INUSE
14364 | FIGHELDEAN | AVON BANKS | S | Sewage Pumping Station | INUSE
14365 | SALISBURY | NETHERHAMPTON ROAD | S | Sewage Pumping Station | INUSE
14367 | MERE | MERE CAUSEWAY | S | Sewage Pumping Station | INUSE
14368 | MERE | EDGEBRIDGE | S | Sewage Pumping Station | INUSE
14369 | MERE | DEAD MAIDS QUARRY | S | Sewage Pumping Station | INUSE
14370 | MAIDEN BRADLEY | FROME ROAD | S | Sewage Pumping Station | INUSE
14371 | CHEDDAR | FROGLANDS | W | Sewage Pumping Station | INUSE
14372 | WEST HUNTSPILL | SLOWAY LANE | W | Sewage Pumping Station | INUSE
14373 | DUNBALL | . | W | Sewage Pumping Station | INUSE
14374 | HIGHBRIDGE | NEWTON | W | Sewage Pumping Station | INUSE
14375 | PEDWELL | . | W | Sewage Pumping Station | INUSE
14376 | MOORLINCH | RIGHT DROVE | W | Sewage Pumping Station | INUSE
14378 | BRIDGWATER | BLAKE GARDENS | W | Sewage Pumping Station | INUSE
14379 | FIDDINGTON | . | W | Sewage Pumping Station | INUSE
14380 | NORTH NEWTON | CHURCH ROAD | W | Sewage Pumping Station | INUSE
14381 | WESTONZOYLAND | . | W | Sewage Pumping Station | INUSE
14382 | BAWDRIP | . | W | Sewage Pumping Station | INUSE
14383 | COMBWICH | BROOKSIDE | W | Sewage Pumping Station | INUSE
14384 | BRIDGWATER | CHILTON STREET SALTLANDS | W | Sewage Pumping Station | INUSE
14385 | BRIDGWATER | BRISTOL ROAD | W | Sewage Pumping Station | INUSE
14386 | GREINTON | MOOR DRIVE | W | Sewage Pumping Station | INUSE
14387 | SHARPNESS | DOCKS WEST | N | Sewage Pumping Station | INUSE
14388 | BERKELEY | PARK VIEW ROAD | N | Sewage Pumping Station | INUSE
14389 | TAUNTON | PRIORY STORM TANKS | W | Sewage Pumping Station | INUSE
14390 | TAUNTON | SILK MILLS | W | Sewage Pumping Station | INUSE
14391 | STOKE ST GREGORY | NO 1 LANE END | W | Sewage Pumping Station | INUSE
14392 | WEST BUCKLAND | . | W | Sewage Pumping Station | INUSE
14393 | HILLFARRANCE | . | W | Sewage Pumping Station | INUSE
14394 | WELLINGTON | MITCHELLS POOL | W | Sewage Pumping Station | INUSE
14395 | HATCH BEAUCHAMP | . | W | Sewage Pumping Station | INUSE
14396 | OVER COMPTON | . | S | Sewage Pumping Station | INUSE
14397 | BEER HACKETT | . | S | Sewage Pumping Station | INUSE
14398 | OWERMOIGNE | CROSSWAYS ROAD | S | Sewage Pumping Station | INUSE
14399 | OSMINGTON MILLS | . | S | Sewage Pumping Station | INUSE
14400 | BROADMAYNE | BROADMAYNE | S | Sewage Pumping Station | INUSE
14402 | OSMINGTON | PONTINS | S | Sewage Pumping Station | INUSE
14403 | TOLLER PORCORUM | LOWER ROAD | S | Sewage Pumping Station | INUSE
14404 | BEAMINSTER | SOUTHGATE | S | Sewage Pumping Station | INUSE
14405 | WEST STAFFORD | DORCHESTER ROAD | S | Sewage Pumping Station | INUSE
14406 | MAIDEN NEWTON | FROME LANE | S | Sewage Pumping Station | INUSE
14407 | STRATTON | STRATTON BRIDGE | S | Sewage Pumping Station | INUSE
14408 | BRADFORD PEVERELL | MR SOFTIES | S | Sewage Pumping Station | INUSE
14409 | BURTON BRADSTOCK | BURTON FRESHWATER | S | Sewage Pumping Station | INUSE
14410 | BURTON BRADSTOCK | BURTON SOUTHOVER | S | Sewage Pumping Station | INUSE
14411 | SYDLING ST NICHOLAS | . | S | Sewage Pumping Station | INUSE
14412 | PUDDLETOWN | BLANDFORD ROAD | S | Sewage Pumping Station | INUSE
14413 | CHIDEOCK | SEATOWN | S | Sewage Pumping Station | INUSE
14414 | CHARMINSTER | NORTH STREET | S | Sewage Pumping Station | INUSE
14415 | LITTON CHENEY | CHICKSBRIDGE | S | Sewage Pumping Station | INUSE
14416 | MINEHEAD | MART ROAD | W | Sewage Pumping Station | INUSE
14417 | DUNSTER | DUNSTER BEACH | W | Sewage Pumping Station | INUSE
14420 | MINEHEAD | QUAY WEST | W | Sewage Pumping Station | INUSE
14421 | CUTCOMBE | . | W | Sewage Pumping Station | INUSE
14422 | SHURTON | . | W | Sewage Pumping Station | INUSE
14423 | BLUE ANCHOR | PILL BRIDGE | W | Sewage Pumping Station | INUSE
14424 | FARRINGDON | . | W | Sewage Pumping Station | INUSE
14425 | CLUTTON | GREENBROOK | N | Sewage Pumping Station | INUSE
14426 | PAULTON | GOOSARD BRIDGE | N | Sewage Pumping Station | INUSE
14427 | HALLATROW | . | N | Sewage Pumping Station | INUSE
14428 | CORSTON | NEWTON ST LOE | N | Sewage Pumping Station | INUSE
14429 | CHEW STOKE | BILBIE ROAD | N | Sewage Pumping Station | INUSE
14430 | CHEW MAGNA | DUMPERS LANE | N | Sewage Pumping Station | INUSE
14431 | BISHOP SUTTON | . | N | Sewage Pumping Station | INUSE
14432 | COMPTON DANDO | TURNBRIDGE | N | Sewage Pumping Station | INUSE
14433 | DILTON MARSH | CLIVEY | N | Sewage Pumping Station | INUSE
14434 | EDINGTON | INMEAD | N | Sewage Pumping Station | INUSE
14435 | WARMINSTER | BOREHAM ROAD | N | Sewage Pumping Station | INUSE
14436 | DILTON MARSH | FAIRHAVEN | N | Sewage Pumping Station | INUSE
14437 | WARMINSTER | PORTWAY | N | Sewage Pumping Station | INUSE
14438 | UPTON SCUDAMORE | . | N | Sewage Pumping Station | INUSE
14439 | WARMINSTER | CALVESWATER | N | Sewage Pumping Station | INUSE
14440 | DILTON MARSH | PEN KNAPP | N | Sewage Pumping Station | INUSE
14441 | WARMINSTER | BISHOPSTROW | N | Sewage Pumping Station | INUSE
14442 | WESTBURY | HAWKERIDGE PARK | N | Sewage Pumping Station | INUSE
14443 | DILTON MARSH | ST MARYS LANE | N | Sewage Pumping Station | INUSE
14444 | WINGFIELD | CHURCH LANE | N | Sewage Pumping Station | INUSE
14445 | WINGFIELD | WINGFIELD COMMON | N | Sewage Pumping Station | INUSE
14446 | WINGFIELD | POMEROY LANE | N | Sewage Pumping Station | INUSE
14447 | KEEVIL | THE STREET | N | Sewage Pumping Station | INUSE
14448 | LIMPLEY STOKE | CROWE HILL | N | Sewage Pumping Station | INUSE
14449 | WESTWOOD | UPPER WESTWOOD | N | Sewage Pumping Station | INUSE
14450 | COULSTON | . | N | Sewage Pumping Station | INUSE
14451 | WESTWOOD | LOWER WESTWOOD | N | Sewage Pumping Station | INUSE
14452 | FRESHFORD | NEW INN | N | Sewage Pumping Station | INUSE
14453 | STAVERTON | NESTLES | N | Sewage Pumping Station | INUSE
14454 | MIDFORD | BOATHOUSE | N | Sewage Pumping Station | INUSE
14455 | NORTH BRADLEY | THE RANK | N | Sewage Pumping Station | INUSE
14456 | BRATTON | TROWBRIDGE ROAD | N | Sewage Pumping Station | INUSE
14457 | BULKINGTON | WICKLEAZE | N | Sewage Pumping Station | INUSE
14458 | NORTH BRADLEY | CHURCHLANDS | N | Sewage Pumping Station | INUSE
14459 | SOUTHWICK | CHANTRY GARDENS | N | Sewage Pumping Station | INUSE
14460 | NORTH BRADLEY | YARNBROOK | N | Sewage Pumping Station | INUSE
14461 | BROUGHTON GIFFORD | THE COMMON | N | Sewage Pumping Station | INUSE
14462 | BROUGHTON GIFFORD | CURTIS ORCHARD | N | Sewage Pumping Station | INUSE
14463 | ATWORTH | PURLPIT | N | Sewage Pumping Station | INUSE
14464 | MELKSHAM | BADER PARK | N | Sewage Pumping Station | INUSE
14466 | SEMINGTON | SEMINGTON BROOK | N | Sewage Pumping Station | INUSE
14467 | HOLT | THE STAR | N | Sewage Pumping Station | INUSE
14468 | MELKSHAM | SEMINGTON ROAD | N | Sewage Pumping Station | INUSE
14469 | GREAT HINTON | . | N | Sewage Pumping Station | INUSE
14470 | WINSLEY | CHURCH FARM (MILBOURNE CLOSE) | N | Sewage Pumping Station | INUSE
14473 | BRADFORD-ON-AVON | WOOLLEY GREEN | N | Sewage Pumping Station | INUSE
14474 | MELKSHAM | SEMINGTON ROUNDABOUT | N | Sewage Pumping Station | INUSE
14475 | BROUGHTON GIFFORD | THE GREEN | N | Sewage Pumping Station | INUSE
14476 | SEMINGTON | LITTLEMARSH | N | Sewage Pumping Station | INUSE
14477 | MELKSHAM | WESTLANDS LANE | N | Sewage Pumping Station | INUSE
14478 | MELKSHAM | NORTHBROOK ROAD | N | Sewage Pumping Station | INUSE
14479 | MELKSHAM | WOODROW ROAD | N | Sewage Pumping Station | INUSE
14480 | MELKSHAM | SPA ROAD | N | Sewage Pumping Station | INUSE
14481 | MELKSHAM | SHAW HILL | N | Sewage Pumping Station | INUSE
14483 | STEEPLE ASHTON | ASHTON COMMON | N | Sewage Pumping Station | INUSE
14485 | MONKTON FARLEIGH | FARLEIGH WICK | N | Sewage Pumping Station | INUSE
14486 | BRADFORD-ON-AVON | SPRINGFIELD | N | Sewage Pumping Station | INUSE
14487 | MELKSHAM | BERRYFIELDS | N | Sewage Pumping Station | INUSE
14488 | MONKTON FARLEIGH | CHURCH FARM | N | Sewage Pumping Station | INUSE
14489 | YATESBURY | VILLAGE | N | Sewage Pumping Station | INUSE
14490 | EDINGTON | TINHEAD LOWER BAYNTON ROAD | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
14491 | WESTBURY LEIGH | MILL LANE | N | Sewage Pumping Station | INUSE
14492 | KENN | KENN PIER | W | Sewage Pumping Station | INUSE
14493 | KINGSTON | BRIDGE | W | Sewage Pumping Station | INUSE
14495 | CLEVEDON | CLEVEDON MAIN | W | Sewage Pumping Station | INUSE
14496 | CONGRESBURY | SOUTH | W | Sewage Pumping Station | INUSE
14497 | KEWSTOKE | SAND ROAD | W | Sewage Pumping Station | INUSE
14498 | UPHILL | . | W | Sewage Pumping Station | INUSE
14501 | BRISTOL | WHITBY ROAD ST ANNES | N | Sewage Pumping Station | INUSE
14502 | BRISTOL | WHITBY ROAD B CO-OP DEPOT ARNOS VALE | N | Sewage Pumping Station | INUSE
14503 | MELKSHAM | BRUNSWICK PARK / JUNCTION LANE | N | Sewage Pumping Station | INUSE
14504 | LAVERSTOCK | MILFORD MANOR GARDENS | S | Sewage Pumping Station | INUSE
14505 | LANGLEY BURREL | PECKINGELL LANE | N | Sewage Pumping Station | INUSE
14507 | SHIREHAMPTON | LAMPLIGHTERS | N | Sewage Pumping Station | INUSE
14508 | SHIREHAMPTON | CERNEY LANE | N | Sewage Pumping Station | INUSE
14510 | TROWBRIDGE | TERMINAL AT BRADFORD ROAD | N | Sewage Pumping Station | INUSE
14511 | COLERNE | PINEWOOD | N | Sewage Pumping Station | INUSE
14512 | GLASTONBURY | PALMERS ROAD | W | Sewage Pumping Station | INUSE
14519 | SOMERTON | BARPOOL LANE | W | Sewage Pumping Station | INUSE
14520 | HEYWOOD | DURSLEY ROAD | N | Sewage Pumping Station | INUSE
14521 | EAST LAMBROOK | . | W | Sewage Pumping Station | INUSE
14523 | LOW HAM | MORETONS LANE | W | Sewage Pumping Station | INUSE
14525 | BABCARY | RIVERSIDE FARM | W | Sewage Pumping Station | INUSE
14526 | SOPWORTH | . | N | Sewage Pumping Station | INUSE
14528 | CARLINGCOTT | STONEAGE LANE | N | Sewage Pumping Station | INUSE
14531 | MIDFORD | TUCKING MILL | N | Sewage Pumping Station | INUSE
14532 | MIDSOMER NORTON | RACKVERNAL COURT | N | Sewage Pumping Station | INUSE
14533 | MIDSOMER NORTON | CAUTLETTS CLOSE | N | Combined Sewer Overflow | INUSE
14534 | HINTON BLEWITT | GLANVILLE FARM | N | Sewage Pumping Station | INUSE
14535 | STREET | THE WITHYS FIELDING ROAD | W | Sewage Pumping Station | INUSE
14538 | WHITCHURCH | THE WITHEYS | N | Sewage Pumping Station | INUSE
14540 | BRADFORD-ON-AVON | WEAVERS BROOK / ST ALDHELMS | N | Sewage Pumping Station | INUSE
14542 | COAT | CRIPPLE STREET (OLD STW SITE) | W | Sewage Pumping Station | INUSE
14543 | FROME | HANDLEMAKERS ROAD | W | Sewage Pumping Station | INUSE
14547 | WEST HARPTREE | . | N | Sewage Pumping Station | INUSE
14549 | ROYAL WOOTTON BASSETT | WHITEHILL LANE | N | Sewage Pumping Station | INUSE
14550 | LACOCK | NETHERCOTE HILL | N | Sewage Pumping Station | INUSE
14551 | BRIDGWATER | BRADNEY BRIDGE | W | Sewage Pumping Station | INUSE
14553 | ILFORD | ILFORD BRIDGES | W | Sewage Pumping Station | INUSE
14554 | CHARD | TOUCHES LANE | W | Sewage Pumping Station | INUSE
14555 | ISLE ABBOTTS | TWO BRIDGES | W | Sewage Pumping Station | INUSE
14558 | COMPTON DURVILLE | STORM SCREEN | W | Combined Sewer Overflow | INUSE
14562 | GLASTONBURY | WIRRAL PARK | W | Sewage Pumping Station | INUSE
14563 | FROME | COURTS BARTON MARSTON LANE | W | Sewage Pumping Station | INUSE
14564 | CHIPPENHAM | MONKTON PARK | N | Sewage Pumping Station | INUSE
14565 | CALNE | DERRY HILL | N | Sewage Pumping Station | INUSE
14567 | HILPERTON | DYMOTT SQUARE | N | S105A Sewage Pumping Station | INUSE
14568 | COLERNE | SOUTHWOOD DOE HOUSING ESTATE | N | Sewage Pumping Station | INUSE
14569 | MALMESBURY | AVON SILK MILLS ALSO S0569 | N | Sewage Pumping Station | INUSE
14570 | AMESBURY | RATFYN LANE | S | Sewage Pumping Station | INUSE
14571 | SANDFORD | ORGANFORD ROAD | S | Sewage Pumping Station | INUSE
14573 | WARMLEY | HORSECROFT GARDENS / WRAXALL ROAD | N | Sewage Pumping Station | INUSE
14574 | HEWISH | PALMERS ELM | W | Sewage Pumping Station | INUSE
14576 | BATHFORD | GARSTONS | N | Sewage Pumping Station | INUSE
14577 | FORD | GREEN LANE | S | Sewage Pumping Station | INUSE
14578 | KINGTON ST MICHAEL | KYNETON WAY | N | Sewage Pumping Station | INUSE
14579 | CORFE MULLEN | MILL FARM | S | Sewage Pumping Station | INUSE
14580 | BRISTOL | ULLSWATER CLOSE | N | Sewage Pumping Station | INUSE
14581 | BRISTOL | VICTORIA ROAD | N | Sewage Pumping Station | INUSE
14582 | BRISTOL | RIVERSIDE ST ANNES | N | Sewage Pumping Station | INUSE
14583 | BRISTOL | WEST TOWN ROAD | N | Sewage Pumping Station | INUSE
14585 | EDINGTON | BROADMEAD LANE (SOM) | W | Sewage Pumping Station | INUSE
14588 | WEST LULWORTH | LULWORTH OUTFALL PS | S | Sewage Pumping Station | INUSE
14591 | COMPTON BISHOP | BIG TREE CLOSE | W | Sewage Pumping Station | INUSE
14592 | WEDMORE | THE LERBURNE | W | Sewage Pumping Station | INUSE
14593 | DEVIZES | MATILDA WAY (SANDCLIFFE FM) | N | Sewage Pumping Station | INUSE
14594 | LONG LOAD | YEOBRIDGE | W | Sewage Pumping Station | INUSE
14595 | LONG LOAD | CHURCH LANE | W | Sewage Pumping Station | INUSE
14596 | LONG LOAD | MEADOW VIEW | W | Sewage Pumping Station | INUSE
14597 | HIGHBRIDGE | LAWRENCE CLOSE ISLEPORT BUSINESS PARK | W | Sewage Pumping Station | INUSE
14598 | LOWER WEARE | . | W | Sewage Pumping Station | INUSE
14599 | CHEDDAR | WEDMORE ROAD | W | Sewage Pumping Station | INUSE
14600 | HIGHBRIDGE | TYLERS END | W | Sewage Pumping Station | INUSE
14601 | TAUNTON | BLACKBROOK BUSINESS PARK SURFACE | W | Sewage Pumping Station | INUSE
14602 | CREECH ST MICHAEL | BULL STREET | W | Sewage Pumping Station | INUSE
14605 | UPTON | PONY DRIVE | S | Sewage Pumping Station | INUSE
14618 | BRISTOL | BUTLERS WALK CREWS HOLE | N | Sewage Pumping Station | INUSE
14620 | PEWSEY | SALISBURY ROAD | N | Sewage Pumping Station | INUSE
14621 | PORTISHEAD | TOWN HARBOUR ROAD | W | Sewage Pumping Station | INUSE
14624 | SALTFORD | MEAD LANE | N | Sewage Pumping Station | INUSE
14627 | WICKWAR | INLET P.S | N | Sewage Pumping Station | INUSE
14629 | WINCANTON | BENNETS FIELD | W | Sewage Pumping Station | INUSE
14630 | HASELBURY PLUCKNETT | . | W | Sewage Pumping Station | INUSE
14631 | MARK | NORTHWICK ROAD | W | Sewage Pumping Station | INUSE
14632 | TAUNTON | MAIDENBROOK | W | Sewage Pumping Station | INUSE
14634 | WELLINGTON | FARTHINGS PITTS | W | Sewage Pumping Station | INUSE
14635 | LYNEHAM | A SITE (PS 1) | N | Sewage Pumping Station | INUSE
14636 | LYNEHAM | BUILDING 383 (C SITE PS 2) | N | Sewage Pumping Station | INUSE
14637 | LYNEHAM | BUILDING 212 (D SITE PS 3) | N | Sewage Pumping Station | INUSE
14638 | LYNEHAM | CRASH BAY (D SITE PS 4) | N | Sewage Pumping Station | INUSE
14639 | LYNEHAM | TECHNICAL SITE DRY WELL (PS 5) | N | Sewage Pumping Station | INUSE
14640 | LYNEHAM | GYMNASIUM (PS 8) | N | Sewage Pumping Station | INUSE
14641 | LYNEHAM | DOMESTIC SITE (PS 9) | N | Sewage Pumping Station | INUSE
14642 | LYNEHAM | BELFAST MEAD (PS 10) | N | Sewage Pumping Station | INUSE
14643 | LYNEHAM | PRESTON LANE BUILDING 488 (PS 11 AND 12) | N | Sewage Pumping Station | INUSE
14644 | LYNEHAM | HALIFAX BLOCK (PS 13) | N | Sewage Pumping Station | INUSE
14645 | LYNEHAM | BUILDING 380 (C SITE PS 14) | N | Sewage Pumping Station | INUSE
14647 | BARRINGTON | GIBBS LANE | W | Sewage Pumping Station | INUSE
14648 | CHILTON POLDEN | MAIN | W | Sewage Pumping Station | INUSE
14649 | TAUNTON | LISIEUX WAY | W | Sewage Pumping Station | INUSE
14650 | DEVIZES | ADLAM CLOSE 2 | N | S105A Sewage Pumping Station | INUSE
14651 | KEYNSHAM | SCHWEPPS DEPOT ASHMEAD RD KEYN | N | Private Sewage Pumping Station | INUSE
14652 | BRISTOL | MAZE STREET | N | S105A Sewage Pumping Station | INUSE
14653 | WESTON-SUPER-MARE | MARINE PARADE | W | Private Sewage Pumping Station | INUSE
14654 | WESTBURY | WASHINGTON ROAD | N | Sewage Pumping Station | INUSE
14656 | BRISTOL | UWE FRENCHAY CAMPUS | N | Private Sewage Pumping Station | INUSE
14657 | STREET | STRODE COLLEGE | W | S105A Sewage Pumping Station | INUSE
14658 | CHARD | COKER WAY | W | S105A Sewage Pumping Station | INUSE
14659 | WINSCOMBE | BEEHIVE COTTAGE CHURCHILL GREEN SINGLE PROPERTY | W | Private Sewage Pumping Station | INUSE
14660 | BRISTOL | BURCOTT ROAD | N | S105A Sewage Pumping Station | INUSE
14661 | WIMBORNE | WOOLSBRIDGE INDUSTRIAL ESTATE | S | Private Sewage Pumping Station | INUSE
14662 | MALMESBURY | PARK MEAD | N | S105A Sewage Pumping Station | INUSE
14663 | BRISTOL | BACKFIELDS | N | Private Sewage Pumping Station | INUSE
14664 | CALNE | ANCHOR ROAD | N | S105A Sewage Pumping Station | INUSE
14665 | RINGWOOD | BURLEY MANOR HOTEL | S | Private Sewage Pumping Station | INUSE
14666 | HULLAVINGTON | HILL HAYES LANE | N | Private Sewage Pumping Station | INUSE
14667 | DEVIZES | ADLAM CLOSE 1 | N | S105A Sewage Pumping Station | INUSE
14668 | DOWNEND | CHESTNUT ROAD | N | Private Sewage Pumping Station | INUSE
14669 | BRISTOL | WOODLAND COURT | N | Private Sewage Pumping Station | INUSE
14670 | CHRISTCHURCH | BEAVER INDUSTRIAL ESTATE AIRFIELD ROAD | S | Private Sewage Pumping Station | INUSE
14671 | BERKELEY | BERKELEY KENNELS | N | Private Sewage Pumping Station | INUSE
14672 | BRADFORD-ON-AVON | WIDBROOK VIEW | N | S105A Sewage Pumping Station | INUSE
14673 | BRISTOL | BOWER ASHTON TERRACE | N | Private Sewage Pumping Station | INUSE
14674 | ALMONDSBURY | COUNCIL DEPOT | N | S105A Sewage Pumping Station | INUSE
14675 | POOLE | CLIFF DRIVE | S | Private Sewage Pumping Station | INUSE
14676 | DOWNEND | DOWNEND ROAD | N | Private Sewage Pumping Station | INUSE
14677 | BRISTOL | SEABANK SPS AVONMOUTH STW | N | Private Sewage Pumping Station | INUSE
14678 | POOLE | BAITER TOILETS | S | Private Sewage Pumping Station | INUSE
14679 | BATH | MIDLAND BRIDGE ROAD | N | Private Sewage Pumping Station | INUSE
14680 | WINSCOMBE | CAMELOT COTTAGE CHURCHILL GREEN SINGLE PROPERTY | W | Private Sewage Pumping Station | INUSE
14681 | YEOVIL | ARTILLERY ROAD | W | S105A Sewage Pumping Station | INUSE
14682 | CHRISTCHURCH | EJECTOR SPS AIRPORT | S | Private Sewage Pumping Station | INUSE
14683 | AVONMOUTH | AVONMOUTH STW | N | Private Sewage Pumping Station | INUSE
14684 | BRISTOL | ST. ANDREWS ROAD SINGLE PROPERTY | N | Private Sewage Pumping Station | INUSE
14685 | MALMESBURY | 1 RIVER VIEW PARK ROAD SINGLE PROPERTY | N | Private Sewage Pumping Station | INUSE
14686 | BECKINGTON | TROWBRIDGE ROAD | N | Private Sewage Pumping Station | INUSE
14687 | BOURNEMOUTH | AVIATION PARK WEST 1 AIRPORT | S | Private Sewage Pumping Station | INUSE
14688 | BOURNEMOUTH | UNDERCLIFFE DRIVE | S | Private Sewage Pumping Station | INUSE
14689 | WESTON-SUPER-MARE | COPSE CORNER | W | S105A Sewage Pumping Station | INUSE
14690 | POOLE | ORCHARD AVENUE | S | S105A Sewage Pumping Station | INUSE
14691 | WELLS | POLICE STATION GLASTONBURY ROAD | W | S105A Sewage Pumping Station | INUSE
14692 | POOLE | HATCH POND ROAD | S | Private Sewage Pumping Station | INUSE
14693 | BANWELL | EAST STREET | W | S105A Sewage Pumping Station | INUSE
14694 | MEARE | MILLBATCH LANE | W | S105A Sewage Pumping Station | INUSE
14695 | CASTLE CARY | WAREHOUSE TORBAY ROAD | W | Sewage Pumping Station | INUSE
14696 | WIMBORNE | WOOLSBRIDGE IND ESTATE | S | Private Sewage Pumping Station | INUSE
14697 | STANTON ST. QUINTIN | HIGHWAYS MAINTENANCE DEPOT | N | Private Sewage Pumping Station | INUSE
14698 | BRISTOL | BROADLEAS | N | Private Sewage Pumping Station | INUSE
14699 | RINGWOOD | HURN FOREST ST LEONARDS HOSPITAL | S | Private Sewage Pumping Station | INUSE
14700 | WESTON-SUPER-MARE | MOORLAND CARAVAN PARK | W | Private Sewage Pumping Station | INUSE
14701 | ROYAL WOOTTON BASSETT | WHITEHILL LANE | N | Private Sewage Pumping Station | INUSE
14702 | RANGEWORTHY | POOL FARM 2 | N | Private Sewage Pumping Station | INUSE
14703 | RANGEWORTHY | POOL FARM 3 | N | Private Sewage Pumping Station | INUSE
14704 | RANGEWORTHY | POOL FARM 1 | N | Private Sewage Pumping Station | INUSE
14705 | CHRISTCHURCH | THE CROW'S NEST WHARNCLIFFE ROAD | S | Private Sewage Pumping Station | INUSE
14706 | CREWKERNE | QUIRES BROOK SINGLE PROPERTY | W | Private Sewage Pumping Station | INUSE
14708 | WESTBURY | BITHAM MILL | N | S105A Sewage Pumping Station | INUSE
14709 | STREET | HIGH STREET | W | Private Sewage Pumping Station | INUSE
14710 | CORSHAM | KINNEIR CLOSE | N | S105A Sewage Pumping Station | INUSE
14711 | BRADFORD-ON-AVON | BRADFORD MARINA | N | S105A Sewage Pumping Station | INUSE
14712 | BRISTOL | BEAUFORT COURT | N | S105A Sewage Pumping Station | INUSE
14713 | DEVIZES | CASTLE LANE | N | Private Sewage Pumping Station | INUSE
14714 | BRISTOL | CABOT PARK | N | Private Sewage Pumping Station | INUSE
14716 | SEAVINGTON | CHURCH LANE | W | Private Sewage Pumping Station | INUSE
14717 | HIGHBRIDGE | EDITHMEAD | W | Private Sewage Pumping Station | INUSE
14718 | BOURNEMOUTH | SOUTH EAST SECTOR AIRPORT | S | Private Sewage Pumping Station | INUSE
14719 | YEOVIL | CARAVAN PARK MARSH LANE | W | Private Sewage Pumping Station | INUSE
14720 | MALMESBURY | 2 RIVER VIEW PARK ROAD SINGLE PROPERTY | N | Private Sewage Pumping Station | INUSE
14721 | DORCHESTER | UKAEA WINFRITH SITE | S | Private Sewage Pumping Station | INUSE
14722 | WESTON-SUPER-MARE | BRISTOL ROAD LOWER | W | Private Sewage Pumping Station | INUSE
14723 | WESTON-SUPER-MARE | FIELD NEAR FULL QUART | W | S105A Sewage Pumping Station | INUSE
14724 | CHILTON POLDEN | DRAINAGE POND SEDGEMOOR COUNCIL | W | Private Sewage Pumping Station | INUSE
14725 | LEIGH WOODS | GARDEN BRIDGE VIEW HOUSE | W | S105A Sewage Pumping Station | INUSE
14726 | WARMINSTER | GRANADA SERVICES | N | Private Sewage Pumping Station | INUSE
14727 | BOURNEMOUTH | AVIATION PARK WEST 3 AIRPORT | S | Private Sewage Pumping Station | INUSE
14728 | BRISTOL | CLEEVE COURT | N | S105A Sewage Pumping Station | INUSE
14729 | CHIPPENHAM | AUDLEY ROAD | N | Private Sewage Pumping Station | INUSE
14730 | WINSCOMBE | BRIDGWATER ROAD | W | Private Sewage Pumping Station | INUSE
14731 | POOLE | CHADDESLEY GLEN | S | Private Sewage Pumping Station | INUSE
14732 | DORCHESTER | LONDON ROAD | S | S105A Sewage Pumping Station | INUSE
14733 | MERRIOTT | THE PIECE | W | S105A Sewage Pumping Station | INUSE
14734 | OLD SARUM | CASTLE WELL DRIVE | S | Private Sewage Pumping Station | INUSE
14735 | BRIDGWATER | CELLOPHANE SITE 2 | W | Private Sewage Pumping Station | INUSE
14736 | BRIDGWATER | ENTRANCE CELLOPHANE WORKS | W | Private Sewage Pumping Station | INUSE
14737 | BRISTOL | ST. MARYS CLOSE | N | S105A Sewage Pumping Station | INUSE
14738 | DEVIZES | OLD PARK | N | S105A Sewage Pumping Station | INUSE
14739 | BRISTOL | KING WILLIAM ALE HOUSE | N | Private Sewage Pumping Station | INUSE
14740 | DEVIZES | COUCH LANE | N | Private Sewage Pumping Station | INUSE
14741 | CHITTENING | CHITTENING INDUSTRIAL ESTATE | N | Private Sewage Pumping Station | INUSE
14743 | DORCHESTER | WINFRITH TECHNOLOGY CENTRE | S | Private Sewage Pumping Station | INUSE
14744 | BITTON | BATH ROAD | N | Private Sewage Pumping Station | INUSE
14745 | CHIPPENHAM | CHARTER COUNTY PRIMARY SCHOOL | N | Private Sewage Pumping Station | INUSE
14746 | WESTBURY | CEMENT WORKS SLAG LANE | N | Private Sewage Pumping Station | INUSE
14747 | BOURNEMOUTH | AVIATION PARK WEST 2 AIRPORT | S | Private Sewage Pumping Station | INUSE
14748 | BRIDGWATER | SOMERSET BRIDGE | W | Private Sewage Pumping Station | INUSE
14749 | LITTLE SOMERFORD | RAILWAY COTTAGES | N | S105A Sewage Pumping Station | INUSE
14750 | WESTON-SUPER-MARE | THE GARAGE OLD WESTLAND | W | Private Sewage Pumping Station | INUSE
14751 | BLANDFORD FORUM | PUMP HOUSE CLAYSMORE SCHOOL | S | Private Sewage Pumping Station | INUSE
14752 | OLVESTON | ELBERTON ROAD | N | Private Sewage Pumping Station | INUSE
14753 | BRIDGWATER | CELLOPHANE SITE 1 | W | Private Sewage Pumping Station | INUSE
14754 | BRIDGWATER | BUILDINGS SOUTH SYDENHAM MANOR | W | Private Sewage Pumping Station | INUSE
14755 | SHERSTON | CHURCH STREET | N | S105A Sewage Pumping Station | INUSE
14757 | BRISTOL | HERAPATH STREET | N | Private Sewage Pumping Station | INUSE
14759 | WESTON-SUPER-MARE | SANDRINGHAM ROAD | W | Private Sewage Pumping Station | INUSE
14760 | WIMBORNE | COBHAM ROAD FERNDOWN | S | Private Sewage Pumping Station | INUSE
14761 | MELKSHAM | LITTLEJOHN AVENUE | N | S105A Sewage Pumping Station | INUSE
14762 | BRISTOL | BRISTOL BUSINESS PARK | N | Private Sewage Pumping Station | INUSE
14763 | BRISTOL | FILTON ROAD | N | Private Sewage Pumping Station | INUSE
14764 | WESTON-SUPER-MARE | OPPOSITE WOODSPRING STADIUM | W | Private Sewage Pumping Station | INUSE
14765 | MINETY | MALMESBURY ROAD | N | Private Sewage Pumping Station | INUSE
14766 | WESTON-SUPER-MARE | OPPOSITE UNIT 7 WESTLAND BUSINESS PARK | W | Private Sewage Pumping Station | INUSE
14767 | DORCHESTER | WEYMOUTH ROAD FOOTBALL STADIUM | S | Private Sewage Pumping Station | INUSE
14768 | WILLSBRIDGE | WILLSBRIDGE HILL | N | Private Sewage Pumping Station | INUSE
14769 | CHRISTCHURCH | ELECTRIC SUB STATION AIRFIELD WAY | S | Private Sewage Pumping Station | INUSE
14770 | BRISTOL | CHITTENING INDUSTRIAL ESTATE | N | Private Sewage Pumping Station | INUSE
15000 | COMPTON MARTIN | UNDERTOWN LANE | N | Sewage Pumping Station | INUSE
15001 | SOUTHBOURNE | WICK LANE | S | Sewage Pumping Station | INUSE
15002 | BOSCOMBE | NO 1 | S | Sewage Pumping Station | INUSE
15003 | BOSCOMBE | NO 2 | S | Sewage Pumping Station | INUSE
15004 | HENGISTBURY HEAD | DOUBLE DYKES | S | Sewage Pumping Station | INUSE
15005 | SOUTHBOURNE | BEDFORD BEACH | S | Sewage Pumping Station | INUSE
15006 | BOURNEMOUTH | NO 2 | S | Sewage Pumping Station | INUSE
15007 | BOURNEMOUTH | IFORD LANE TUCKTON | S | Sewage Pumping Station | INUSE
15008 | BOURNEMOUTH | RINGWOOD ROAD | S | Sewage Pumping Station | INUSE
15009 | BOURNEMOUTH | ALUM CHINE | S | Sewage Pumping Station | INUSE
15010 | BOSCOMBE | NO 3 | S | Sewage Pumping Station | INUSE
15011 | BOURNEMOUTH | ST IVES GARDENS | S | Sewage Pumping Station | INUSE
15012 | BOURNEMOUTH | KINSON MAIN MILLHAMS ROAD | S | Sewage Pumping Station | INUSE
15013 | SOUTHBOURNE | HENGISTBURY HEAD | S | Sewage Pumping Station | INUSE
15014 | HENGISTBURY HEAD | WARDENS COTTAGE | S | Sewage Pumping Station | INUSE
15015 | BOURNEMOUTH | MUSCLIFF LANE | S | Sewage Pumping Station | INUSE
15016 | SOUTHBOURNE | AMENITIES | S | Sewage Pumping Station | INUSE
15017 | BOURNEMOUTH | FISHERMANS WALK | S | Sewage Pumping Station | INUSE
15018 | BOURNEMOUTH | WEST OVERCLIFF | S | Sewage Pumping Station | INUSE
15019 | BOURNEMOUTH | NO 1 | S | Sewage Pumping Station | INUSE
15020 | HIGHCLIFFE | BUTE DRIVE | S | Sewage Pumping Station | INUSE
15021 | CHRISTCHURCH | MILLHAMS STREET | S | Sewage Pumping Station | INUSE
15022 | HIGHCLIFFE | MARRYAT COURT | S | Sewage Pumping Station | INUSE
15024 | CHRISTCHURCH | HOBORNE FARM | S | Sewage Pumping Station | INUSE
15025 | CHRISTCHURCH | LINKS DRIVE | S | Sewage Pumping Station | INUSE
15026 | CHRISTCHURCH | RODNEY DRIVE | S | Sewage Pumping Station | INUSE
15027 | CHRISTCHURCH | AVENUE ROAD | S | Sewage Pumping Station | INUSE
15028 | CHRISTCHURCH | CLIVE ROAD | S | Sewage Pumping Station | INUSE
15029 | CHRISTCHURCH | CONIFER CLOSE | S | Sewage Pumping Station | INUSE
15030 | CHRISTCHURCH | ARGYLE ROAD | S | Sewage Pumping Station | INUSE
15031 | CHRISTCHURCH | AMBERWOOD GARDENS | S | Sewage Pumping Station | INUSE
15032 | MUDEFORD | MUDEFORD QUAY | S | Sewage Pumping Station | INUSE
15033 | MUDEFORD | MUDEFORD CHURCH | S | Sewage Pumping Station | INUSE
15034 | CHRISTCHURCH | ENDFIELD ROAD | S | Sewage Pumping Station | INUSE
15035 | CHRISTCHURCH | QUEENS ROAD | S | Sewage Pumping Station | INUSE
15036 | CHRISTCHURCH | ABINGDON DRIVE | S | Sewage Pumping Station | INUSE
15037 | CHRISTCHURCH | QUOMPS NO 2 | S | Sewage Pumping Station | INUSE
15038 | CHRISTCHURCH | AVON MILL LANE | S | Sewage Pumping Station | INUSE
15039 | CHRISTCHURCH | BEACONSFIELD ROAD | S | Sewage Pumping Station | INUSE
15040 | CHRISTCHURCH | WILVERLEY ROAD | S | Sewage Pumping Station | INUSE
15041 | CHRISTCHURCH | LODGE ROAD | S | Sewage Pumping Station | INUSE
15042 | BURTON | STONY LANE | S | Sewage Pumping Station | INUSE
15043 | MUDEFORD | MUDEFORD GARDENS | S | Sewage Pumping Station | INUSE
15044 | BURTON | SANDY PLOT | S | Sewage Pumping Station | INUSE
15045 | CHRISTCHURCH | BRIDGE STREET | S | Sewage Pumping Station | INUSE
15046 | CHRISTCHURCH | RUSSELL DRIVE RIVERSLEA ESTATE | S | Sewage Pumping Station | INUSE
15047 | FERNDOWN | REDWOOD DRIVE | S | Sewage Pumping Station | INUSE
15048 | VERWOOD | ACACIA AVENUE | S | Sewage Pumping Station | INUSE
15049 | WIMBORNE | BROOK ROAD NO 3 | S | Sewage Pumping Station | INUSE
15050 | WIMBORNE | WINSTON CHURCHILL | S | Sewage Pumping Station | INUSE
15051 | CORFE MULLEN | RUSHCOMBE BOTTOM | S | Sewage Pumping Station | INUSE
15052 | VERWOOD | EBBLAKE | S | Sewage Pumping Station | INUSE
15053 | FERNDOWN | GOLF LINKS ROAD | S | Sewage Pumping Station | INUSE
15054 | VERWOOD | BLACKMOOR ROAD | S | Sewage Pumping Station | INUSE
15055 | WOOLSBRIDGE | INDUSTRIAL ESTATE | S | Sewage Pumping Station | INUSE
15056 | SHAPWICK | SHAPWICK CROSS | S | Sewage Pumping Station | INUSE
15057 | FERNDOWN | THAMES CLOSE | S | Sewage Pumping Station | INUSE
15058 | STURMINSTER MARSHALL | HIGH STREET | S | Sewage Pumping Station | INUSE
15059 | WEST MOORS | THREE LEGGED CROSS | S | Sewage Pumping Station | INUSE
15060 | WEST MOORS | PENNINGTON COPSE | S | Sewage Pumping Station | INUSE
15061 | SHAPWICK | SHAPWICK EAST | S | Sewage Pumping Station | INUSE
15062 | STURMINSTER MARSHALL | CHURCH STREET | S | Sewage Pumping Station | INUSE
15063 | STURMINSTER MARSHALL | NEWTON ROAD | S | Sewage Pumping Station | INUSE
15064 | SHAPWICK | STEWARDS LANE | S | Sewage Pumping Station | INUSE
15065 | STURMINSTER MARSHALL | STATION ROAD | S | Sewage Pumping Station | INUSE
15066 | WIMBORNE | BROOK ROAD NO 2 | S | Sewage Pumping Station | INUSE
15067 | WEST PARLEY | CHRISTCHURCH ROAD | S | Sewage Pumping Station | INUSE
15068 | ST LEONARDS | WAYSIDE ROAD NO 1 | S | Sewage Pumping Station | INUSE
15069 | WIMBORNE | EAST BOROUGH ROAD | S | Sewage Pumping Station | INUSE
15070 | WIMBORNE | HAYES LANE COLEHILL | S | Sewage Pumping Station | INUSE
15071 | ST LEONARDS | CRAIGSIDE ROAD | S | Sewage Pumping Station | INUSE
15072 | FERNDOWN | AMEYSFORD ROAD | S | Sewage Pumping Station | INUSE
15073 | WIMBORNE | PILFORD HEATH | S | Sewage Pumping Station | INUSE
15074 | WEST MOORS | THE FOREST | S | Sewage Pumping Station | INUSE
15075 | CORFE MULLEN | PARDYS HILL | S | Sewage Pumping Station | INUSE
15076 | WIMBORNE | CUTHBURY CLOSE | S | Sewage Pumping Station | INUSE
15077 | WIMBORNE | THE BOATYARD | S | Sewage Pumping Station | INUSE
15078 | FERNDOWN | A31 TRICKETTS CROSS | S | Sewage Pumping Station | INUSE
15079 | WIMBORNE | POOLE ROAD | S | Sewage Pumping Station | INUSE
15080 | FERNDOWN | DUGDELL CLOSE | S | Sewage Pumping Station | INUSE
15081 | STONEY DOWN | CRUMPET FARM ROAD | S | Sewage Pumping Station | INUSE
15082 | WIMBORNE | BROOK ROAD NO 1 | S | Sewage Pumping Station | INUSE
15083 | ST LEONARDS | FOREST EDGE DRIVE | S | Sewage Pumping Station | INUSE
15084 | VERWOOD | POTTERNE WAY | S | Sewage Pumping Station | INUSE
15085 | ST IVES | AVON CASTLE | S | Sewage Pumping Station | INUSE
15086 | VERWOOD | ASPEN DRIVE | S | Sewage Pumping Station | INUSE
15087 | ST LEONARDS | WAYSIDE ROAD NO 2 | S | Sewage Pumping Station | INUSE
15088 | ALDERHOLT | SANDLEHEATH ROAD | S | Sewage Pumping Station | INUSE
15089 | ST LEONARDS | LIONS LANE ASHLEY HEATH | S | Sewage Pumping Station | INUSE
15090 | WEST PARLEY | CHURCH LANE | S | Sewage Pumping Station | INUSE
15091 | FERNDOWN | ALDRIDGE ROAD | S | Sewage Pumping Station | INUSE
15092 | BURBAGE | STIBBS GREEN | N | Sewage Pumping Station | INUSE
15093 | SEEND | BARGE INN | N | Sewage Pumping Station | INUSE
15094 | WORTON | ORCHARD | N | Sewage Pumping Station | INUSE
15095 | STERT | FULLAWAY FARM | N | Sewage Pumping Station | INUSE
15096 | DEVIZES | OLD PARK | N | Sewage Pumping Station | INUSE
15097 | PEWSEY | WOOTTON RIVERS | N | Sewage Pumping Station | INUSE
15098 | DEVIZES | MAYENNE PLACE | N | Sewage Pumping Station | INUSE
15099 | DEVIZES | WAIBLINGEN WAY | N | Sewage Pumping Station | INUSE
15100 | NORTH NEWNTON | . | N | Sewage Pumping Station | INUSE
15101 | PATNEY | PATNEY WEIR | N | Sewage Pumping Station | INUSE
15102 | MARSTON | THE PLOUGH | N | Sewage Pumping Station | INUSE
15103 | BROMHAM | LOOP HILL | N | Sewage Pumping Station | INUSE
15104 | DEVIZES | AVON ROAD | N | Sewage Pumping Station | INUSE
15105 | BROMHAM | WESTBROOK GREEN | N | Sewage Pumping Station | INUSE
15106 | POULSHOT | TOWNSEND | N | Sewage Pumping Station | INUSE
15107 | WILSFORD | . | N | Sewage Pumping Station | INUSE
15108 | POTTERNE | COURT HILL | N | Sewage Pumping Station | INUSE
15109 | NORTH TIDWORTH | THE RAM | N | Sewage Pumping Station | INUSE
15110 | ETCHILHAMPTON | MIXON CLOSE | N | Sewage Pumping Station | INUSE
15111 | ALL CANNINGS | . | N | Sewage Pumping Station | INUSE
15112 | LYDEWAY | MARSH FARM | N | Sewage Pumping Station | INUSE
15113 | ROWDE | MARSH LANE | N | Sewage Pumping Station | INUSE
15114 | OARE | HIGH STREET | N | Sewage Pumping Station | INUSE
15115 | CHIRTON | SMALL STREET | N | Sewage Pumping Station | INUSE
15116 | COATE | LODGE | N | Sewage Pumping Station | INUSE
15117 | DEVIZES | DUNKIRK HILL | N | Sewage Pumping Station | INUSE
15118 | SEEND | NEW BULDINGS | N | Sewage Pumping Station | INUSE
15119 | CONOCK | . | N | Sewage Pumping Station | INUSE
15120 | ALLINGTON | . | N | Sewage Pumping Station | INUSE
15121 | COMPTON | ENFORD | N | Sewage Pumping Station | INUSE
15122 | ENFORD | LONG STREET | N | Sewage Pumping Station | INUSE
15123 | SEEND | BELL INN / BELL HILL | N | Sewage Pumping Station | INUSE
15124 | ENFORD | COOMBE | N | Sewage Pumping Station | INUSE
15125 | WORTON | MILL ROAD | N | Sewage Pumping Station | INUSE
15126 | MARDEN | HATFIELDS | N | Sewage Pumping Station | INUSE
15127 | LYDEWAY | CLOCK INN | N | Sewage Pumping Station | INUSE
15128 | SEEND | SELLS GREEN | N | Sewage Pumping Station | INUSE
15129 | POTTERNE | WICK | N | Sewage Pumping Station | INUSE
15130 | PEWSEY | WHARF | N | Sewage Pumping Station | INUSE
15131 | COLLINGBOURNE KINGSTON | . | N | Sewage Pumping Station | INUSE
15132 | WILCOT | CANAL CLOSE | N | Sewage Pumping Station | INUSE
15133 | OARE | SUNNYHILL LANE | N | Sewage Pumping Station | INUSE
15134 | SEVERN BEACH | . | N | Sewage Pumping Station | INUSE
15135 | YATE | BROAD LANE | N | Sewage Pumping Station | INUSE
15136 | PATCHWAY | SYCAMORE DRIVE | N | Sewage Pumping Station | INUSE
15137 | PATCHWAY | HIGHWOOD TRADING ESTATE EAST | N | Sewage Pumping Station | INUSE
15138 | PILNING | WAINBRIDGE CRESCENT | N | Sewage Pumping Station | INUSE
15139 | PILNING | SWANMOOR BRIDGE | N | Sewage Pumping Station | INUSE
15140 | TYTHERINGTON | SOUTHLANDS | N | Sewage Pumping Station | INUSE
15141 | RANGEWORTHY | PATCH ELM LANE | N | Sewage Pumping Station | INUSE
15142 | WINTERBOURNE | SWAN LANE | N | Sewage Pumping Station | INUSE
15143 | PATCHWAY | HIGHWOOD TRADING ESTATE WEST | N | Sewage Pumping Station | INUSE
15144 | PUCKLECHURCH | WESTERLEIGH ROAD | N | Sewage Pumping Station | INUSE
15145 | HALLEN | HALLEN VILLAGE | N | Sewage Pumping Station | INUSE
15146 | FRAMPTON COTTERELL | CHURCH ROAD | N | Sewage Pumping Station | INUSE
15147 | PILNING | PILL HEAD | N | Sewage Pumping Station | INUSE
15148 | ACTON TURVILLE | BADMINTON STATION | N | Sewage Pumping Station | INUSE
15149 | HAWKESBURY UPTON | BRITAIN BOTTOM | N | Sewage Pumping Station | INUSE
15150 | OLDBURY | THE NAITE | N | Sewage Pumping Station | INUSE
15151 | AUST | M48 SERVICES | N | Sewage Pumping Station | INUSE
15152 | PATCHWAY | BROOKFIELD ROAD | N | Sewage Pumping Station | INUSE
15153 | PATCHWAY | BRIGHTON ROAD | N | Sewage Pumping Station | INUSE
15154 | WESTERLEIGH | KIDNEY HILL | N | Sewage Pumping Station | INUSE
15155 | WESTERLEIGH | HENFIELD | N | Sewage Pumping Station | INUSE
15156 | TORMARTON | MARSHFIELD ROAD | N | Sewage Pumping Station | INUSE
15157 | WINTERBOURNE | HICKS COMMON ROAD | N | Sewage Pumping Station | INUSE
15158 | OLVESTON | THE COMMON | N | Sewage Pumping Station | INUSE
15159 | PILNING | NEW PASSAGE | N | Sewage Pumping Station | INUSE
15160 | PILNING | FIRE STATION | N | Sewage Pumping Station | INUSE
15161 | PILNING | CHESSEL AVENUE | N | Sewage Pumping Station | INUSE
15162 | ALVESTON | ALVESTON DOWN | N | Sewage Pumping Station | INUSE
15163 | CROMHALL | TOWNWELL | N | Sewage Pumping Station | INUSE
15164 | TYTHERINGTON | STIDCOTT | N | Sewage Pumping Station | INUSE
15165 | EASTER COMPTON | PILNING ROAD | N | Sewage Pumping Station | INUSE
15166 | RANGEWORTHY | BERROWS MEAD | N | Sewage Pumping Station | INUSE
15167 | CROMHALL | JUBILEE LANE | N | Sewage Pumping Station | INUSE
15168 | GREAT BADMINTON | BADMINTON HOUSE | N | Sewage Pumping Station | INUSE
15169 | HILLESLEY | KILCOTT LANE | N | Sewage Pumping Station | INUSE
15170 | HORTON | KINGS LANE | N | Sewage Pumping Station | INUSE
15171 | HALLEN | CARAVAN SITE | N | Sewage Pumping Station | INUSE
15172 | BRISTOL | NEWLANDS | N | Sewage Pumping Station | INUSE
15173 | ALMONDSBURY | HORTHAM LANE | N | Sewage Pumping Station | INUSE
15174 | HAWKESBURY UPTON | POOL FARM | N | Sewage Pumping Station | INUSE
15175 | FRAMPTON COTTERELL | MEDWAY DRIVE | N | Sewage Pumping Station | INUSE
15176 | OLD SODBURY | CROSS HANDS | N | Sewage Pumping Station | INUSE
15177 | WICK | ROCK ROAD | N | Sewage Pumping Station | INUSE
15178 | PILNING | PILNING CHURCH THE GREEN | N | Sewage Pumping Station | INUSE
15179 | PILNING | SHAYMOOR LANE | N | Sewage Pumping Station | INUSE
15180 | PILNING | REDWICK ROAD | N | Sewage Pumping Station | INUSE
15181 | PILNING | PILNING SCHOOL | N | Sewage Pumping Station | INUSE
15182 | THORNBURY | ORCHARD AVENUE | N | Sewage Pumping Station | INUSE
15183 | BAGSTONE | . | N | Sewage Pumping Station | INUSE
15184 | ACTON TURVILLE | SCHOOL LUCKINGTON ROAD | N | Sewage Pumping Station | INUSE
15185 | LITTLE BADMINTON | WELL LANE | N | Sewage Pumping Station | INUSE
15186 | IRON ACTON | LATTERIDGE ROAD | N | Sewage Pumping Station | INUSE
15187 | OLD DOWN | FOX INN | N | Sewage Pumping Station | INUSE
15188 | YATE | NORTH ROAD | N | Sewage Pumping Station | INUSE
15189 | AUST | VILLAGE | N | Sewage Pumping Station | INUSE
15190 | MILBORNE ST ANDREW | MANOR FARM | S | Sewage Pumping Station | INUSE
15191 | BLANDFORD | BLANDFORD HEIGHTS | S | Sewage Pumping Station | INUSE
15192 | MARNHULL | CHURCH HILL SINGLE PROPERTY | S | Private Sewage Pumping Station | INUSE
15193 | CHILD OKEFORD | GOLD HILL | S | Sewage Pumping Station | INUSE
15194 | MARNHULL | MUSBURY | S | Sewage Pumping Station | INUSE
15195 | BRYANSTON | FORUM VIEW | S | Sewage Pumping Station | INUSE
15196 | STURMINSTER NEWTON | THE BRIDGE | S | Sewage Pumping Station | INUSE
15197 | BLANDFORD ST MARY | BREWERY NO 2 | S | Sewage Pumping Station | INUSE
15198 | GILLINGHAM | CLARENDON CLOSE | S | Sewage Pumping Station | INUSE
15200 | MARNHULL | SODOM LANE | S | Sewage Pumping Station | INUSE
15201 | DURWESTON | WATER LANE | S | Sewage Pumping Station | INUSE
15202 | SHROTON | THE GLEBE | S | Sewage Pumping Station | INUSE
15203 | SHILLINGSTONE | HAYWARDS BRIDGE | S | Sewage Pumping Station | INUSE
15204 | IWERNE MINSTER | OAKWOOD DRIVE | S | Sewage Pumping Station | INUSE
15205 | BLANDFORD ST MARY | BOURNEMOUTH ROAD | S | Sewage Pumping Station | INUSE
15206 | BLANDFORD | LANGTON ROAD (BLANDFORD NO 1) | S | Sewage Pumping Station | INUSE
15207 | SHAFTESBURY | LONG CROSS | S | Sewage Pumping Station | INUSE
15208 | SHILLINGSTONE | HONEYSUCKLE GARDENS | S | Sewage Pumping Station | INUSE
15209 | SPETISBURY | CRAWFORD BRIDGE | S | Sewage Pumping Station | INUSE
15210 | HALE | . | S | Sewage Pumping Station | INUSE
15211 | BURLEY | FOREST ROAD | S | Sewage Pumping Station | INUSE
15212 | RINGWOOD | FAIRLIE PARK | S | Sewage Pumping Station | INUSE
15213 | RINGWOOD | PARKSIDE INDUSTRIAL ESTATE | S | Sewage Pumping Station | INUSE
15214 | THORNEY HILL | WHITELANDS | S | Sewage Pumping Station | INUSE
15215 | RINGWOOD | SEYMOUR ROAD | S | Sewage Pumping Station | INUSE
15216 | SOPLEY | RINGWOOD ROAD | S | Sewage Pumping Station | INUSE
15217 | BRANSGORE | NEACROFT NO 2 | S | Sewage Pumping Station | INUSE
15218 | BURLEY | MILL LAWN | S | Sewage Pumping Station | INUSE
15219 | FORDINGBRIDGE | GREEN LANE | S | Sewage Pumping Station | INUSE
15220 | BRANSGORE | DIAL CLOSE | S | Sewage Pumping Station | INUSE
15221 | BRANSGORE | NEACROFT NO 3 | S | Sewage Pumping Station | INUSE
15222 | BRANSGORE | BURLEY ROAD (THE DELL) | S | Sewage Pumping Station | INUSE
15223 | BURLEY | MOORHILL | S | Sewage Pumping Station | INUSE
15225 | FORDINGBRIDGE | HORSEPORT | S | Sewage Pumping Station | INUSE
15226 | THORNEY HILL | VALLEY LANE | S | Sewage Pumping Station | INUSE
15227 | RINGWOOD | POPLAR WAY | S | Sewage Pumping Station | INUSE
15228 | POOLE | ROCKLEY ROAD | S | Sewage Pumping Station | INUSE
15229 | POOLE | WHITECLIFF RECREATION GROUND | S | Sewage Pumping Station | INUSE
15230 | POOLE | KENNART ROAD | S | Sewage Pumping Station | INUSE
15231 | POOLE | SANDBANKS PAVILION | S | Sewage Pumping Station | INUSE
15232 | POOLE | SALTERNS WAY | S | Sewage Pumping Station | INUSE
15233 | POOLE | WILDERTON ROAD | S | Sewage Pumping Station | INUSE
15234 | POOLE | TURLIN MOOR SW | S | Sewage Pumping Station | INUSE
15235 | POOLE | SHORE ROAD | S | Sewage Pumping Station | INUSE
15236 | POOLE | CANFORD HEATH ROAD | S | Sewage Pumping Station | INUSE
15237 | POOLE | MAGNA ROAD | S | Sewage Pumping Station | INUSE
15238 | POOLE | HATCH POND ROAD | S | Sewage Pumping Station | INUSE
15239 | POOLE | POOLE PARK | S | Sewage Pumping Station | INUSE
15240 | POOLE | BRANKSOME CHINE | S | Sewage Pumping Station | INUSE
15241 | POOLE | HARKWOOD DRIVE | S | Sewage Pumping Station | INUSE
15242 | POOLE | MERLEYS WAY MERLEY | S | Sewage Pumping Station | INUSE
15243 | BRIDGWATER | EAST QUAY | W | Sewage Pumping Station | INUSE
15244 | POOLE | ELGIN ROAD | S | Sewage Pumping Station | INUSE
15245 | POOLE | BLUE LAGOON SANDBANKS ROAD | S | Sewage Pumping Station | INUSE
15246 | CANFORD MAGNA | CANFORD MAIN | S | Sewage Pumping Station | INUSE
15247 | POOLE | RECTORY / ASHMORE AVENUE | S | Sewage Pumping Station | INUSE
15248 | POOLE | QUAY SURFACE WATER | S | Sewage Pumping Station | INUSE
15249 | POOLE | RNLI SURFACE WATER SLIPWAY | S | Sewage Pumping Station | INUSE
15250 | POOLE | BLANDFORD ROAD MINI ROUNDABOUT | S | Sewage Pumping Station | INUSE
15251 | POOLE | CABOT LANE | S | Sewage Pumping Station | INUSE
15252 | POOLE | EGMONT ROAD | S | Sewage Pumping Station | INUSE
15253 | POOLE | FAIRVIEW ROAD | S | Sewage Pumping Station | INUSE
15254 | POOLE | ASHWOOD DRIVE | S | Sewage Pumping Station | INUSE
15255 | POOLE | EAST QUAY SURFACE WATER SLIPWAY | S | Sewage Pumping Station | INUSE
15256 | POOLE | LAURAL DRIVE | S | Sewage Pumping Station | INUSE
15257 | POOLE | POOLE BRIDGE POOLE QUAY | S | Sewage Pumping Station | INUSE
15258 | POOLE | WILLIS WAY | S | Sewage Pumping Station | INUSE
15259 | POOLE | COY POND | S | Sewage Pumping Station | INUSE
15260 | POOLE | ESPLANADE STERTE | S | Sewage Pumping Station | INUSE
15261 | POOLE | TAVERNER CLOSE | S | Sewage Pumping Station | INUSE
15262 | POOLE | PARK LAKE ROAD | S | Sewage Pumping Station | INUSE
15263 | POOLE | FLEETSBRIDGE SURFACE WATER | S | Sewage Pumping Station | INUSE
15264 | POOLE | ORCHARD AVENUE | S | Sewage Pumping Station | INUSE
15265 | POOLE | CANFORD SCHOOL | S | Sewage Pumping Station | INUSE
15266 | POOLE | MERLEY LANE MERLEY | S | Sewage Pumping Station | INUSE
15267 | POOLE | QUEEN ANNE DRIVE | S | Sewage Pumping Station | INUSE
15268 | POOLE | GREENSLEEVES AVENUE | S | Sewage Pumping Station | INUSE
15269 | POOLE | BLANDFORD ROAD | S | Sewage Pumping Station | INUSE
15270 | POOLE | CREEKMOOR LANE | S | Sewage Pumping Station | INUSE
15271 | POOLE | KING JOHN AVENUE | S | Sewage Pumping Station | INUSE
15272 | POOLE | SEACOMBE ROAD | S | Sewage Pumping Station | INUSE
15273 | POOLE | TURLIN MAIN BLANDFORD ROAD TURLIN MOOR | S | Sewage Pumping Station | INUSE
15274 | POOLE | WOODLANDS AVENUE | S | Sewage Pumping Station | INUSE
15275 | POOLE | HEWITT ROAD | S | Sewage Pumping Station | INUSE
15276 | POOLE | RECREATION ROAD | S | Sewage Pumping Station | INUSE
15277 | POOLE | WOOD LANE | S | Sewage Pumping Station | INUSE
15278 | LONG SUTTON | BENNETTS ORCHARD | W | Sewage Pumping Station | INUSE
15279 | HORSINGTON | HORSINGTON SCHOOL | W | Sewage Pumping Station | INUSE
15280 | MARTOCK | COAT ROAD | W | Sewage Pumping Station | INUSE
15281 | HOLTON | . | W | Sewage Pumping Station | INUSE
15282 | BRADFORD ABBAS | MILL LANE | S | Sewage Pumping Station | INUSE
15283 | WINCANTON | BAYFORD | W | Sewage Pumping Station | INUSE
15284 | HUISH EPISCOPI | WAGG DROVE | W | Sewage Pumping Station | INUSE
15285 | HORSINGTON | HORSINGTON MAIN | W | Sewage Pumping Station | INUSE
15286 | MILBORNE PORT | HENNING WAY | W | Sewage Pumping Station | INUSE
15287 | YEOVIL | COMBE STREET LANE | W | Sewage Pumping Station | INUSE
15288 | EAST COKER | MARSH | W | Sewage Pumping Station | INUSE
15289 | YEOVIL | MARSH LANE | W | Sewage Pumping Station | INUSE
15290 | HENSTRIDGE | MARSH LANE (HENSTRIDGE NO 2) | W | Sewage Pumping Station | INUSE
15291 | ODCOMBE | NO 2 | W | Sewage Pumping Station | INUSE
15292 | HENSTRIDGE | PARK LANE (RIVERSIDE GARDENS) HENSTRIDGE NO 1 | W | Sewage Pumping Station | INUSE
15293 | STOFORD | NEWTON ROAD GARAGE | W | Sewage Pumping Station | INUSE
15294 | MARTOCK | MATFURLONG CLOSE OFF WATER STREET | W | Sewage Pumping Station | INUSE
15295 | LIMINGTON | GLANFIELD TERRACE | W | Sewage Pumping Station | INUSE
15297 | DRAYTON | DUCKS LANE | W | Sewage Pumping Station | INUSE
15298 | LIMINGTON | MAIN | W | Sewage Pumping Station | INUSE
15299 | KINGSDON | . | W | Sewage Pumping Station | INUSE
15300 | MERRIOTT | BOOZER PITT | W | Sewage Pumping Station | INUSE
15301 | ODCOMBE | NO 1 | W | Sewage Pumping Station | INUSE
15302 | YEOVIL | ST JOHNS ROAD | W | Sewage Pumping Station | INUSE
15303 | HUISH EPISCOPI | PEONY VALLEY | W | Sewage Pumping Station | INUSE
15304 | WEST CHINNOCK | GARAGE | W | Sewage Pumping Station | INUSE
15305 | YEOVIL | PRIMROSE LANE | W | Sewage Pumping Station | INUSE
15306 | LOWER SOMERTON | . | W | Sewage Pumping Station | INUSE
15307 | SOUTH PETHERTON | WEST STREET | W | Sewage Pumping Station | INUSE
15308 | WEST CHINNOCK | SNAILS HILL | W | Sewage Pumping Station | INUSE
15309 | CHARLTON MACKERELL | ROOKERY FARM | W | Sewage Pumping Station | INUSE
15310 | ALLER | . | W | Sewage Pumping Station | INUSE
15311 | YEOVIL | MUDFORD | W | Sewage Pumping Station | INUSE
15312 | ODCOMBE | NO 3 | W | Sewage Pumping Station | INUSE
15313 | HUISH EPISCOPI | PIBSBURY | W | Sewage Pumping Station | INUSE
15314 | UPTON | NR LANGPORT | W | Sewage Pumping Station | INUSE
15315 | HUISH EPISCOPI | WAGG BRIDGE | W | Sewage Pumping Station | INUSE
15316 | BARTON ST DAVID | TOOTAL BRIDGE | W | Sewage Pumping Station | INUSE
15317 | NORTON SUB HAMDON | . | W | Sewage Pumping Station | INUSE
15318 | STOFORD | HILLSIDE MAIN | W | Sewage Pumping Station | INUSE
15319 | CHARD | EDWARDS | W | Sewage Pumping Station | INUSE
15320 | LONG SUTTON | KNOLE | W | Sewage Pumping Station | INUSE
15321 | HUISH EPISCOPI | COURTFIELD NO 2 | W | Sewage Pumping Station | INUSE
15322 | PITNEY | . | W | Sewage Pumping Station | INUSE
15323 | LIMINGTON | FAIRVIEW TERRACE | W | Sewage Pumping Station | INUSE
15324 | CHARLTON HORETHORNE | KENNELS | W | Sewage Pumping Station | INUSE
15325 | KEINTON MANDEVILLE | . | W | Sewage Pumping Station | INUSE
15326 | ILCHESTER | THE MEAD PILL BRIDGE LANE | W | Sewage Pumping Station | INUSE
15327 | ILMINSTER | LORD NELSON | W | Sewage Pumping Station | INUSE
15328 | CREWKERNE | WADHAM PARK | W | Sewage Pumping Station | INUSE
15330 | CHARD | TOUCHES MEADOW | W | Sewage Pumping Station | INUSE
15331 | SHEPTON BEAUCHAMP | . | W | Sewage Pumping Station | INUSE
15332 | CREWKERNE | HARDY COURT | W | Sewage Pumping Station | INUSE
15333 | PENSELWOOD | PENN MILL | S | Sewage Pumping Station | INUSE
15334 | CHARLTON ADAM | . | W | Sewage Pumping Station | INUSE
15335 | SOUTH PETHERTON | PITWAY | W | Sewage Pumping Station | INUSE
15336 | CHILTON CANTELO | LOWER CHILTON CANTELO | W | Sewage Pumping Station | INUSE
15337 | PENSELWOOD | GREAT HILL | S | Sewage Pumping Station | INUSE
15338 | ASH | ASH SCHOOL | W | Sewage Pumping Station | INUSE
15339 | TEMPLECOMBE | SLADES HILL | W | Sewage Pumping Station | INUSE
15340 | BRIDGWATER | BOWER MANOR 7 WILKINS ROAD | W | Sewage Pumping Station | INUSE
15341 | BURNHAM-ON-SEA | LYNTON ROAD | W | Sewage Pumping Station | INUSE
15342 | BRENT KNOLL | FORGE HOUSE BRENT STREET | W | Sewage Pumping Station | INUSE
15343 | PURITON | DOWNEND | W | Sewage Pumping Station | INUSE
15344 | HIGHBRIDGE | COMMERCE WAY | W | Sewage Pumping Station | INUSE
15345 | MARK | QUEENSWAY | W | Sewage Pumping Station | INUSE
15347 | WOOLAVINGTON | CAUSEWAY | W | Sewage Pumping Station | INUSE
15348 | BURNHAM-ON-SEA | BRENT ROAD | W | Sewage Pumping Station | INUSE
15349 | BURNHAM-ON-SEA | BRAITHWAITE PLACE OFF BERROW ROAD | W | Sewage Pumping Station | INUSE
15350 | HIGHBRIDGE | OLIVE TERRACE | W | Sewage Pumping Station | INUSE
15351 | BURNHAM-ON-SEA | BROADHURST GARDENS | W | Sewage Pumping Station | INUSE
15352 | EAST BRENT | ORCHARD CLOSE | W | Sewage Pumping Station | INUSE
15353 | BURNHAM-ON-SEA | QUANTOCK CLOSE | W | Sewage Pumping Station | INUSE
15354 | BURNHAM-ON-SEA | ST PETERS ROAD | W | Sewage Pumping Station | INUSE
15355 | WEST HUNTSPILL | MAIN ROAD | W | Sewage Pumping Station | INUSE
15356 | ROOKSBRIDGE | MENDIP ROAD (FACTORY ROAD) EDINGWORTH | W | Sewage Pumping Station | INUSE
15357 | WEST HUNTSPILL | GROVE ROAD | W | Sewage Pumping Station | INUSE
15358 | BERROW | WHITEGATES YEW TREE HURN LANE | W | Sewage Pumping Station | INUSE
15359 | LYMPSHAM | CHURCH ROAD | W | Sewage Pumping Station | INUSE
15360 | WEDMORE | SAND | W | Sewage Pumping Station | INUSE
15361 | WEST HUNTSPILL | CROSSWAYS WITHY ROAD | W | Sewage Pumping Station | INUSE
15362 | BRIDGWATER | SILVER SPRINGS FOLLETTS FARM | W | Sewage Pumping Station | INUSE
15363 | CHICKERELL | CHICKERELL CAMP | S | Private Sewage Pumping Station | INUSE
15365 | AXBRIDGE | WALNUT FARM | W | Sewage Pumping Station | INUSE
15366 | BERROW | BARTON ROAD IN BETWEEN 60 BARTON ROAD & BONER COTTAGE | W | Sewage Pumping Station | INUSE
15367 | CANNINGTON | MILL CLOSE | W | Sewage Pumping Station | INUSE
15369 | BURNHAM-ON-SEA | PILLSMOUTH MARINE DRIVE | W | Sewage Pumping Station | INUSE
15370 | WESTONZOYLAND | LAKEWALL ROAD | W | Sewage Pumping Station | INUSE
15371 | CROSS | CROSS EAST | W | Sewage Pumping Station | INUSE
15372 | BRIDGWATER | CHURCH PATH | W | Sewage Pumping Station | INUSE
15373 | CHEDZOY | MANOR DRIVE | W | Sewage Pumping Station | INUSE
15374 | BRIDGWATER | LATE HEAL | W | Sewage Pumping Station | INUSE
15375 | CHILTON POLDEN | BROADWAY | W | Sewage Pumping Station | INUSE
15376 | CROSS | CROSS WEST OLD COACH ROAD | W | Sewage Pumping Station | INUSE
15377 | EAST BRENT | CHESTNUT FARM | W | Sewage Pumping Station | INUSE
15378 | PAWLETT | VICARAGE LANE | W | Sewage Pumping Station | INUSE
15379 | HIGHBRIDGE | PADDOCK DRIVE | W | Sewage Pumping Station | INUSE
15380 | BRIDGWATER | CROWS LANE SURFACE WATER | W | Sewage Pumping Station | INUSE
15381 | WEMBDON | COMMON | W | Sewage Pumping Station | INUSE
15382 | EAST HUNTSPILL | HACKNESS ROAD | W | Sewage Pumping Station | INUSE
15383 | POOLE | EAST QUAY PERRY GARDENS | S | Sewage Pumping Station | INUSE
15384 | BRIDGWATER | BRISTOL ROAD NO 1 BCL | W | Sewage Pumping Station | INUSE
15385 | BREAN | MERRY BEE SOUTH ROAD | W | Sewage Pumping Station | INUSE
15386 | BRIDGWATER | WYLDS ROAD SURFACE WATER | W | Sewage Pumping Station | INUSE
15387 | CHEDZOY | FISHERS FARM | W | Sewage Pumping Station | INUSE
15388 | OTHERY | RYE LANE/ SUMMERHEDGE ROAD | W | Sewage Pumping Station | INUSE
15389 | PAWLETT | MAIN ROAD | W | Sewage Pumping Station | INUSE
15390 | BURNHAM-ON-SEA | WESTFIELD DRIVE | W | Sewage Pumping Station | INUSE
15391 | WESTONZOYLAND | HAMROD LANE | W | Sewage Pumping Station | INUSE
15392 | CHEDZOY | WARD LANE | W | Sewage Pumping Station | INUSE
15393 | BRIDGWATER | TAUNTON ROAD | W | Sewage Pumping Station | INUSE
15394 | SUTTON MALLET | . | W | Sewage Pumping Station | INUSE
15395 | BASON BRIDGE | CHURCH ROAD | W | Sewage Pumping Station | INUSE
15396 | WOOLAVINGTON | MEADOW FARM | W | Sewage Pumping Station | INUSE
15397 | STAWELL | FORD LANE | W | Sewage Pumping Station | INUSE
15398 | BRIDGWATER | FRIARN LAWN | W | Sewage Pumping Station | INUSE
15399 | PURITON | RYE | W | Sewage Pumping Station | INUSE
15400 | BRIDGWATER | WEST QUAY DRAWBRIDGE | W | Sewage Pumping Station | INUSE
15401 | MUDGLEY | MUDGLEY CROSS | W | Sewage Pumping Station | INUSE
15402 | MIDDLEZOY | NETHERMOOR ROAD | W | Sewage Pumping Station | INUSE
15403 | BRIDGWATER | WYLDS ROAD FOUL | W | Sewage Pumping Station | INUSE
15405 | BRIDGWATER | BOWER MANOR 3A | W | Sewage Pumping Station | INUSE
15406 | DURLEIGH | QUEENSWOOD LANE BROADLANDS | W | Sewage Pumping Station | INUSE
15407 | DUNWEAR | RIVERSIDE | W | Sewage Pumping Station | INUSE
15408 | BRIDGWATER | EASTERN AVENUE | W | Sewage Pumping Station | INUSE
15409 | BRIDGWATER | BOWER LANE BOWER MANOR | W | Sewage Pumping Station | INUSE
15410 | HORSEY | CHEDZOY LANE BRIDGWATER | W | Sewage Pumping Station | INUSE
15411 | BURNHAM-ON-SEA | RECTORY DRIVE | W | Sewage Pumping Station | INUSE
15412 | EAST HUNTSPILL | WITHY ROAD | W | Sewage Pumping Station | INUSE
15413 | DURLEIGH | ENMORE ROAD RESERVOIR | W | Sewage Pumping Station | INUSE
15414 | BRISTOL | CENTRAL TRADING ESTATE BATH ROAD | N | Sewage Pumping Station | INUSE
15415 | BRIDGWATER | COLLEY LANE | W | Sewage Pumping Station | INUSE
15416 | BERROW | MEADE FARM COAST ROAD | W | Sewage Pumping Station | INUSE
15417 | BURNHAM-ON-SEA | ASHCOTT DRIVE | W | Sewage Pumping Station | INUSE
15418 | PAWLETT | CHAPEL ROAD | W | Sewage Pumping Station | INUSE
15419 | BREAN | SUNNYSIDE WARREN FARM | W | Sewage Pumping Station | INUSE
15420 | NORTH NIBLEY | MILL END | N | Sewage Pumping Station | INUSE
15421 | STONE | OLD MILL | N | Sewage Pumping Station | INUSE
15422 | SHARPNESS | OLD MINSTER ROAD | N | Sewage Pumping Station | INUSE
15423 | PURTON | WATERWORKS | N | Sewage Pumping Station | INUSE
15424 | BERKELEY | MOBLEY | N | Sewage Pumping Station | INUSE
15425 | SHARPNESS | DOCKS ROAD EAST | N | Sewage Pumping Station | INUSE
15426 | NEWPORT | SOUTH | N | Sewage Pumping Station | INUSE
15427 | PURTON | No 5 BERKELY ARMS | N | Sewage Pumping Station | INUSE
15428 | SHARPNESS | SANIGAR LANE | N | Sewage Pumping Station | INUSE
15429 | HALMORE | . | N | Sewage Pumping Station | INUSE
15430 | PURTON | HINTON ROAD | N | Sewage Pumping Station | INUSE
15431 | STONE | COURTMEAD ESTATE | N | Sewage Pumping Station | INUSE
15432 | WANSWELL | FARM LANE | N | Sewage Pumping Station | INUSE
15433 | BERKELEY | BERKELEY HEATH | N | Sewage Pumping Station | INUSE
15434 | NEWPORT | NORTH | N | Sewage Pumping Station | INUSE
15435 | BATHPOOL | HYDE LANE | W | Sewage Pumping Station | INUSE
15436 | RUISHTON | BARTON LANE | W | Sewage Pumping Station | INUSE
15439 | HENLADE | . | W | Sewage Pumping Station | INUSE
15440 | NORTH CURRY | MAIN | W | Sewage Pumping Station | INUSE
15441 | CHEDDON FITZPAINE | CHEDDON FARM | W | Sewage Pumping Station | INUSE
15443 | TAUNTON | NEW BARN QUEENSWAY | W | Sewage Pumping Station | INUSE
15444 | GOOSENFORD | . | W | Sewage Pumping Station | INUSE
15445 | NYNEHEAD | . | W | Sewage Pumping Station | INUSE
15446 | HILLCOMMON | HILL COMMON | W | Sewage Pumping Station | INUSE
15447 | TAUNTON | MOUNTWAY BISHOPS HULL | W | Sewage Pumping Station | INUSE
15448 | TAUNTON | LONGACRE CLOSE | W | Sewage Pumping Station | INUSE
15449 | MEARE GREEN | WRANTAGE | W | Sewage Pumping Station | INUSE
15450 | NORTON FITZWARREN | LANGFORD LANE | W | Sewage Pumping Station | INUSE
15451 | BRADFORD ON TONE | THREE BRIDGES | W | Sewage Pumping Station | INUSE
15452 | TAUNTON | TANGIER | W | Sewage Pumping Station | INUSE
15453 | BURROWBRIDGE | SCHOOL LANE | W | Sewage Pumping Station | INUSE
15454 | CREECH ST MICHAEL | NORTH END | W | Sewage Pumping Station | INUSE
15455 | WELLINGTON | WHARF COTTAGES | W | Sewage Pumping Station | INUSE
15457 | WELLINGTON | WESTFORD | W | Sewage Pumping Station | INUSE
15458 | STOKE ST GREGORY | CURLOAD | W | Sewage Pumping Station | INUSE
15459 | RUMWELL | . | W | Sewage Pumping Station | INUSE
15460 | MEARE GREEN | STOKE ST GREGORY | W | Sewage Pumping Station | INUSE
15461 | STOKE ST GREGORY | WOODHILL | W | Sewage Pumping Station | INUSE
15462 | BISHOPS LYDEARD | GREENWAY | W | Sewage Pumping Station | INUSE
15463 | BRADFORD ON TONE | TONE GREEN | W | Sewage Pumping Station | INUSE
15464 | TAUNTON | VENTURE WAY PRIORSWOOD | W | Sewage Pumping Station | INUSE
15465 | NORTH CURRY | STOKE ROAD | W | Sewage Pumping Station | INUSE
15466 | OAKE | . | W | Sewage Pumping Station | INUSE
15467 | NAILSBOURNE | . | W | Sewage Pumping Station | INUSE
15468 | BRADFORD ON TONE | HOCKHOLLER A38 | W | Sewage Pumping Station | INUSE
15469 | LEIGH | FRAMPTON FARM | S | Sewage Pumping Station | INUSE
15470 | CERNE ABBAS | BARN | S | Sewage Pumping Station | INUSE
15471 | DORCHESTER | MILL STREET DURNOVER COURT | S | Sewage Pumping Station | INUSE
15472 | SHERBORNE | LENTHAY ROAD | S | Sewage Pumping Station | INUSE
15473 | STRATTON | MILL LANE | S | Sewage Pumping Station | INUSE
15474 | CROSSWAYS | COMBE WAY | S | Sewage Pumping Station | INUSE
15475 | THORNFORD | BLACKBIRDS | S | Sewage Pumping Station | INUSE
15476 | CHIDEOCK | GILES CLOSE | S | Sewage Pumping Station | INUSE
15478 | CHARMINSTER | COCKLANDS | S | Sewage Pumping Station | INUSE
15479 | DORCHESTER | CASTLE PARK | S | Sewage Pumping Station | INUSE
15480 | MOSTERTON | HIGH STREET | S | Private Sewage Pumping Station | INUSE
15481 | BRADPOLE | LEE LANE | S | Sewage Pumping Station | INUSE
15482 | SWYRE | GORSELANDS CARAVAN PARK | S | Sewage Pumping Station | INUSE
15483 | BRADPOLE | FISHWEIR FLOOD SURFACE WATER | S | Sewage Pumping Station | INUSE
15484 | CHARMOUTH | LOWER SEA LANE | S | Sewage Pumping Station | INUSE
15485 | CROSSWAYS | EGDON GLEN | S | Sewage Pumping Station | INUSE
15486 | WEST BEXINGTON | . | S | Sewage Pumping Station | INUSE
15487 | BRIDPORT | EAST ROAD | S | Sewage Pumping Station | INUSE
15489 | LEIGH | YETMINSTER ROAD | S | Sewage Pumping Station | INUSE
15490 | CROSSWAYS | REDBRIDGE | S | Sewage Pumping Station | INUSE
15491 | SYMONDSBURY | QUARR LANE | S | Sewage Pumping Station | INUSE
15492 | SYMONDSBURY | MILES CROSS | S | Sewage Pumping Station | INUSE
15493 | FRAMPTON | MUCKLEFORD | S | Sewage Pumping Station | INUSE
15494 | ABBOTSBURY | CHURCH STREET | S | Sewage Pumping Station | INUSE
15495 | NETHERBURY | BEAMINSTER | S | Sewage Pumping Station | INUSE
15496 | LEIGH | BRIDGE FARM | S | Sewage Pumping Station | INUSE
15497 | MARTINSTOWN | B3159 | S | Sewage Pumping Station | INUSE
15498 | CORSCOMBE | HIGH STREET | S | Sewage Pumping Station | INUSE
15499 | WEST KNIGHTON | KNIGHTON LANE | S | Sewage Pumping Station | INUSE
15500 | BRADPOLE | FISHWEIR FOUL | S | Sewage Pumping Station | INUSE
15501 | FRAMPTON | SOUTHOVER | S | Sewage Pumping Station | INUSE
15502 | BRADFORD ABBAS | COMPTON ROAD | S | Sewage Pumping Station | INUSE
15503 | CHICKERELL | MONTEVIDEO | S | Sewage Pumping Station | INUSE
15504 | DORCHESTER | MELLSTOCK AVENUE | S | Sewage Pumping Station | INUSE
15505 | SYMONDSBURY | WEST ROAD FOUNDRY | S | Sewage Pumping Station | INUSE
15506 | SALWAY ASH | VALE VIEW | S | Sewage Pumping Station | INUSE
15507 | BRIDPORT | WEST BAY SLUICES | S | Sewage Pumping Station | INUSE
15508 | WOOTTON COURTENAY | . | W | Sewage Pumping Station | INUSE
15510 | HOLFORD | . | W | Sewage Pumping Station | INUSE
15511 | MONKSILVER | B3188 | W | Sewage Pumping Station | INUSE
15513 | WILLITON | TOWER HILL | W | Sewage Pumping Station | INUSE
15514 | LAWFORD | STICKLE HILL | W | Sewage Pumping Station | INUSE
15515 | WATCHET | WERREN CLOSE | W | Sewage Pumping Station | INUSE
15516 | BILBROOK | . | W | Sewage Pumping Station | INUSE
15517 | STOGURSEY | KNIGHTON | W | Sewage Pumping Station | INUSE
15518 | KILVE | HILLTOP LANE | W | Sewage Pumping Station | INUSE
15519 | WATCHET | MARKET STREET (TUNNEL) | W | Sewage Pumping Station | INUSE
15520 | MINEHEAD | VULCAN ROAD | W | Sewage Pumping Station | INUSE
15521 | RADSTOCK | VICTORIA SQUARE | N | Sewage Pumping Station | INUSE
15522 | CLUTTON | KINGS OAK MEADOW | N | Sewage Pumping Station | INUSE
15523 | CAMERTON | SUNNYVALE | N | Sewage Pumping Station | INUSE
15524 | BATHEASTON | ELMHURST | N | Sewage Pumping Station | INUSE
15525 | BATHAMPTON | MILL LANE (BEAFEATER) | N | Sewage Pumping Station | INUSE
15526 | HINTON CHARTERHOUSE | OLD QUARRY MIDFORD ROAD | N | Sewage Pumping Station | INUSE
15527 | DUNKERTON | BROOKLANDS | N | Sewage Pumping Station | INUSE
15529 | TIMSBURY | SOMERSET FOLLY | N | Sewage Pumping Station | INUSE
15530 | HIGH LITTLETON | . | N | Sewage Pumping Station | INUSE
15531 | RADSTOCK | CURTSONS | N | Sewage Pumping Station | INUSE
15532 | TIMSBURY | LIPPIATT LANE | N | Sewage Pumping Station | INUSE
15533 | MONKTON COMBE | MILL LANE | N | Sewage Pumping Station | INUSE
15534 | TIMSBURY | THE HOOK | N | Sewage Pumping Station | INUSE
15535 | PEASEDOWN ST JOHN | NEW BUILDINGS / WHITEBROOK LANE | N | Sewage Pumping Station | INUSE
15536 | WELLOW | MILL HILL | N | Sewage Pumping Station | INUSE
15537 | SHOSCOMBE | SINGLE HILL | N | Sewage Pumping Station | INUSE
15538 | KEYNSHAM | ABBEY PARK | N | Sewage Pumping Station | INUSE
15540 | FRESHFORD | STAPLES HILL | N | Sewage Pumping Station | INUSE
15541 | KEYNSHAM | THE HAMS | N | Sewage Pumping Station | INUSE
15542 | KEYNSHAM | KEYNSHAM HIGH LEVEL | N | Sewage Pumping Station | INUSE
15543 | KEYNSHAM | BATH HILL CHEW PARK | N | Sewage Pumping Station | INUSE
15544 | TEMPLE CLOUD | TEMPLE BRIDGE | N | Sewage Pumping Station | INUSE
15545 | FARRINGTON GURNEY | HILL VIEW | N | Sewage Pumping Station | INUSE
15547 | SALTFORD | THE SHALLOWS | N | Sewage Pumping Station | INUSE
15548 | KEYNSHAM | KEYNSHAM LOW LEVEL | N | Sewage Pumping Station | INUSE
15549 | SALTFORD | CHELWOOD ROAD | N | Sewage Pumping Station | INUSE
15550 | WEYMOUTH | MARKHAM HOUSE WYKE ROAD | S | Sewage Pumping Station | INUSE
15551 | WEYMOUTH | PRESTON FISHERBRIDGE ESTATE | S | Sewage Pumping Station | INUSE
15552 | WEYMOUTH | KNIGHTSDALE NEWSTEAD ROAD | S | Sewage Pumping Station | INUSE
15553 | PORTLAND | VICTORIA SQUARE | S | Sewage Pumping Station | INUSE
15554 | WEYMOUTH | LODMOOR WEYMOUTH BAY AVENUE | S | Sewage Pumping Station | INUSE
15555 | WYKE REGIS | HILLCREST ROAD | S | Sewage Pumping Station | INUSE
15556 | WEYMOUTH | RADIPOLE | S | Sewage Pumping Station | INUSE
15557 | WEYMOUTH | OVERCOMBE | S | Sewage Pumping Station | INUSE
15558 | WEYMOUTH | SWIMMING POOL KNIGHTSDALE ROAD | S | Sewage Pumping Station | INUSE
15559 | PORTLAND | PENNSYLVANIA ROAD | S | Sewage Pumping Station | INUSE
15561 | WEYMOUTH | FERRYBRIDGE PORTLAND ROAD | S | Sewage Pumping Station | INUSE
15562 | WEYMOUTH | BOWLEAZE COVE | S | Sewage Pumping Station | INUSE
15564 | KINGSTON SEYMOUR | NORTH | W | Sewage Pumping Station | INUSE
15565 | PORTISHEAD | BLACKBERRY LANE (VALLEY ROAD) | W | Sewage Pumping Station | INUSE
15566 | CLEVEDON | TEIGNMOUTH ROAD | W | Sewage Pumping Station | INUSE
15567 | BROCKLEY | CHELVEY GREEN | W | Sewage Pumping Station | INUSE
15568 | TICKENHAM | WEST | W | Sewage Pumping Station | INUSE
15569 | PORTBURY | DROVE | W | Sewage Pumping Station | INUSE
15570 | CLEVEDON | MIDDLE YEO | W | Sewage Pumping Station | INUSE
15572 | LOCKING | LOCKING VILLAGE | W | Sewage Pumping Station | INUSE
15573 | BLEADON | PURN | W | Sewage Pumping Station | INUSE
15574 | SANDFORD BATCH | . | W | Sewage Pumping Station | INUSE
15575 | PORTBURY | HUNDRED | W | Sewage Pumping Station | INUSE
15576 | CONGRESBURY | NORTH | W | Sewage Pumping Station | INUSE
15577 | SANDFORD | SANDMEAD LANE | W | Sewage Pumping Station | INUSE
15580 | LANGFORD | BLACKMOOR ROAD | W | Sewage Pumping Station | INUSE
15581 | BACKWELL | BACKWELL GREEN | W | Sewage Pumping Station | INUSE
15582 | BANWELL | RIVERSIDE | W | Sewage Pumping Station | INUSE
15583 | CLEVEDON | ST CHRISTOPHER COURT | W | Sewage Pumping Station | INUSE
15584 | KINGSTON SEYMOUR | RUSTIC FARM (KINGSTON SEYMOUR CENTRAL) | W | Sewage Pumping Station | INUSE
15585 | BLEADON | BLEADON BRIDGE | W | Sewage Pumping Station | INUSE
15586 | WORLE | MADAM RHYNE | W | Sewage Pumping Station | INUSE
15587 | SANDFORD | MEAD LANE | W | Sewage Pumping Station | INUSE
15588 | WORLE | NORTH (FW) | W | Sewage Pumping Station | INUSE
15589 | PORTISHEAD | POACHER HOTEL (ANCHOR HOTEL) | W | Sewage Pumping Station | INUSE
15590 | CLEVEDON | REGENTS PARK | W | Sewage Pumping Station | INUSE
15591 | PORTISHEAD | HARBOUR ROAD | W | Sewage Pumping Station | INUSE
15592 | PORTISHEAD | NORTH WESTON | W | Sewage Pumping Station | INUSE
15593 | TICKENHAM | EAST | W | Sewage Pumping Station | INUSE
15594 | CLEVEDON | MARSHALLS FIELD | W | Sewage Pumping Station | INUSE
15595 | WESTON-SUPER-MARE | ANCHOR HEAD | W | Sewage Pumping Station | INUSE
15597 | PORTISHEAD | GOLF COURSE | W | Sewage Pumping Station | INUSE
15598 | PORTISHEAD | OLD MILL LANE | W | Sewage Pumping Station | INUSE
15599 | WESTON-SUPER-MARE | CAPRI VILLAS | W | Sewage Pumping Station | INUSE
15600 | KINGSTON SEYMOUR | FAIRFIELD (KINGSTON SEYMOUR WEST) | W | Sewage Pumping Station | INUSE
15601 | KINGSTON SEYMOUR | POOL FARM | W | Sewage Pumping Station | INUSE
15602 | KEWSTOKE | CROOKS LANE | W | Sewage Pumping Station | INUSE
15603 | ST GEORGES | GOOSEY LANE | W | Sewage Pumping Station | INUSE
15605 | NAILSEA | BROCKLEY COURT | W | Sewage Pumping Station | INUSE
15606 | CLEVEDON | THE BEACH | W | Sewage Pumping Station | INUSE
15607 | KEWSTOKE | NORTON LANE | W | Sewage Pumping Station | INUSE
15608 | WORLE | SUMMER LANE | W | Sewage Pumping Station | INUSE
15609 | CLAPTON IN GORDANO | . | W | Sewage Pumping Station | INUSE
15610 | KENN | MOORSIDE | W | Sewage Pumping Station | INUSE
15611 | BACKWELL | BROOK FARM | W | Sewage Pumping Station | INUSE
15612 | BACKWELL | BACKWELL COMMON | W | Sewage Pumping Station | INUSE
15613 | WESTON-SUPER-MARE | HUTTON PARK CARAVAN SITE | W | Sewage Pumping Station | INUSE
15614 | PORTBURY | DOCK | W | Sewage Pumping Station | INUSE
15615 | HIGH LITTLETON | BEAUFORT PARK GORES YARD | N | Sewage Pumping Station | INUSE
15616 | BARRINGTON | WEST END VIEW | W | Sewage Pumping Station | INUSE
15618 | CHRISTCHURCH | CHRISTCHURCH AIRFIELD | S | Sewage Pumping Station | INUSE
15619 | BRINKWORTH | ST MICHEALS CLOSE | N | Sewage Pumping Station | INUSE
15620 | RINGWOOD | BROOK CLOSE | S | Sewage Pumping Station | INUSE
15621 | CLEVEDON | LADYE BAY | W | Sewage Pumping Station | INUSE
15622 | CLEVEDON | MARINE PARADE | W | Sewage Pumping Station | INUSE
15623 | LEIGH | DEWLANDS ORCHARD | S | Sewage Pumping Station | INUSE
15624 | TIMSBURY | CROWCOMBE LANE | N | Sewage Pumping Station | INUSE
15625 | WINCANTON | ELM DRIVE | W | Sewage Pumping Station | INUSE
15627 | ILTON | FROST LANE | W | Sewage Pumping Station | INUSE
15628 | DORCHESTER | HERRINGSTON ROAD | S | Sewage Pumping Station | INUSE
15629 | HAMBRIDGE | . | W | Sewage Pumping Station | INUSE
15630 | CHICKERELL | LOWER WAY | S | Sewage Pumping Station | INUSE
15632 | ASHLEY HEATH | MOORS VALLEY NO 2 | S | Private Sewage Pumping Station | INUSE
15635 | POOLE | COWSLIP ROAD PINE SPRINGS | S | Sewage Pumping Station | INUSE
15637 | STURMINSTER NEWTON | ROLLS MILL | S | S105A Sewage Pumping Station | INUSE
15638 | MANNINGFORD | NO 4 PS PEWSEY | N | Sewage Pumping Station | INUSE
15639 | COMPTON DUNDON | MOOR CLOSE | W | Sewage Pumping Station | INUSE
15640 | DORCHESTER | SOUTH STATION | S | Sewage Pumping Station | INUSE
15641 | SALWAY ASH | OLD STW | S | Sewage Pumping Station | INUSE
15642 | POOLE | STERTE F W | S | Sewage Pumping Station | INUSE
15643 | POOLE | STERTE STORM WATER LIFT STATION | S | Private Sewage Pumping Station | INUSE
15644 | SUTTON WALDRON | . | S | Sewage Pumping Station | INUSE
15645 | PILL | AVON ROAD | W | Sewage Pumping Station | INUSE
15646 | PITCOMBE | VALE ROAD | W | Sewage Pumping Station | INUSE
15647 | BRIDGWATER | POLLARD WAY | W | Sewage Pumping Station | INUSE
15648 | PORTLAND | PORTLAND BILL | S | Sewage Pumping Station | INUSE
15649 | WEST HUNTSPILL | ROSE FARM | W | Sewage Pumping Station | INUSE
15650 | BRIDGWATER | SHELTHORN GROVE | W | Sewage Pumping Station | INUSE
15651 | BRIDPORT | SOUTH BRIDGE TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
15652 | HALSTOCK | STREET FARM | S | Sewage Pumping Station | INUSE
15653 | CHRISTCHURCH | TWYNHAM SW DETENTION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
15654 | ILMINSTER | WESTPORT | W | Sewage Pumping Station | INUSE
15655 | DORCHESTER | WEYMOUTH AVENUE | S | Sewage Pumping Station | INUSE
15656 | ILMINSTER | WHARF LANE | W | Sewage Pumping Station | INUSE
15657 | WEST HUNTSPILL | WHITE COTTAGE | W | Sewage Pumping Station | INUSE
15658 | BRIDGWATER | WHITFIELD ROAD | W | Sewage Pumping Station | INUSE
15659 | BRIDGWATER | WILLS ROAD | W | Sewage Pumping Station | INUSE
15660 | WOODBOROUGH PS1 | . | N | Sewage Pumping Station | INUSE
15661 | WRINGTON | GARSTONS | W | Sewage Pumping Station | INUSE
15669 | MELKSHAM | WESTERN WAY | N | Sewage Pumping Station | INUSE
15671 | POOLE | CREEKMOOR PIT | S | Sewage Pumping Station | INUSE
15672 | WORLE | PARKWAY | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
15673 | PORTLAND | SOUTHWELL | S | Sewage Pumping Station | INUSE
15674 | EYPE | MOUNT LANE | S | Sewage Pumping Station | INUSE
15675 | BRIDPORT | WANDERWELL | S | Sewage Pumping Station | INUSE
15676 | SHAFTESBURY | TOLLGATE PARK | S | Sewage Pumping Station | INUSE
15678 | SHAFTESBURY | WINCOMBE PARK | S | Sewage Pumping Station | INUSE
15680 | PORTISHEAD | BLACK NORE (NAUTICAL SCHOOL) | W | Sewage Pumping Station | INUSE
15681 | WESTON-SUPER-MARE | RAILWAY TRIANGLE | W | Sewage Pumping Station | INUSE
15682 | ASHCOTT | BRADLEY LANE (TAUNTON ROAD) | W | Sewage Pumping Station | INUSE
15683 | BURTON BRADSTOCK | ANNINGS LANE | S | Sewage Pumping Station | INUSE
15686 | COMPTON DUNDON | HAM LANE | W | Sewage Pumping Station | INUSE
15687 | WIMBORNE | LONNEN ROAD WOOD VIEW COLEHILL | S | Sewage Pumping Station | INUSE
15688 | BRIDGWATER | HAMP WARD | W | Sewage Pumping Station | INUSE
15689 | HILCOTT | PUMPING STATION NO 3 | N | Sewage Pumping Station | INUSE
15690 | TAUNTON | HOLWAY BARTON | W | Sewage Pumping Station | INUSE
15691 | MOTCOMBE | TANK (PUMPED) | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
15692 | ISLE BREWERS | . | W | Sewage Pumping Station | INUSE
15693 | FORDINGBRIDGE | BURGATE FIELDS BURGATE SCHOOL | S | Sewage Pumping Station | INUSE
15694 | WEYMOUTH | BINCLEAVES | S | Sewage Pumping Station | INUSE
15695 | WINCANTON | LAWRENCE HILL | W | Sewage Pumping Station | INUSE
15697 | SALWAY ASH | SALWAY DRIVE | S | Sewage Pumping Station | INUSE
15699 | CHARMOUTH | NEWLANDS BRIDGE | S | Sewage Pumping Station | INUSE
15700 | BRIDGWATER | DAWES PARK NO 3 | W | Sewage Pumping Station | INUSE
15701 | WEMBDON | KELTINGS | W | Sewage Pumping Station | INUSE
15702 | RUSHALL | PEWSEY ROAD | N | Sewage Pumping Station | INUSE
15703 | BABCARY | ORCHARD COTTAGE | W | Sewage Pumping Station | INUSE
15704 | BOTTLESFORD | . | N | Sewage Pumping Station | INUSE
15706 | POOLE | DELPH GARDENS | S | Sewage Pumping Station | INUSE
15708 | CORSCOMBE | CORSCOMBE COURT | S | Sewage Pumping Station | INUSE
15709 | CHICKERELL | EAST FLEET FARM | S | Sewage Pumping Station | INUSE
15710 | BRIDGWATER | DOCKS | W | Sewage Pumping Station | INUSE
15711 | EYPE | PICNIC SITE | S | Sewage Pumping Station | INUSE
15714 | POOLE | WENTWORTH DRIVE | S | Sewage Pumping Station | INUSE
15715 | BRIDGWATER | HORSEY BATH ROAD | W | Sewage Pumping Station | INUSE
15718 | BISHOPS HULL | SHUTEMEAD | W | Sewage Pumping Station | INUSE
15719 | HIGH HAM | . | W | Sewage Pumping Station | INUSE
15720 | NORTON FITZWARREN | STEMBRIDGE WAY | W | Sewage Pumping Station | INUSE
15722 | WELLINGTON | POOLE BRICKYARD | W | Sewage Pumping Station | INUSE
15723 | TETBURY | SPRINGFIELDS | N | Sewage Pumping Station | INUSE
15725 | WIVELISCOMBE | FORD ROAD (LION D'ANGERS) | W | Sewage Pumping Station | INUSE
15726 | PORTISHEAD | LAKE GROUNDS | W | Sewage Pumping Station | INUSE
15727 | CREWKERNE | BLACKNELL LANE | W | Sewage Pumping Station | INUSE
15728 | TAUNTON | KILLAMS PARK | W | Sewage Pumping Station | INUSE
15732 | SHILLINGSTONE | SPENCER GARDENS | S | Sewage Pumping Station | INUSE
15733 | RINGWOOD | HEADLANDS | S | Sewage Pumping Station | INUSE
15734 | WELLINGTON | LOWMOOR TRADING ESTATE 1 | W | Sewage Pumping Station | INUSE
15735 | RINGWOOD | WATERLOO WAY (STATION YARD) | S | Sewage Pumping Station | INUSE
15736 | HIGHBRIDGE | HIGHBRIDGE SOUTH ALSTONE ROAD | W | Sewage Pumping Station | INUSE
15737 | BISHOPSTONE | STANLEY VIEW | S | Private Sewage Pumping Station | INUSE
15738 | BISHOPSTONE | MEADOW VIEW | S | Private Sewage Pumping Station | INUSE
15740 | CHOLDERTON | EDRICS GREEN | S | Private Sewage Pumping Station | INUSE
15741 | BOWERCHALKE | SHEPHERDS CROFT | S | Private Sewage Pumping Station | INUSE
15742 | BOWERCHALKE | SOUTHFIELDS | S | Private Sewage Pumping Station | INUSE
15744 | BROADCHALKE | DOVES MEADOW | S | Private Sewage Pumping Station | INUSE
15745 | BROADCHALKE | KNIGHTON ROAD | S | Private Sewage Pumping Station | INUSE
15746 | BROADCHALKE | NEWTOWN | S | Private Sewage Pumping Station | INUSE
15747 | BURCOMBE | HILLSIDE | S | Private Sewage Pumping Station | INUSE
15748 | COOMBE BISSETT | DROVE (DRAW) CLOSE | S | Private Sewage Pumping Station | INUSE
15749 | COOMBE BISSETT | THRONE CLOSE | S | Private Sewage Pumping Station | INUSE
15750 | FONTHILL BISHOP | SALISBURY ROAD | S | Private Sewage Pumping Station | INUSE
15752 | DURNFORD | LITTLEDOWN VIEW | S | Private Sewage Pumping Station | INUSE
15753 | KILMINGTON | MANOR TERRACE | S | Private Sewage Pumping Station | INUSE
15755 | NUNTON | EBBLESIDE VILLAS | S | Private Sewage Pumping Station | INUSE
15758 | SEDGEHILL | COUNCIL HOUSES | S | Private Sewage Pumping Station | INUSE
15759 | SEMLEY | SEM HILL | S | Private Sewage Pumping Station | INUSE
15761 | TISBURY | SQUALLS LANE | S | Private Sewage Pumping Station | INUSE
15762 | WEST DEAN | MOODYS HILL | S | Private Sewage Pumping Station | INUSE
15763 | WEST KNOYLE | PUCKWELL | S | Private Sewage Pumping Station | INUSE
15766 | WOODFORD | AVON MEADOWS | S | Private Sewage Pumping Station | INUSE
15767 | SALISBURY | HUDSON ROAD | S | Sewage Pumping Station | INUSE
15768 | SALISBURY | KIVEL COURT SALISBURY | S | S105A Sewage Pumping Station | INUSE
15769 | SALISBURY | HALLUM CLOSE | S | S105A Sewage Pumping Station | INUSE
15770 | WILTON | NO 4 RANDALLS CROFT ROAD WILTON | S | S105A Sewage Pumping Station | INUSE
15771 | SALISBURY | GRANGE GARDENS | S | S105A Sewage Pumping Station | INUSE
15772 | PEASEDOWN ST JOHN | WELLOW LANE | N | Sewage Pumping Station | INUSE
15773 | BRIDGWATER | ARGOS HUNTWORTH GATE | W | Private Sewage Pumping Station | INUSE
15774 | BEERCROCOMBE | . | W | Sewage Pumping Station | INUSE
15775 | BROADSTONE | BRYONY CLOSE | S | Sewage Pumping Station | INUSE
15779 | STOCKLINCH | STOCKYARD | W | Sewage Pumping Station | INUSE
15781 | CALNE | BEAVERSBROOK FARM | N | Sewage Pumping Station | INUSE
15782 | KEYNSHAM | DAPPS HILL | N | Sewage Pumping Station | INUSE
15786 | NORTH PETHERTON | NEWTON ROAD | W | Sewage Pumping Station | INUSE
15789 | GILLINGHAM | CHANTRY FIELDS (WAITROSE) | S | Sewage Pumping Station | INUSE
15790 | WEST PARLEY | DUNEDIN DRIVE | S | Sewage Pumping Station | INUSE
15791 | WEST MOORS | GUNDRYMOR INDUSTRIAL ESTATE | S | Sewage Pumping Station | INUSE
15792 | WESTON-SUPER-MARE | KNIGHTSTONE ROAD | W | Sewage Pumping Station | INUSE
15795 | BATH | HAZELTON GARDENS | N | Sewage Pumping Station | INUSE
15796 | TROWBRIDGE | JASMINE WAY | N | Sewage Pumping Station | INUSE
15800 | POOLE | NEWFOUNDLAND DRIVE OPP 20 | S | Sewage Pumping Station | INUSE
15801 | POOLE | ALBANY PARK | S | Sewage Pumping Station | INUSE
15803 | BLEADON | BLEADON MILL | W | Sewage Pumping Station | INUSE
15804 | TAUNTON | KILLAMS LANE | W | Sewage Pumping Station | INUSE
15805 | BRIDGWATER | SHOWGROUND NO1 | W | Sewage Pumping Station | INUSE
15806 | BRIDGWATER | SHOWGROUND NO2 | W | Sewage Pumping Station | INUSE
15807 | WOOL | CHALKE PIT LANE | S | Sewage Pumping Station | INUSE
15808 | ISLE BREWERS | WESTPORT ROAD | W | Sewage Pumping Station | INUSE
15809 | CURRY RIVEL | WESTFIELD EJECTOR STATION | W | Sewage Pumping Station | INUSE
15810 | MELKSHAM | PRIMROSE DRIVE | N | Sewage Pumping Station | INUSE
15811 | MELKSHAM | AWDRY AVENUE NEW | N | Sewage Pumping Station | INUSE
15812 | MELKSHAM | BOWERHILL LANE BOWERHILL | N | Sewage Pumping Station | INUSE
15814 | CHIPPENHAM | METHUEN PARK BATH ROAD | N | Sewage Pumping Station | INUSE
15815 | STREET | BOWLING GREEN | W | Sewage Pumping Station | INUSE
15816 | WINTERBOURNE | DRAGON ROAD (SANDSTONE RISE) | N | Sewage Pumping Station | INUSE
15817 | YATE | SCOTT WAY | N | Sewage Pumping Station | INUSE
15818 | BRISTOL | WAPPING DOCK (SS GREAT BRITAIN) | N | Private Sewage Pumping Station | INUSE
15819 | CHARD | BRYER CLOSE (LORDLEAZE LANE) | W | Sewage Pumping Station | INUSE
15820 | CHRISTCHURCH | FAIRFIELD CLOSE | S | Sewage Pumping Station | INUSE
15821 | FROME | GARSDALE | W | Sewage Pumping Station | INUSE
15861 | KEYNSHAM | THE BRASSMILLS AVON MILL LANE | N | Sewage Pumping Station | INUSE
15887 | BATH | NEWTON ROAD | N | Sewage Pumping Station | INUSE
15900 | CLUTTON | BATCH FARM | N | Sewage Pumping Station | INUSE
15965 | BRISTOL | ST GEORGES AVENUE CREWS HOLE ROAD | N | Sewage Pumping Station | INUSE
16000 | WELLINGTON | CORAMS LANE | W | Combined Sewer Overflow | INUSE
16010 | BATH | WIDCOMBE RISE OFF PRIOR PARK ROAD | N | Combined Sewer Overflow | INUSE
16011 | BATH | ENGLISHCOMBE LANE / STIRTINGDALE ROAD JUNCTION | N | Combined Sewer Overflow | INUSE
16012 | BATH | HAZEL GROVE S/O NO 22/23 | N | Combined Sewer Overflow | INUSE
16013 | BATH | HAZEL GROVE R/O NO 24 TO 39 | N | Combined Sewer Overflow | INUSE
16014 | BATH | BECKHAMPTON ROAD O/S NO 50 | N | Combined Sewer Overflow | INUSE
16016 | BATH | MOORLAND ROAD NEAR NO 49 | N | Combined Sewer Overflow | INUSE
16017 | BATH | DORSET CLOSE O/S SCHOOL | N | Combined Sewer Overflow | INUSE
16018 | BATH | HISCOCKS DRIVE ADJ TO RAILWAY BRIDGE | N | Combined Sewer Overflow | INUSE
16019 | BATH | DURLEY PARK / OLDFIELD LANE JUNCTION | N | Combined Sewer Overflow | INUSE
16035 | BATH | HUNGERFORD ROAD / UPPER BRISTOL ROAD JUNCTION | N | Combined Sewer Overflow | INUSE
16040 | BATH | NORFOLK BUILDINGS | N | Combined Sewer Overflow | INUSE
16042 | BATH | SOUTH PARADE IN GARDEN | N | Combined Sewer Overflow | INUSE
16043 | BATH | RECREATION GROUND BY NORTH STAND | N | Combined Sewer Overflow | INUSE
16045 | BATH | ST JOHNS RC PRIM SCHOOL AT REAR NR RECREATION GROUND | N | Combined Sewer Overflow | INUSE
16046 | BATH | FERRY LANE O/S FUNERAL DIRECTOR | N | Combined Sewer Overflow | INUSE
16048 | BATH | ST JOHNS ROAD OPP VULCAN HOUSE | N | Combined Sewer Overflow | INUSE
16049 | BATH | WARMINSTER ROAD / SYDNEY ROAD JUNCTION | N | Combined Sewer Overflow | INUSE
16050 | BATH | EA DEPOT | N | Sewage Pumping Station | INUSE
16052 | BATH | BRASSMILL LANE BETWEEN OSBOURN / AVONDALE ROAD | N | Combined Sewer Overflow | INUSE
16053 | BATH | LOWER BRISTOL ROAD NEAR MILL LANE | N | Combined Sewer Overflow | INUSE
16057 | BATH | TECHNOLOGY HOUSE | N | Sewage Pumping Station | INUSE
16058 | BATH | FIELDINGS ROAD | N | Combined Sewer Overflow | INUSE
16059 | BATH | STATION ROAD S/O 44 LOCKSBROOK ROAD | N | Combined Sewer Overflow | INUSE
16060 | BATH | SPRING GARDENS ROAD NO 1 | N | Combined Sewer Overflow | INUSE
16061 | BATH | GROVE STREET OPP NO 13 | N | Combined Sewer Overflow | INUSE
16062 | BATH | WALCOT SYPHON AT HEAD | N | Combined Sewer Overflow | INUSE
16063 | BATH | RIVERSIDE WALK OLD CATTLE MARKET WALCOT | N | Combined Sewer Overflow | INUSE
16064 | BATH | GROVE STREET / ST JOHNS STREET JUNC NR BETHEL CH | N | Combined Sewer Overflow | INUSE
16065 | BATH | RIVERSIDE OLD ORCHARD ROAD WALCOT | N | Combined Sewer Overflow | INUSE
16067 | BATH | LADYMEAD HOUSE (R/O) WALCOT | N | Combined Sewer Overflow | INUSE
16068 | BATH | WALCOT RIVER BANK END OF CHATHAM ROW | N | Combined Sewer Overflow | INUSE
16069 | BATH | LOOP ROAD WALCOT STREET CAR PARK | N | Combined Sewer Overflow | INUSE
16070 | BATH | WALCOT ST RIVER BANK R/O ALDRIDGES | N | Combined Sewer Overflow | INUSE
16072 | BATH | ST JOHNS ROAD SCOUTS SITE | N | Combined Sewer Overflow | INUSE
16073 | BATH | CLEVELAND BRIDGE TO THE WEST | N | Combined Sewer Overflow | INUSE
16077 | BATH | WALCOT TERRACE R/O NO 1 ON LONDON ROAD | N | Combined Sewer Overflow | INUSE
16078 | BATH | FORESTER AVENUE O/S HORTON HOUSE | N | Combined Sewer Overflow | INUSE
16081 | BATH | ROCKCLIFFE ROAD R/O NO 45 | N | Combined Sewer Overflow | INUSE
16083 | BATH | KENSINGTON MEADOWS BUS DEPOT STORM TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
16084 | BATH | HAMPTON ROW / ROCKLIFFE AVENUE R/O (NR BATHS) | N | Combined Sewer Overflow | INUSE
16088 | BATH | PARADE GARDENS | N | Combined Sewer Overflow | INUSE
16089 | BATH | NEWMARKET ROW GRAND PARADE | N | Combined Sewer Overflow | INUSE
16090 | BATH | SPRING GARDENS ROAD U/S K&A CANAL SYPHON | N | Combined Sewer Overflow | INUSE
16091 | BATH | ENTRY HILL GARDENS R/G NO 6 (LYNCOMBE VALE) | N | Combined Sewer Overflow | INUSE
16092 | BATH | FOX HILL O/S WOODLANDS COTTAGE | N | Combined Sewer Overflow | INUSE
16093 | BATH | LYNCOMBE VALE O/S 3 NEW VILLAS | N | Combined Sewer Overflow | INUSE
16095 | BATH | PRIOR PARK ROAD | N | Combined Sewer Overflow | INUSE
16096 | BATH | LYNCOMBE VALE O/S NO 1 | N | Combined Sewer Overflow | INUSE
16098 | BATH | WIDCOMBE BAPTIST CHURCH AT REAR CLAVERTON | N | Combined Sewer Overflow | INUSE
16099 | BATH | PRIOR PARK ROAD OPP NO 9 | N | Combined Sewer Overflow | INUSE
16110 | BATH | BLOOMFIELD ROAD NO 33 JUNCTION WITH HENSLEY ROAD | N | Combined Sewer Overflow | INUSE
16111 | BATH | WELLSWAY JUNCTION WITH KIPLING AVE | N | Combined Sewer Overflow | INUSE
16112 | BATH | WELLSWAY / BLOOMFIELD ROAD JUNCTION BEAR FLAT | N | Combined Sewer Overflow | INUSE
16113 | BATH | WELLSWAY R/O NO 34 | N | Combined Sewer Overflow | INUSE
16115 | BATH | WESTMORELAND ROAD / CHELTENHAM STREET JUNCTION | N | Combined Sewer Overflow | INUSE
16116 | BATH | LOWER BRISTOL ROAD WEST OF OAK STREET | N | Combined Sewer Overflow | INUSE
16117 | BATH | CHURCHILL BRIDGE ISLAND OPP WELLS ROAD | N | Combined Sewer Overflow | INUSE
16119 | BATH | RUSH HILL OPP CULVERHAY SCHOOL | N | Combined Sewer Overflow | INUSE
16120 | BATH | WHITEWAY / RUSH HILL / ENGLISHCOMBE LANE JUNCTION | N | Combined Sewer Overflow | INUSE
16121 | BATH | ENGLISHCOMBE LANE O/S 275 JUNCTION WITH MOUNT ROAD | N | Combined Sewer Overflow | INUSE
16122 | BATH | SOUTHDOWN ROAD O/S NO 85 NR GLEBE ROAD JUNCTION | N | Combined Sewer Overflow | INUSE
16123 | BATH | ENGLISHCOMBE LANE / SOUTHDOWN ROAD JUNCTION | N | Combined Sewer Overflow | INUSE
16124 | BATH | RUSH HILL / OLD FOSSE ROAD JUNCTION | N | Combined Sewer Overflow | INUSE
16125 | BATH | LYMORE GARDENS O/S NO 15 ADJ LAUNDRY | N | Combined Sewer Overflow | INUSE
16127 | BATH | MILLMEAD ROAD NR JUNCTION LYNDHURST ROAD | N | Combined Sewer Overflow | INUSE
16131 | BOURNEMOUTH | TUCKTON ROAD O/S 156 | S | Combined Sewer Overflow | INUSE
16134 | BRISTOL | AVONMOUTH WAY | N | Combined Sewer Overflow | INUSE
16136 | BRISTOL | OLD PARK ROAD O/S NO 45 | N | Combined Sewer Overflow | INUSE
16137 | BRISTOL | PORTWAY UNDER AVON BRIDGE | N | Combined Sewer Overflow | INUSE
16138 | BRISTOL | QUEEN STREET / MEADOW STREET | N | Combined Sewer Overflow | INUSE
16139 | BRISTOL | PORTWAY NEAR RAILWAY | N | Combined Sewer Overflow | INUSE
16142 | BRISTOL | SPRINGFIELD AVENUE O/S NO 5 | N | Combined Sewer Overflow | INUSE
16143 | BRISTOL | SPRINGFIELD AVENUE O/S NO 7 | N | Combined Sewer Overflow | INUSE
16144 | BRISTOL | STATION ROAD O/S NO 30 | N | Combined Sewer Overflow | INUSE
16145 | BRISTOL | STATION ROAD O/S LAMPLIGTERS PUB | N | Combined Sewer Overflow | INUSE
16146 | BRISTOL | THIRD WAY | N | Combined Sewer Overflow | INUSE
16147 | BRISTOL | WATLING WAY IN GARDEN NO 27 | N | Combined Sewer Overflow | INUSE
16152 | BRISTOL | BATH ROAD / FLOWERS HILL | N | Combined Sewer Overflow | INUSE
16155 | BRISTOL | BATH ROAD TRADING ESTATE | N | Combined Sewer Overflow | INUSE
16156 | BRISTOL | BRISLINGTON HILL/BRISTOL HILL JNC. | N | Combined Sewer Overflow | INUSE
16159 | BRISTOL | BRISTOL ROAD / SALTWELL VIADUCT | N | Combined Sewer Overflow | INUSE
16160 | BRISTOL | BROOMHILL ROAD / HUBERT CLOSE | N | Combined Sewer Overflow | INUSE
16161 | BRISTOL | CENTRAL INDUSTRIAL ESTATE BATH ROAD | N | Combined Sewer Overflow | INUSE
16167 | BRISTOL | MAXSE ROAD JUNCTION MARSTON ROAD | N | Combined Sewer Overflow | INUSE
16168 | BRISTOL | PETHERTON ROAD PAINT FACTORY | N | Combined Sewer Overflow | INUSE
16170 | BRISTOL | SCHOOL ROAD O/S NO 112 | N | Combined Sewer Overflow | INUSE
16171 | BRISTOL | SIDCOT | N | Combined Sewer Overflow | INUSE
16172 | BRISTOL | SIDCOT O/S NO 8 | N | Combined Sewer Overflow | INUSE
16173 | BRISTOL | SOMERDALE AVENUE / SALCOMBE ROAD | N | Combined Sewer Overflow | INUSE
16174 | BRISTOL | SOMERDALE AVENUE / SPRING GARDENS | N | Combined Sewer Overflow | INUSE
16175 | BRISTOL | ST ANNES TERR/BRISLINGTON BROOK | N | Combined Sewer Overflow | INUSE
16176 | BRISTOL | STOCKWOOD LANE / SCOTLAND BOTTOM | N | Private Sewage Pumping Station | INUSE
16177 | BRISTOL | WELLS ROAD/MARSTON ROAD | N | Combined Sewer Overflow | INUSE
16178 | BRISTOL | WELLS ROAD / GREENMORE ROAD | N | Combined Sewer Overflow | INUSE
16179 | BRISTOL | WELLS ROAD O/S NO 395 | N | Combined Sewer Overflow | INUSE
16180 | BRISTOL | WELLS ROAD O/S NO 424 | N | Combined Sewer Overflow | INUSE
16181 | BRISTOL | WELLS ROAD / PRIORY ROAD | N | Combined Sewer Overflow | INUSE
16183 | BRISTOL | WHITBY ROAD NEAR BLOOMFIELD ROAD | N | Combined Sewer Overflow | INUSE
16185 | BRISTOL | WOOTTON PARK | N | Combined Sewer Overflow | INUSE
16186 | BRISTOL | BOND STREET O/S CAR PARK | N | Combined Sewer Overflow | INUSE
16188 | BRISTOL | BROADMEAD ON HUB | N | Combined Sewer Overflow | INUSE
16189 | BRISTOL | BROADMEAD / PENN STREET | N | Combined Sewer Overflow | INUSE
16190 | BRISTOL | CATTLE MARKET ROAD SIPHON | N | Combined Sewer Overflow | INUSE
16192 | BRISTOL | CHRISTMAS STEPS AT THE BOTTOM | N | Combined Sewer Overflow | INUSE
16193 | BRISTOL | COMMERCIAL ROAD / BEDMIN BRIDGE | N | Combined Sewer Overflow | INUSE
16194 | BRISTOL | CUMBERLAND ROAD OLD GAOL SIPHON | N | Combined Sewer Overflow | INUSE
16195 | BRISTOL | FEEDER ROAD / BARTON HILL BRIDGE | N | Combined Sewer Overflow | INUSE
16196 | BRISTOL | HOTWELLS ROAD APPROX NO 100 | N | Combined Sewer Overflow | INUSE
16197 | BRISTOL | HOTWELLS ROAD EAST | N | Combined Sewer Overflow | INUSE
16198 | BRISTOL | LEWIN MEAD O/S GREYFRIARS | N | Combined Sewer Overflow | INUSE
16199 | BRISTOL | NELSON STREET O/S POLICE STATION | N | Combined Sewer Overflow | INUSE
16201 | BRISTOL | NEWFOUNDLAND ROAD / PRITCHARD STREET | N | Combined Sewer Overflow | INUSE
16202 | BRISTOL | NURSING SCHOOL MARLBOROUGH STREET | N | Combined Sewer Overflow | INUSE
16204 | BRISTOL | PORTWAY NEAR PLIMSOLL BRIDGE (PUMPED) | N | Combined Sewer Overflow | INUSE
16205 | BRISTOL | PORTWAY CLIFTON LOW LEVEL PST | N | Combined Sewer Overflow | INUSE
16206 | BRISTOL | SILVER ST/BROADMEAD | N | Combined Sewer Overflow | INUSE
16207 | BRISTOL | VICTOR STREET | N | Combined Sewer Overflow | INUSE
16208 | BRISTOL | WELLINGTON ROAD PLAYGROUND | N | Combined Sewer Overflow | INUSE
16209 | BRISTOL | WHITEHALL ROAD O/S NO 46 | N | Combined Sewer Overflow | INUSE
16210 | BRISTOL | VALLEY ROAD ZIG ZAG PATH BRIDGE | N | Combined Sewer Overflow | INUSE
16213 | BRISTOL | BLACKBERRY HILL O/S NO 9 FROME BRIDGE | N | Combined Sewer Overflow | INUSE
16214 | BRISTOL | BRENTRY ROAD O/S NO 57 | N | Combined Sewer Overflow | INUSE
16216 | BRISTOL | BURCHILLS GREEN ROAD O/S NO 164 | N | Combined Sewer Overflow | INUSE
16222 | BRISTOL | FILWOOD ROAD / GOODNESTON ROAD | N | Combined Sewer Overflow | INUSE
16226 | BRISTOL | FOUNDARY LANE OPEN SPACE | N | Combined Sewer Overflow | INUSE
16229 | BRISTOL | FRENCHAY PARK ROAD NO 46A | N | Combined Sewer Overflow | INUSE
16230 | BRISTOL | FRENCHAY PARK ROAD O/S NO 201 | N | Combined Sewer Overflow | INUSE
16233 | BRISTOL | FACTORY R/O GORDON ROAD | N | Combined Sewer Overflow | INUSE
16234 | BRISTOL | GREENBANK VIEW | N | Combined Sewer Overflow | INUSE
16235 | BRISTOL | GROVE ROAD NEAR FISHPONDS ROAD | N | Combined Sewer Overflow | INUSE
16236 | BRISTOL | GROVE ROAD O/S NO 31 | N | Combined Sewer Overflow | INUSE
16237 | BRISTOL | GROVE ROAD O/S NO 41 | N | Combined Sewer Overflow | INUSE
16244 | BRISTOL | LODGE CAUSEWAY O/S 147 | N | Combined Sewer Overflow | INUSE
16247 | BRISTOL | MOORLANDS ROAD O/S NO 63 | N | Combined Sewer Overflow | INUSE
16251 | BRISTOL | PARNALLS FACTORY | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
16252 | BRISTOL | ROSE GREEN ROAD | N | Combined Sewer Overflow | INUSE
16254 | BRISTOL | STAPLETON ROAD / GLENFROME ROAD | N | Combined Sewer Overflow | INUSE
16256 | BRISTOL | SPEEDWELL ROAD O/S NO 415 | N | Combined Sewer Overflow | INUSE
16260 | BRISTOL | ANDOVER ROAD / STOCKWOOD CRESCENT | N | Combined Sewer Overflow | INUSE
16261 | BRISTOL | BEDMINSTER ROAD CYCLE TRACK | N | Combined Sewer Overflow | INUSE
16262 | BRISTOL | BEDMINSTER ROAD SIDE OF 191 | N | Combined Sewer Overflow | INUSE
16266 | BRISTOL | CLIFT HOUSE ROAD ASHTON AVENUE P STN INLET OVERFLO | N | Combined Sewer Overflow | INUSE
16268 | BRISTOL | DERHAM ROAD R/O NO 31 | N | Combined Sewer Overflow | INUSE
16269 | BRISTOL | EAST STREET | N | Combined Sewer Overflow | INUSE
16270 | BRISTOL | FORTFIELD ROAD O/S NO 166 | N | Combined Sewer Overflow | INUSE
16271 | BRISTOL | GREENWAY BUSH LANE / GREENBANK ROAD | N | Combined Sewer Overflow | INUSE
16272 | BRISTOL | GREENWAY BUSH LANE / LOWER SIDNEY STREET | N | Combined Sewer Overflow | INUSE
16276 | BRISTOL | HILL AVENUE / ST LUKES ROAD | N | Combined Sewer Overflow | INUSE
16279 | BRISTOL | MYRTLE ST IN CAR PARK | N | Combined Sewer Overflow | INUSE
16280 | BRISTOL | OLD MEAD WALK NO 9 | N | Combined Sewer Overflow | INUSE
16281 | BRISTOL | PARSON STREET / NOVERS HILL | N | Combined Sewer Overflow | INUSE
16282 | BRISTOL | PEMBROKE ROAD NO 19 | N | Combined Sewer Overflow | INUSE
16285 | BRISTOL | ST JOHNS LANE | N | Combined Sewer Overflow | INUSE
16286 | BRISTOL | TUGELA ROAD O/S NO 18 | N | Combined Sewer Overflow | INUSE
16287 | BRISTOL | VALE LANE | N | Combined Sewer Overflow | INUSE
16289 | BRISTOL | YORK ROAD | N | Combined Sewer Overflow | INUSE
16290 | BRISTOL | ALMA ROAD O/S NO 87 | N | Combined Sewer Overflow | INUSE
16291 | BRISTOL | BIRCHALL ROAD O/S NO 1 | N | Combined Sewer Overflow | INUSE
16292 | BRISTOL | BISHOP ROAD / 214 GLOUCESTER ROAD | N | Combined Sewer Overflow | INUSE
16297 | BRISTOL | CLIFTON DOWN STATION | N | Combined Sewer Overflow | INUSE
16298 | BRISTOL | COTHAM BROW O/S NO 137 | N | Combined Sewer Overflow | INUSE
16299 | BRISTOL | COTHAM HILL / HAMPTON PARK | N | Combined Sewer Overflow | INUSE
16301 | SHEPTON MALLET | VICTORIA GROVE/CHARLTON ROAD | W | Combined Sewer Overflow | INUSE
16302 | STON EASTON | WELLOW BROOK IN FIELD NEAR BY | W | Combined Sewer Overflow | INUSE
16304 | BRISTOL | GLOUCESTER ROAD O/S NO 199 | N | Combined Sewer Overflow | INUSE
16306 | BRISTOL | HAMPTON ROAD / MELVILLE COURT | N | Combined Sewer Overflow | INUSE
16308 | STREET | FARM LANE | W | Combined Sewer Overflow | INUSE
16312 | BRISTOL | SOMMERVILLE ROAD / NORTH ROAD | N | Combined Sewer Overflow | INUSE
16313 | BRISTOL | ST OSWALDS ROAD NO 2 IN BACK GARDEN | N | Combined Sewer Overflow | INUSE
16314 | BRISTOL | BROOK ROAD / WHITEFIELD ROAD | N | Combined Sewer Overflow | INUSE
16315 | BRISTOL | BROOK ROAD CAR PARK J SOMERS & SONS | N | Combined Sewer Overflow | INUSE
16316 | BRISTOL | BUDE AVENUE FOOTBALL PITCH | N | Combined Sewer Overflow | INUSE
16317 | BRISTOL | CHAPLIN ROAD O/S NO 60 | N | Combined Sewer Overflow | INUSE
16318 | BRISTOL | CHARLTON ROAD O/S NO 82 | N | Combined Sewer Overflow | INUSE
16321 | BRISTOL | CONHAM VALE | N | Combined Sewer Overflow | INUSE
16322 | BRISTOL | HIGH STREET / ST MARKS ROAD | N | Combined Sewer Overflow | INUSE
16323 | BRISTOL | HILLBURN ROAD / AVENING ROAD | N | Combined Sewer Overflow | INUSE
16324 | BRISTOL | HOLMES HILL ROAD OPP NO 1 | N | Combined Sewer Overflow | INUSE
16326 | BRISTOL | HUDDS VALE ROAD / PLUMERS HILL | N | Combined Sewer Overflow | INUSE
16327 | BRISTOL | LYPPIATT ROAD O/S NO 29 | N | Combined Sewer Overflow | INUSE
16328 | BRISTOL | LYPPIATT ROAD O/S NO 57 | N | Combined Sewer Overflow | INUSE
16329 | BRISTOL | MARION WALK O/S NO 4 | N | Combined Sewer Overflow | INUSE
16330 | BRISTOL | MEADOW VALE NO 40 FRONT GARDEN | N | Combined Sewer Overflow | INUSE
16334 | BRISTOL | NEW QUEEN ST O/S NO 72 | N | Combined Sewer Overflow | INUSE
16335 | BRISTOL | HOLDENHURST ROAD / BROAD ROAD | N | Combined Sewer Overflow | INUSE
16336 | BRISTOL | QUEEN STREET O/S NO 2 | N | Combined Sewer Overflow | INUSE
16338 | BRISTOL | SALISBURY AVE O/S NO 30 | N | Combined Sewer Overflow | INUSE
16339 | BRISTOL | SPEEDWELL ROAD O/S NO 34 | N | Combined Sewer Overflow | INUSE
16341 | BRISTOL | SPEEDWELL ROAD / VENTNOR ROAD | N | Combined Sewer Overflow | INUSE
16342 | BRISTOL | ST GEORGES PARK SOUTH 28 LYNDALE ROAD | N | Combined Sewer Overflow | INUSE
16343 | BRISTOL | ST GEORGES PARK NORTH 329 CHURCH ROAD | N | Combined Sewer Overflow | INUSE
16347 | BRISTOL | WHITEWAY ROAD O/S NO 67 | N | Combined Sewer Overflow | INUSE
16348 | BRISTOL | ASHLEY DOWN ROAD ALLOTMENTS | N | Combined Sewer Overflow | INUSE
16349 | BRISTOL | FILTON AVENUE OUTSIDE NO 230 | N | Combined Sewer Overflow | INUSE
16353 | BRISTOL | LANDSEER AVENUE O/S NO 50 | N | Combined Sewer Overflow | INUSE
16354 | BRISTOL | MINA ROAD O/S NO 212 | N | Combined Sewer Overflow | INUSE
16355 | BRISTOL | MULLER ROAD ALLOTMENTS | N | Combined Sewer Overflow | INUSE
16359 | BRISTOL | ROWLANDSON GARDENS NO 24 | N | Combined Sewer Overflow | INUSE
16361 | BRISTOL | THE MANSE SUMMERS LANE | N | Combined Sewer Overflow | INUSE
16362 | BRISTOL | SUSSEX PLACE R/O NO 48 | N | Combined Sewer Overflow | INUSE
16363 | BRISTOL | TORTWORTH ROAD | N | Combined Sewer Overflow | INUSE
16365 | BRISTOL | ABBEY ROAD O/S NO 123 | N | Combined Sewer Overflow | INUSE
16367 | BRISTOL | CANFORD ROAD / CANFORD LANE | N | Combined Sewer Overflow | INUSE
16369 | BRISTOL | CHERINGTON ROAD O/S NO 2 | N | Combined Sewer Overflow | INUSE
16372 | BRISTOL | EAST HILL / CHOCK LANE | N | Combined Sewer Overflow | INUSE
16374 | BRISTOL | HARBURY ROAD / WELLINGTON HILL W | N | Combined Sewer Overflow | INUSE
16376 | BRISTOL | HENBURY ROAD O/S NO 47 | N | Combined Sewer Overflow | INUSE
16378 | BRISTOL | HENLEAZE ROAD | N | Combined Sewer Overflow | INUSE
16379 | BRISTOL | HENLEAZE ROAD O/S EASTFIELD INN | N | Combined Sewer Overflow | INUSE
16380 | BRISTOL | HENLEAZE ROAD / WANSCOW WALK | N | Combined Sewer Overflow | INUSE
16381 | BRISTOL | HIGH STREET / HENBURY ROAD | N | Combined Sewer Overflow | INUSE
16382 | BRISTOL | LAWRENCE GROVE O/S NO 21 | N | Combined Sewer Overflow | INUSE
16384 | BRISTOL | NEWCOMBE ROAD O/S NO 11 | N | Combined Sewer Overflow | INUSE
16387 | BRISTOL | OAKWOOD ROAD O/S NO 21 | N | Combined Sewer Overflow | INUSE
16388 | BRISTOL | ROCKSIDE DRIVE O/S NO 2 | N | Combined Sewer Overflow | INUSE
16392 | BRISTOL | SEA MILLS LANE NR BRIDGE | N | Combined Sewer Overflow | INUSE
16394 | BRISTOL | SHIREHAMPTON ROAD NO 100 | N | Combined Sewer Overflow | INUSE
16398 | BRISTOL | STOKE LANE O/S NO 122 WESTBURY ON TRYM | N | Combined Sewer Overflow | INUSE
16401 | BRISTOL | TRYM ROAD O/S NO 41 | N | Combined Sewer Overflow | INUSE
16403 | BRISTOL | WELLINGTON HILL WEST NO 147 (NO 1) | N | Combined Sewer Overflow | INUSE
16404 | BRISTOL | WELLINGTON HILL WEST NO 147 (NO 2) | N | Combined Sewer Overflow | INUSE
16405 | BRISTOL | WELLINGTON HILL WEST NO 158 | N | Combined Sewer Overflow | INUSE
16406 | BRISTOL | WELLINGTON HILL WEST NO 175 | N | Combined Sewer Overflow | INUSE
16407 | BRISTOL | WELLINGTON HILL WEST / BISHOPTHORPE ROAD | N | Combined Sewer Overflow | INUSE
16410 | BRISTOL | WESTBURY ROAD / GRANGE COURT ROAD | N | Combined Sewer Overflow | INUSE
16414 | BRISTOL | AVONMOUTH ROAD / WEST TOWN ROAD | N | Combined Sewer Overflow | INUSE
16415 | BRISTOL | PRINCE STREET ROUNDABOUT | N | Combined Sewer Overflow | INUSE
16416 | BRISTOL | CLARE STREET | N | Combined Sewer Overflow | INUSE
16417 | BRISTOL | AVON STREET / OXFORD STREET | N | Combined Sewer Overflow | INUSE
16418 | BRISTOL | ST JAMES BARTON | N | Combined Sewer Overflow | INUSE
16419 | BRISTOL | MULLER ROAD / FROME BRIDGE | N | Combined Sewer Overflow | INUSE
16422 | BRISTOL | NEATH ROAD / WHITEHALL ROAD | N | Combined Sewer Overflow | INUSE
16423 | BRISTOL | PORTWAY BRIDGE | N | Combined Sewer Overflow | INUSE
16424 | BRISTOL | DRUID WOOD | N | Combined Sewer Overflow | INUSE
16434 | BRISTOL | AVONMOUTH ROAD / WEST TOWN ROAD | N | Combined Sewer Overflow | INUSE
16438 | BRISTOL | BROADMEAD / SILVER STREET | N | Combined Sewer Overflow | INUSE
16440 | BRISTOL | MAGGS LANE OPEN SPACE | N | Combined Sewer Overflow | INUSE
16448 | EASTERTON | MANOR HOUSE | N | Combined Sewer Overflow | INUSE
16449 | POULSHOT | MILL LANE | N | Combined Sewer Overflow | INUSE
16451 | DEVIZES | ROUNDWAY HOSPITAL | N | Combined Sewer Overflow | INUSE
16453 | LITTLETON PANELL | RUSSELL MILL LANE | N | Combined Sewer Overflow | INUSE
16455 | DEVIZES | VALLEY SEWER | N | Combined Sewer Overflow | INUSE
16462 | BRISTOL HANHAM | BEECHWOOD AVENUE | N | Combined Sewer Overflow | INUSE
16464 | BRISTOL HANHAM | CENTRAL AVENUE | N | Combined Sewer Overflow | INUSE
16467 | BRISTOL HANHAM | FOOTSHILL ROAD | N | Combined Sewer Overflow | INUSE
16468 | BRISTOL HANHAM | HIGH STREET | N | Combined Sewer Overflow | INUSE
16469 | BRISTOL HANHAM | LOWER HANHAM ROAD | N | Combined Sewer Overflow | INUSE
16470 | BRISTOL HANHAM | POLLY BARNES HILL | N | Combined Sewer Overflow | INUSE
16472 | BRISTOL KINGSWOOD | WOOD ROAD | N | Combined Sewer Overflow | INUSE
16473 | BRISTOL KINGSWOOD | WOODSIDE ROAD | N | Combined Sewer Overflow | INUSE
16475 | BRISTOL KINGSWOOD | NEW CHELTENHAM ROAD NO 170 | N | Combined Sewer Overflow | INUSE
16476 | BRISTOL KINGSWOOD | DAWN RISE O/S 45 | N | Combined Sewer Overflow | INUSE
16478 | BRISTOL KINGSWOOD | DOWNEND ROAD NO 48 | N | Combined Sewer Overflow | INUSE
16479 | BRISTOL KINGSWOOD | NEW CHELTENHAM ROAD NO 20 | N | Combined Sewer Overflow | INUSE
16480 | BRISTOL KINGSWOOD | NEW CHELTENHAM ROAD O/S 23 / 25 | N | Combined Sewer Overflow | INUSE
16481 | BRISTOL KINGSWOOD | NEW CHELTENHAM ROAD O/S 43 | N | Combined Sewer Overflow | INUSE
16482 | BRISTOL KINGSWOOD | NEW CHELTENHAM ROAD NO 84 | N | Combined Sewer Overflow | INUSE
16484 | BRISTOL KINGSWOOD | ALMA ROAD / NEW CHELTENHAM ROAD JUNCTION | N | Combined Sewer Overflow | INUSE
16486 | BRISTOL KINGSWOOD | HOLLY HILL ROAD / NEW CHELTENHAM ROAD JUNCTION | N | Combined Sewer Overflow | INUSE
16487 | BRISTOL KINGSWOOD | STATION ROAD OPP 61 | N | Combined Sewer Overflow | INUSE
16488 | BRISTOL KINGSWOOD | HILL STREET | N | Combined Sewer Overflow | INUSE
16489 | BRISTOL KINGSWOOD | ORCHARD ROAD | N | Combined Sewer Overflow | INUSE
16491 | BRISTOL WARMLEY | MILL LANE AT REAR | N | Combined Sewer Overflow | INUSE
16497 | BALTONSBOROUGH | ORCHARD LEIGH | W | Combined Sewer Overflow | INUSE
16498 | COLEFORD | KINGS HEAD | W | Combined Sewer Overflow | INUSE
16499 | CROSCOMBE | FAYRE WAY / LONG | W | Combined Sewer Overflow | INUSE
16500 | CROSCOMBE | MANOR HOUSE OPP | W | Combined Sewer Overflow | INUSE
16501 | FROME | FARRANT ROAD NEAR YOUTH CENTRE | W | Combined Sewer Overflow | INUSE
16502 | FROME | LOWER KEYFORD | W | Combined Sewer Overflow | INUSE
16503 | FROME | FELTHAM DRIVE NEAR FOOTBRIDGE | W | Combined Sewer Overflow | INUSE
16504 | FROME | MERCHANTS BARTON | W | Combined Sewer Overflow | INUSE
16505 | FROME | SINGERS CATTLE MARKET | W | Combined Sewer Overflow | INUSE
16506 | FROME | WHATCOMBE ROAD NO 20 | W | Combined Sewer Overflow | INUSE
16507 | FROME | WESTWAY PRECINCT CAR PARK R/O | W | Combined Sewer Overflow | INUSE
16508 | FROME | COURT HOUSE KING STREET | W | Combined Sewer Overflow | INUSE
16509 | FROME | ADDERWELL CLOSE | W | Combined Sewer Overflow | INUSE
16510 | FROME | PORTWAY / LOCKS HILL | W | Combined Sewer Overflow | INUSE
16511 | FROME | NORTH OF CARPET FACTORY NEAR RAILWAY JUNCTION | W | Combined Sewer Overflow | INUSE
16512 | FROME | WALLBRIDGE | W | Combined Sewer Overflow | INUSE
16513 | FROME | RODDEN ROAD | W | Combined Sewer Overflow | INUSE
16514 | GLASTONBURY | PARK FARM ROAD WIRRAL PARK | W | Combined Sewer Overflow | INUSE
16525 | SHEPTON MALLET | SHAFTGATE AV NO 82/84 | W | Combined Sewer Overflow | INUSE
16526 | SHEPTON MALLET | CATS ASH/COWL STREET | W | Combined Sewer Overflow | INUSE
16527 | SHEPTON MALLET | SUNNY MOUNT/HAM LANE | W | Combined Sewer Overflow | INUSE
16540 | STREET | GLASTON ROAD OPP 30 | W | Combined Sewer Overflow | INUSE
16541 | STREET | STRODE ROAD ALLOTMENTS | W | Combined Sewer Overflow | INUSE
16543 | WELLS | PRIORY HOSPITAL IN THE REAR GARDEN NEAR WEIR | W | Combined Sewer Overflow | INUSE
16544 | WOOKEY HOLE | KENNEL BATCH / HIGH STREET | W | Combined Sewer Overflow | INUSE
16546 | RODE | BARROW FARM TANK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
16550 | GILLINGHAM | QUEEN STREET | S | Combined Sewer Overflow | INUSE
16551 | SHAFTESBURY | HOLLYROOD FARM | S | Combined Sewer Overflow | INUSE
16552 | STURMINSTER NEWTON | BULL INN | S | Combined Sewer Overflow | INUSE
16555 | FRAMPTON COTTERELL | ST PETERS CHURCH (SE) BRIDGE WAY | N | Combined Sewer Overflow | INUSE
16556 | FRAMPTON COTTERELL | ST PETERS CHURCH (NW) CHURCH ROAD | N | Combined Sewer Overflow | INUSE
16557 | FRAMPTON COTTERELL | CLYDE ROAD BRICKENHILL PERSONAGE BRIDGE (SE) | N | Combined Sewer Overflow | INUSE
16558 | FRAMPTON COTTERELL | RECTORY ROAD O/S 54 PARSONAGE BRIDGE (NW) | N | Combined Sewer Overflow | INUSE
16559 | PUCKLECHURCH | FELTHAM ROAD | N | Combined Sewer Overflow | INUSE
16561 | WINTERBOURNE | WATLEYS END IN FIELD OFF FACTORY ROAD | N | Combined Sewer Overflow | INUSE
16562 | FRAMPTON COTTERELL | WEST END NIGHTINGALES BRIDGE | N | Combined Sewer Overflow | INUSE
16564 | CHIPPENHAM | BRISTOL ROAD | N | Combined Sewer Overflow | INUSE
16566 | CALNE | OXFORD ROAD / WOOD STREET | N | Combined Sewer Overflow | INUSE
16569 | CHIPPENHAM | COMMONS SLIP | N | Combined Sewer Overflow | INUSE
16572 | CHIPPENHAM | DALLAS ROAD | N | Combined Sewer Overflow | INUSE
16574 | MALMESBURY | DARK LANE / 8 FOXLEY LANE | N | Combined Sewer Overflow | INUSE
16575 | BRINKWORTH | FOUL SEW O/F | N | Combined Sewer Overflow | INUSE
16577 | CHIPPENHAM | GASTONS ROAD | N | Combined Sewer Overflow | INUSE
16579 | MALMESBURY | HARPERS LANE | N | Combined Sewer Overflow | INUSE
16582 | CHIPPENHAM | LONG CLOSE | N | Combined Sewer Overflow | INUSE
16583 | MALMESBURY | LOWER HIGH STREET | N | Combined Sewer Overflow | INUSE
16585 | CALNE | MARDEN HOUSE CULVERT AT REAR | N | Combined Sewer Overflow | INUSE
16587 | CHIPPENHAM | MONKTON PARK OFFICES | N | Combined Sewer Overflow | INUSE
16588 | CALNE | MOSSES MILL 2 | N | Combined Sewer Overflow | INUSE
16589 | ROYAL WOOTTON BASSETT | NEAR STW | N | Combined Sewer Overflow | INUSE
16590 | CALNE | RIVER MARDEN (RIVER BANK) SOUTH MARDEN HOUSE NEW ROAD | N | Combined Sewer Overflow | INUSE
16592 | ROYAL WOOTTON BASSETT | NEW ROAD | N | Combined Sewer Overflow | INUSE
16594 | MALMESBURY | PARK ROAD | N | Combined Sewer Overflow | INUSE
16596 | CALNE | QUEMERFORD BRIDGE | N | Combined Sewer Overflow | INUSE
16601 | CALNE | STRAND / CHURCH STREET | N | Combined Sewer Overflow | INUSE
16603 | CHIPPENHAM | THE IVY | N | Combined Sewer Overflow | INUSE
16604 | SHERSTON | THE TARTARS | N | Combined Sewer Overflow | INUSE
16605 | BOX | VALENS TERRACE | N | Combined Sewer Overflow | INUSE
16606 | CHIPPENHAM | WOOD LANE | N | Combined Sewer Overflow | INUSE
16608 | MALMESBURY | PARLIAMENT ROW | N | Combined Sewer Overflow | INUSE
16609 | CALNE | MOSSES MILL 1 | N | Combined Sewer Overflow | INUSE
16611 | CALNE | MARKET HILL / STRAND | N | Combined Sewer Overflow | INUSE
16613 | POOLE | STANLEY GREEN ROAD | S | Combined Sewer Overflow | INUSE
16614 | POOLE | WIMBORNE ROAD FOUL SEWER BUSHELL ROAD | S | Combined Sewer Overflow | INUSE
16615 | POOLE | SANDBANKS RD R/O NO 344 EVENING HILL (ELGIN RD O/F 2) | S | Combined Sewer Overflow | INUSE
16617 | POOLE | DELPH GARDENS SPS | S | Combined Sewer Overflow | INUSE
16627 | SWANAGE | THE SQUARE | S | Combined Sewer Overflow | INUSE
16632 | WAREHAM | ABBOTTS QUAY | S | Combined Sewer Overflow | INUSE
16633 | WAREHAM | GRANARY PRIVATE | S | Combined Sewer Overflow | INUSE
16640 | WOOL | STATION ROAD IN GRASS VERGE | S | Combined Sewer Overflow | INUSE
16641 | SALISBURY | CHURCHILL GARDENS NEAR COLLEGE | S | Combined Sewer Overflow | INUSE
16643 | SALISBURY | ENDLESS LANE/SCOTS LANE | S | Combined Sewer Overflow | INUSE
16646 | SALISBURY | BRIDGE STREET/HIGH STREET | S | Combined Sewer Overflow | INUSE
16647 | SALISBURY | COLLEGE STREET NO 28 | S | Combined Sewer Overflow | INUSE
16651 | MERE | STW ADJ TO | S | Combined Sewer Overflow | INUSE
16652 | MERE | SHAFTESBURY ROAD | S | Combined Sewer Overflow | INUSE
16653 | MERE | GARAGE ADJ TO | S | Combined Sewer Overflow | INUSE
16654 | MERE | WHITE ROAD | S | Combined Sewer Overflow | INUSE
16655 | TISBURY | NADDER CLOSE PLAYING FIELDS | S | Combined Sewer Overflow | INUSE
16657 | MAIDEN BRADLEY | STW ADJ TO | S | Combined Sewer Overflow | INUSE
16662 | CANNINGTON | MARSH LANE | W | Combined Sewer Overflow | INUSE
16664 | CHEDDAR | HELLIER LANE / LOWER NEW ROAD | W | Combined Sewer Overflow | INUSE
16665 | WESTONZOYLAND | BROADSTONE | W | Combined Sewer Overflow | INUSE
16666 | COSSINGTON | BROOKHAYES | W | Combined Sewer Overflow | INUSE
16670 | CASTLE CARY | TORBAY ROAD | W | Combined Sewer Overflow | INUSE
16671 | CREWKERNE | HENHAYES | W | Combined Sewer Overflow | INUSE
16673 | ILMINSTER | BREWERY LANE | W | Combined Sewer Overflow | INUSE
16674 | ILMINSTER | STATION ROAD NO 37 | W | Combined Sewer Overflow | INUSE
16677 | STOKE SUB HAMDON | WINDSOR LANE | W | Combined Sewer Overflow | INUSE
16679 | STOKE SUB HAMDON | NORTH STREET O/S NO 50 | W | Combined Sewer Overflow | INUSE
16680 | MARTOCK | CHURCH HOUSE WATER STREET | W | Combined Sewer Overflow | INUSE
16681 | MARTOCK | HURST NO 22 | W | Combined Sewer Overflow | INUSE
16684 | YEOVIL | COOPERS MILL HENDFORD | W | Combined Sewer Overflow | INUSE
16685 | YEOVIL | GOLDCROFT | W | Combined Sewer Overflow | INUSE
16689 | YEOVIL | WYNDHAM HILL | W | Combined Sewer Overflow | INUSE
16690 | YEOVIL | PRESTON GROVE O/S 2 | W | Combined Sewer Overflow | INUSE
16691 | YEOVIL | HORSEY LANE | W | Combined Sewer Overflow | INUSE
16692 | ALLER | . | W | Combined Sewer Overflow | INUSE
16693 | LONG SUTTON | BACK STREET | W | Combined Sewer Overflow | INUSE
16697 | EAST COKER | MOOR LANE | W | Combined Sewer Overflow | INUSE
16705 | NORTH PERROTT | OLD STW SITE | W | Combined Sewer Overflow | INUSE
16707 | QUEEN CAMEL | MILDMAY PLACE IN THE REAR GARDEN OF MILDMAY ORCHARD | W | Combined Sewer Overflow | INUSE
16708 | TEMPLECOMBE | ROYAL HOTEL | W | Combined Sewer Overflow | INUSE
16709 | LANGPORT | SOMERTON ROAD | W | Combined Sewer Overflow | INUSE
16710 | STOKE SUB HAMDON | QUEENS CRESCENT R/O (OS 5300) | W | Combined Sewer Overflow | INUSE
16711 | UPTON | UPTON BRIDGE COTTAGE O/S | W | Combined Sewer Overflow | INUSE
16716 | WINCANTON | BENNET FIELD | W | Combined Sewer Overflow | INUSE
16717 | WINCANTON | MOOR LANE | W | Combined Sewer Overflow | INUSE
16720 | CURRY RIVEL | CURRY RIVEL STORM O/F | W | Combined Sewer Overflow | INUSE
16722 | WOTTON-UNDER-EDGE | BRICKFIELDS | N | Combined Sewer Overflow | INUSE
16723 | WOTTON-UNDER-EDGE | HACK MILL | N | Combined Sewer Overflow | INUSE
16725 | WOTTON-UNDER-EDGE | WATER LANE | N | Combined Sewer Overflow | INUSE
16726 | WOTTON-UNDER-EDGE | OLD COACH YARD | N | Combined Sewer Overflow | INUSE
16730 | TRULL | EASTBROOK ROAD | W | Combined Sewer Overflow | INUSE
16731 | TAUNTON | GOOSENFORD | W | Combined Sewer Overflow | INUSE
16733 | TAUNTON | MILL LANE CORFE NO 2 | W | Combined Sewer Overflow | INUSE
16738 | WELLINGTON | RELYON FACTORY ENTRANCE | W | Combined Sewer Overflow | INUSE
16744 | CHEDDON FITZPAINE | MAIDENBROOK LANE | W | Combined Sewer Overflow | INUSE
16746 | MILVERTON | HOUNDSMOOR LANE | W | Combined Sewer Overflow | INUSE
16748 | HATCH BEAUCHAMP | PALMERS GREEN | W | Combined Sewer Overflow | INUSE
16749 | NORTH CURRY | QUEENS SQUARE | W | Combined Sewer Overflow | INUSE
16750 | NORTH CURRY | WINDMILL HILL | W | Combined Sewer Overflow | INUSE
16753 | BATHEASTON | COALPIT ROAD JUNCTION WITH LONDON ROAD | N | Combined Sewer Overflow | INUSE
16755 | BATHAMPTON | M H K | N | Combined Sewer Overflow | INUSE
16757 | BATHEASTON | MILL HOUSE | N | Combined Sewer Overflow | INUSE
16758 | BATHAMPTON | MILL LANE | N | Combined Sewer Overflow | INUSE
16759 | BATHFORD | OSTLING LANE | N | Combined Sewer Overflow | INUSE
16760 | SALTFORD | O/S 46 HIGH STREET | N | Combined Sewer Overflow | INUSE
16761 | SALTFORD | WICKHOUSE FARM BATH ROAD | N | Combined Sewer Overflow | INUSE
16762 | SALTFORD | SALTFORD HILL | N | Combined Sewer Overflow | INUSE
16763 | KEYNSHAM | ST LADOC / BRISTOL ROAD | N | Combined Sewer Overflow | INUSE
16765 | RADSTOCK | WATERSIDE SO | N | Combined Sewer Overflow | INUSE
16766 | RADSTOCK | WATERLOO ROAD SO (DOWNSTREAM) | N | Combined Sewer Overflow | INUSE
16768 | MIDSOMER NORTON | BERKELEY AVENUE SO | N | Combined Sewer Overflow | INUSE
16769 | RADSTOCK | KILMERSDON ROAD SYPHON EO | N | Combined Sewer Overflow | INUSE
16770 | CAMERTON | BRIDGE PLACE ROAD MH D19 | N | Combined Sewer Overflow | INUSE
16772 | BATHEASTON | BATHEASTON GARDEN | N | Combined Sewer Overflow | INUSE
16773 | MIDSOMER NORTON | WELTON SO | N | Combined Sewer Overflow | INUSE
16774 | MIDSOMER NORTON | STORM RETENTION TANK (OLD STW) | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
16778 | RADSTOCK | SOMERVALE ROAD REAR KHANDALLA WELTON ROAD | N | Combined Sewer Overflow | INUSE
16779 | STON EASTON | HOME FARM SO | W | Combined Sewer Overflow | INUSE
16782 | CLUTTON | MAYPOLE FARM | N | Combined Sewer Overflow | INUSE
16784 | KEYNSHAM | CHARLTON ROAD O/S 138 | N | Combined Sewer Overflow | INUSE
16786 | PAULTON | PAULTON WORKS OFF BRISTOL ROAD | N | Combined Sewer Overflow | INUSE
16788 | MIDFORD | ADJ ABANDONED RAILWAY | N | Combined Sewer Overflow | INUSE
16789 | MONKTON COMBE | SUMMER LANE | N | Combined Sewer Overflow | INUSE
16790 | MONKTON COMBE | MILL LANE | N | Combined Sewer Overflow | INUSE
16793 | FORDINGTON | HIGH STREET NO 16 | S | Combined Sewer Overflow | INUSE
16794 | FORDINGTON | HIGH STREET NO 97 | S | Combined Sewer Overflow | INUSE
16795 | DORCHESTER | KINGS ROAD NO 35 | S | Combined Sewer Overflow | INUSE
16798 | DORCHESTER | PRINCES BRIDGE | S | Combined Sewer Overflow | INUSE
16799 | DORCHESTER | LITTLE BRITTAIN ADJ SCOUT HUT | S | Combined Sewer Overflow | INUSE
16800 | DORCHESTER | SOUTH WALKS / SOUTH STREET | S | Combined Sewer Overflow | INUSE
16802 | DORCHESTER | VICTORIA ROAD / DAMERS ROAD | S | Combined Sewer Overflow | INUSE
16803 | SHERBORNE | ABBEY ROAD | S | Combined Sewer Overflow | INUSE
16804 | SHERBORNE | CHEAP STREET | S | Combined Sewer Overflow | INUSE
16805 | SHERBORNE | WESTBURY OPP DALWOODS | S | Combined Sewer Overflow | INUSE
16806 | SHERBORNE | LONG STREET OUTSIDE THORN BANK | S | Combined Sewer Overflow | INUSE
16807 | SHERBORNE | LUDBORNE ROAD / SOUTH STREET | S | Combined Sewer Overflow | INUSE
16808 | SHERBORNE | NEWLANDS/THE AVENUE | S | Combined Sewer Overflow | INUSE
16810 | SHERBORNE | LONG STREET THE VINES | S | Combined Sewer Overflow | INUSE
16811 | BRIDPORT | EAST BRIDGE | S | Combined Sewer Overflow | INUSE
16813 | BRIDPORT | SOUTH STREET DEPOT | S | Combined Sewer Overflow | INUSE
16815 | BEAMINSTER | HAMS PLOT SOUTH GATE | S | Combined Sewer Overflow | INUSE
16816 | EVERSHOT | COMMON | S | Combined Sewer Overflow | INUSE
16817 | BURTON BRADSTOCK | GROVE ROAD | S | Combined Sewer Overflow | INUSE
16818 | BROADMAYNE | KNIGHTON LANE (PUMPED) | S | Combined Sewer Overflow | INUSE
16819 | CHARMOUTH | THE STREET ADJ BENHARH | S | Combined Sewer Overflow | INUSE
16821 | BRIDPORT | WEST BRIDGE | S | Combined Sewer Overflow | INUSE
16822 | BRIDPORT | WEST STREET | S | Combined Sewer Overflow | INUSE
16825 | CLEVEDON | LADYE BAY SPS | W | Combined Sewer Overflow | INUSE
16827 | CLEVEDON | PARNELL ROAD | W | Combined Sewer Overflow | INUSE
16829 | PILL | AVON ROAD PS | W | Combined Sewer Overflow | INUSE
16831 | PORTISHEAD | HILLSIDE ROAD REDCLIFF BAY | W | Combined Sewer Overflow | INUSE
16835 | CHEW MAGNA | BATTLE LANE | N | Combined Sewer Overflow | INUSE
16838 | PORTISHEAD | PORTBURY DITCH OFF HARBOUR RD | W | Combined Sewer Overflow | INUSE
16839 | WYKE REGIS | DONCASTER ROAD | S | Combined Sewer Overflow | INUSE
16847 | WEYMOUTH | CHICKERELL ROAD BOYS CLUB | S | Combined Sewer Overflow | INUSE
16848 | WEYMOUTH | CHICKERELL ROAD | S | Combined Sewer Overflow | INUSE
16849 | WEYMOUTH | CRANFORD AVENUE | S | Combined Sewer Overflow | INUSE
16852 | WEYMOUTH | GRASMERE ROAD | S | Combined Sewer Overflow | INUSE
16853 | WEYMOUTH | LONGCROFT ROAD / QUEENSLAND ROAD | S | Combined Sewer Overflow | INUSE
16854 | WEYMOUTH | MARLOW ROAD | S | Combined Sewer Overflow | INUSE
16855 | WEYMOUTH | MELCOMBE AVENUE | S | Combined Sewer Overflow | INUSE
16857 | WEYMOUTH | RODWELL AVENUE | S | Combined Sewer Overflow | INUSE
16861 | WEYMOUTH | SPRING LANE | S | Combined Sewer Overflow | INUSE
16862 | WEYMOUTH | ULLSWATER CRESCENT | S | Combined Sewer Overflow | INUSE
16863 | WEYMOUTH | WARDCLIFFE ROAD | S | Combined Sewer Overflow | INUSE
16864 | WEYMOUTH | WESTON ROAD | S | Combined Sewer Overflow | INUSE
16866 | PORTLAND | HIGH STREET | S | Combined Sewer Overflow | INUSE
16867 | PORTLAND | RAILWAY GRAVITY SEWER | S | Combined Sewer Overflow | INUSE
16877 | COWBRIDGE | COWBRIDGE SO | W | Combined Sewer Overflow | INUSE
16879 | HAWKWELL | HAWKWELL SO | W | Combined Sewer Overflow | INUSE
16886 | WATCHET | MILL STREET SO | W | Combined Sewer Overflow | INUSE
16888 | BICKNOLLER | BICKNOLLER SO | W | Combined Sewer Overflow | INUSE
16889 | PORLOCK | PORLOCK SO | W | Combined Sewer Overflow | INUSE
16890 | SAMPFORD BRETT | SAMPFORD BRETT SO | W | Combined Sewer Overflow | INUSE
16891 | STOGUMBER | STOGUMBER SO | W | Combined Sewer Overflow | INUSE
16893 | WILLITON | UNION LANE SO | W | Combined Sewer Overflow | INUSE
16894 | MINEHEAD | BLENHEIM ROAD O/S COASTGUARD COTTAGES | W | Combined Sewer Overflow | INUSE
16895 | MINEHEAD | GREEN SPOT | W | Combined Sewer Overflow | INUSE
16896 | DILTON MARSH | IN FIELD BEHIND 127 HIGH STREET | N | Combined Sewer Overflow | INUSE
16897 | BRADFORD-ON-AVON | CULVER STREET RECREATION PARK OFF POUND | N | Combined Sewer Overflow | INUSE
16898 | BRADFORD-ON-AVON | SPRING FIELD AND WOOLLEY STREET JUNCTION | N | Combined Sewer Overflow | INUSE
16899 | BRADFORD-ON-AVON | MARKET STREET JUNCTION WITH CHURCH STREET | N | Combined Sewer Overflow | INUSE
16900 | TROWBRIDGE | CANAL ROAD | N | Combined Sewer Overflow | INUSE
16901 | WESTBURY | ALFRED ST CONSERVATIVE CLUB | N | Combined Sewer Overflow | INUSE
16902 | WESTBURY | BRIDGE FARM OUTBUILDINGS | N | Combined Sewer Overflow | INUSE
16904 | WESTBURY | WEST END O/S 36 | N | Combined Sewer Overflow | INUSE
16909 | MELKSHAM | SHAW C OF E SCHOOL PLAYING FIELD | N | Combined Sewer Overflow | INUSE
16911 | MELKSHAM | BRADFORD ROAD NEAR UDC DEPOT | N | Combined Sewer Overflow | INUSE
16912 | MELKSHAM | HORNBEAM CRESCENT VERGE | N | Combined Sewer Overflow | INUSE
16914 | WARMINSTER | WEYMOUTH STREET R/O 23 IN PLEASURE GARDENS NEAR SWIMMING POOL | N | Combined Sewer Overflow | INUSE
16916 | MELKSHAM | BATH ROAD OFF ROAD F/O SCOUT HALL | N | Combined Sewer Overflow | INUSE
16920 | BRADFORD-ON-AVON | BARTON FARM TERMINAL P STN | N | Sewage Pumping Station | INUSE
16922 | SAINT ALDHELMS | BARTON BRIDGE BARTON FARM (175M DS) | N | Combined Sewer Overflow | INUSE
16925 | BRADFORD-ON-AVON | MARKET STREET/ SILVER STREET JUNCTION | N | Combined Sewer Overflow | INUSE
16934 | TROWBRIDGE | THE SHIRES MULTI-STOREY CAR PARK/BASEMENT | N | Combined Sewer Overflow | INUSE
16935 | TROWBRIDGE | STALLARD STREET O/S 58 | N | Combined Sewer Overflow | INUSE
16938 | BURNHAM-ON-SEA | ST ANDREWS SCHOOL LOVE LANE | W | Combined Sewer Overflow | INUSE
16940 | POOLE | LEICESTER ROAD / PENN HILL AVENUE JUNCTION | S | Combined Sewer Overflow | INUSE
16944 | CLEEVE | OLD CLEEVE FARM | W | Combined Sewer Overflow | INUSE
16946 | CHIPPENHAM | HIGH STREET OPP 25 | N | Combined Sewer Overflow | INUSE
16947 | CHIPPENHAM | HIGH STREET O/S 6 | N | Combined Sewer Overflow | INUSE
16950 | WINTERBOURNE | HARCOMBE FARM HICKS COMMON IN FIELD | N | Combined Sewer Overflow | INUSE
16955 | YEOVIL | PRESTON GROVE O/S 55 | W | Combined Sewer Overflow | INUSE
16956 | YEOVIL | HENFORD O/S HEALTH CENTRE | W | Combined Sewer Overflow | INUSE
16957 | POOLE | ALDER ROAD OPP 180 | S | Combined Sewer Overflow | INUSE
16999 | CREWKERNE | NORTH OLD STW SITE | W | Combined Sewer Overflow | INUSE
17002 | OLD CLEEVE | BYE FARM NEW SO | W | Combined Sewer Overflow | INUSE
17024 | WAREHAM | NORTH BESTWALL ROAD OIL INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17027 | SOUTH CADBURY | . | W | Sewage Pumping Station | INUSE
17029 | PORTLAND | WESTON STREET NEW | S | Combined Sewer Overflow | INUSE
17030 | WEYMOUTH | ROMAN ROAD NEW | S | Combined Sewer Overflow | INUSE
17031 | LYMPSHAM | RECTORY WAY | W | Sewage Pumping Station | INUSE
17032 | LYMPSHAM | PAVILION | W | Sewage Pumping Station | INUSE
17034 | LYMPSHAM | INNSBRUCK | W | Sewage Pumping Station | INUSE
17035 | LYMPSHAM | HOBBS BOAT | W | Sewage Pumping Station | INUSE
17036 | BRISTOL | BLAISE DELL | N | S105A Sewage Pumping Station | INUSE
17039 | ENMORE | NUMBER ONE | W | Sewage Pumping Station | INUSE
17040 | RINGWOOD | WINDMILL LANE | S | Sewage Pumping Station | INUSE
17041 | RINGWOOD | AVON CASTLE DRIVE | S | Sewage Pumping Station | INUSE
17044 | BRIDPORT | ST ANDREWS TRADING ESTATE | S | Sewage Pumping Station | INUSE
17046 | WEST LULWORTH | LULSTEAD | S | Sewage Pumping Station | INUSE
17047 | WEST LULWORTH | BARN | S | Sewage Pumping Station | INUSE
17058 | WRINGTON | WILTONS | W | Combined Sewer Overflow | INUSE
17060 | EASTER COMPTON | FIRWOOD HOUSE | N | Sewage Pumping Station | INUSE
17077 | CASTLE COMBE | MANOR HOUSE HOTEL | N | Private Sewage Pumping Station | INUSE
17079 | BRIDGWATER | REEDMOOR GARDENS | W | Sewage Pumping Station | INUSE
17082 | BOURNEMOUTH | FORTON CLOSE | S | S105A Sewage Pumping Station | INUSE
17083 | BRISTOL | NEW STATION ROAD | N | Sewage Pumping Station | INUSE
17087 | BRIDPORT | MEADOWLANDS | S | Sewage Pumping Station | INUSE
17088 | THREE LEGGED CROSS | OLD BARN FARM ROAD ATT TANK AND BALANCING POND | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17091 | PILL | EDEN OFFICE PARK HAM GREEN | W | Sewage Pumping Station | INUSE
17093 | LOCKING | WOOLVERS WAY | W | Sewage Pumping Station | INUSE
17098 | WINFRITH NEWBURGH | TECHNOLOGY CENTRE NO.2 | S | Sewage Pumping Station | INUSE
17102 | TAUNTON | SEVERN DRIVE | W | Sewage Pumping Station | INUSE
17103 | SALISBURY | RIVERBOURNE ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17104 | DURLEIGH | SAILING CLUB | W | Sewage Pumping Station | INUSE
17113 | BATH | HAYCOMBE DRIVE NO 223 IN BACK GARDEN | N | Combined Sewer Overflow | INUSE
17114 | VERWOOD | MERRYFIELD CLOSE | S | Sewage Pumping Station | INUSE
17117 | BOURNEMOUTH | KNOLE ROAD O/S NO. 13 | S | Single Property Pumping Station | INUSE
17118 | BOURNEMOUTH | KNOLE ROAD O/S NO. 11 | S | Single Property Pumping Station | INUSE
17119 | BOURNEMOUTH | KNOLE ROAD O/S NO. 9 | S | Single Property Pumping Station | INUSE
17120 | BLANDFORD | WYVERN WAY | S | Sewage Pumping Station | INUSE
17121 | VERWOOD | EBBLAKE CLOSE | S | Sewage Pumping Station | INUSE
17122 | WAYTOWN | SLAPE MILL PARK | S | Sewage Pumping Station | INUSE
17123 | BRISTOL | EASTVILLE PARK FISHPONDS BROOK | N | Combined Sewer Overflow | INUSE
17124 | HIGHER WOODSFORD | PARK DRIVE | S | Sewage Pumping Station | INUSE
17125 | FRAMPTON COTTERELL | MILL LANE | N | Sewage Pumping Station | INUSE
17128 | POOLE | TATNAM ROAD | S | Sewage Pumping Station | INUSE
17129 | BRISTOL | CLANAGE FLOOD RELIEF PSTN | N | Sewage Pumping Station | INUSE
17131 | PLECK | . | S | Sewage Pumping Station | INUSE
17137 | CROSSWAYS | HYBRIS BUSINESS PARK | S | Sewage Pumping Station | INUSE
17140 | BRIDGWATER | EXPRESS PARK | W | Sewage Pumping Station | INUSE
17141 | WAREHAM | STOBOROUGH MEADOWS | S | Sewage Pumping Station | INUSE
17142 | BATH | WINDSOR VILLAS PUMPING STATION | N | Sewage Pumping Station | INUSE
17146 | WINTERBORNE KINGSTON | BROAD CLOSE | S | Private Sewage Pumping Station | INUSE
17150 | WINTERBORNE WHITCHURCH | CHESCOMBE COURT | S | Private Sewage Pumping Station | INUSE
17162 | CHARLTON DOWN | . | S | S105A Sewage Pumping Station | INUSE
17163 | TROWBRIDGE | WEST ASHTON ROAD | N | Sewage Pumping Station | INUSE
17166 | BATH | BEWDLEY ROAD | N | Combined Sewer Overflow | INUSE
17167 | SHAFTESBURY | WINCOMBE LANE | S | Sewage Pumping Station | INUSE
17169 | STURMINSTER NEWTON | FIELD CLOSE | S | Sewage Pumping Station | INUSE
17170 | RINGSTEAD | . | S | Sewage Pumping Station | INUSE
17171 | STOKE GIFFORD | BALANCING POND | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17172 | BATH | BRASSMILL LANE OPP NO 22 | N | Combined Sewer Overflow | INUSE
17174 | GILLINGHAM | BARNABY MEAD | S | Sewage Pumping Station | INUSE
17175 | PURITON | DOWNEND TERRACE | W | Sewage Pumping Station | INUSE
17179 | BRISTOL | CROSSWAYS ROAD GARDEN R/O NO 114 | N | Combined Sewer Overflow | INUSE
17185 | SHEPTON MALLET | SHOWGROUND | W | Sewage Pumping Station | INUSE
17188 | WOOLAVINGTON | REEDS DRIVE | W | Sewage Pumping Station | INUSE
17190 | GUYS MARSH | . | S | Sewage Pumping Station | INUSE
17195 | LOCKING | PINE TREE ROAD | W | Sewage Pumping Station | INUSE
17201 | PORTISHEAD | MASONIC LODGE | W | Sewage Pumping Station | INUSE
17202 | TEMPLE CLOUD | PROSPECT HOUSE | N | Sewage Pumping Station | INUSE
17203 | BRISTOL | BROAD QUAY | N | Sewage Pumping Station | INUSE
17208 | AMESBURY | MAPLE WAY | S | Sewage Pumping Station | INUSE
17209 | PULHAM | DUNTISH VIEW | S | Private Sewage Pumping Station | INUSE
17210 | WINTERBORNE KINGSTON | WARES CLOSE | S | Private Sewage Pumping Station | INUSE
17211 | WINTERBORNE STICKLAND | FAIRMEAD | S | Private Sewage Pumping Station | INUSE
17212 | FORDINGBRIDGE | SALISBURY STREET | S | Combined Sewer Overflow | INUSE
17213 | WESTON-SUPER-MARE | MOOR LANE AREA 22 | W | Sewage Pumping Station | INUSE
17214 | HAZELBURY BRYAN | WOODLANDS | S | Sewage Pumping Station | INUSE
17216 | NETHER STOWEY | STOGURSEY LN | W | Sewage Pumping Station | INUSE
17224 | BRISTOL | IRVING CLOSE SEYMOUR ROAD | N | Combined Sewer Overflow | INUSE
17227 | BOURNEMOUTH | ALUM CHINE | S | Combined Sewer Overflow | INUSE
17232 | PORTISHEAD | MARINA BOATYARD | W | Sewage Pumping Station | INUSE
17233 | PORTISHEAD | MARINA LOCK GATE | W | Sewage Pumping Station | INUSE
17234 | PORTISHEAD | FORTH AVENUE | W | Sewage Pumping Station | INUSE
17235 | PORTISHEAD | MARJORAM WAY | W | Sewage Pumping Station | INUSE
17236 | MAIDEN BRADLEY | DRIVE TO STW | S | Combined Sewer Overflow | INUSE
17237 | BRIDPORT | ST. CECILIA'S GARDENS | S | Sewage Pumping Station | INUSE
17238 | LOCKING | LANEYS DROVE WESTON BUSINESS PARK | W | Private Sewage Pumping Station | INUSE
17239 | LOCKING | SIGNAL SQUARE WESTON BUSINESS PARK | W | Private Sewage Pumping Station | INUSE
17240 | OTTERHAMPTON | DAME WITHYCOMBE VILLAS | W | Sewage Pumping Station | INUSE
17241 | PORTLAND | OSPREY QUAY | S | Sewage Pumping Station | INUSE
17242 | CHARLTON ADAM | WITHY HAYES ROAD | W | S105A Sewage Pumping Station | INUSE
17243 | CHRISTCHURCH | MONKSWELL GREEN | S | Sewage Pumping Station | INUSE
17244 | WEST MOORS | BLACKFIELD FARM | S | Sewage Pumping Station | INUSE
17245 | BLANDFORD | WESTBURY WAY | S | Sewage Pumping Station | INUSE
17246 | GILLINGHAM | LODDEN FARM | S | Sewage Pumping Station | INUSE
17247 | MORETON | QUEENS DRIVE | S | Sewage Pumping Station | INUSE
17249 | TOLPUDDLE | EAST FARM | S | Sewage Pumping Station | INUSE
17250 | POOLE | BROOMHILL WAY | S | Sewage Pumping Station | INUSE
17251 | YATE | THE FOX PH GOOSE GREEN WAY | N | Private Sewage Pumping Station | INUSE
17252 | CHRISTCHURCH | WICK FERRY | S | Sewage Pumping Station | INUSE
17253 | PORTLAND | SAILING ACADEMY | S | Sewage Pumping Station | INUSE
17255 | GILLINGHAM | PARK FARM | S | Sewage Pumping Station | INUSE
17256 | COLLINGBOURNE KINGSTON | MILE END | N | Private Sewage Pumping Station | INUSE
17259 | BURBAGE | HAREPATH FARM | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17263 | BRISTOL | CANONS HOUSE | N | Private Sewage Pumping Station | INUSE
17265 | FORESTERS ARMS | GLOUCESTER ROAD BRISTOL | N | Single Property Pumping Station | INUSE
17266 | HOBGOBLIN | GLOUCESTER ROAD BRISTOL | N | Single Property Pumping Station | INUSE
17267 | PRINCE OF WALES | GLOUCESTER ROAD BRISTOL | N | Single Property Pumping Station | INUSE
17268 | KINGSWOOD | STATION ROAD STORM TANK | N | Sewage Pumping Station | INUSE
17269 | WINCANTON | SPORTS GROUND | W | Sewage Pumping Station | INUSE
17272 | ALDERTON | . | N | Sewage Pumping Station | INUSE
17274 | OLD ROYAL SHIP | LUCKINGTON SINGLE PROPERTY | N | Private Sewage Pumping Station | INUSE
17285 | CROMHALL | CHURCH LANE | N | S105A Sewage Pumping Station | INUSE
17286 | RADSTOCK | WATERLOO ROAD/PINE COURT | N | Combined Sewer Overflow | INUSE
17288 | TRULL | TAUNTON DEAN MOTORWAY SERVICES | W | Private Sewage Pumping Station | INUSE
17289 | CORFE | BARTON GRANGE 1 | W | S105A Sewage Pumping Station | INUSE
17290 | CORFE | BARTON GRANGE 2 | W | S105A Sewage Pumping Station | INUSE
17292 | BRIDGWATER | WEST BOWER FARM | W | Private Sewage Pumping Station | INUSE
17306 | YATE | STATION YARD SURFACE WATER | N | Sewage Pumping Station | INUSE
17313 | COMPTON BASSETT | SPRECKLEY ROAD | N | Single Property Pumping Station | INUSE
17314 | PORTISHEAD | TALLIS HOUSE | W | S105A Sewage Pumping Station | INUSE
17315 | KEYNSHAM | CULVERS CLOSE | N | S105A Sewage Pumping Station | INUSE
17317 | BACKWELL | BACKWELL LAKE BALANCING POND | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17318 | TAUNTON | BRIDGWATER ROAD O/S 75 | W | Combined Sewer Overflow | INUSE
17319 | BREAN | BEACH | W | Sewage Pumping Station | INUSE
17320 | BREAN | DOWN | W | Sewage Pumping Station | INUSE
17322 | SHEPTON MALLET | FORUM LANE | W | Single Property Pumping Station | INUSE
17323 | LOCKING | FIR TREE AVENUE | W | Sewage Pumping Station | INUSE
17324 | WARMLEY | TOWER ROAD NORTH | N | Private Sewage Pumping Station | INUSE
17325 | YATTON | STOWEY ROAD | W | Private Sewage Pumping Station | INUSE
17326 | CONGRESBURY | THE STAR | W | Private Sewage Pumping Station | INUSE
17327 | FLAX BOURTON | POST OFFICE LANE SURFACE WATER | W | Private Sewage Pumping Station | INUSE
17328 | YEOVIL | DODHAM CRESCENT ADJACENT 13 | W | S105A Sewage Pumping Station | INUSE
17329 | BRISTOL | OPPOSITE 83 AIRPORT ROAD | N | Combined Sewer Overflow | INUSE
17330 | BANWELL | PARKHOMES SUMMERLANE | W | Private Sewage Pumping Station | INUSE
17332 | SIDCOT | OAKRIDGE LANE | W | S105A Sewage Pumping Station | INUSE
17336 | HANHAM | ANSTEYS ROAD | N | Combined Sewer Overflow | INUSE
17338 | TAUNTON | MARKET | W | Combined Sewer Overflow | INUSE
17339 | WEST CHINNOCK | FLAXS MILL HOUSE | W | Private Sewage Pumping Station | INUSE
17342 | CHICKERELL | RASHLEY ROAD GARDEN OF NO 19 | S | Combined Sewer Overflow | INUSE
17344 | LYNEHAM | WEBBS COURT | N | Sewage Pumping Station | INUSE
17345 | CLAVERHAM | LOWER CLAVERHAM | W | Sewage Pumping Station | INUSE
17350 | RADSTOCK | WATERLOO ROAD BUILDERS YARD | N | Combined Sewer Overflow | INUSE
17351 | MILBORNE ST ANDREW | WHITE COTTAGE THE GROVE | S | Single Property Pumping Station | INUSE
17352 | POOLE | 144 CANFORD CLIFFS ROAD | S | Single Property Pumping Station | INUSE
17353 | RODE | THE OLD BREWERY | W | Sewage Pumping Station | INUSE
17354 | FROME | COMMERCE PARK | W | Sewage Pumping Station | INUSE
17355 | GREAT CHEVERELL | VICTORIA PARK | N | Private Sewage Pumping Station | INUSE
17356 | BISHOPS LYDEARD | CHURCH STREET | W | Combined Sewer Overflow | INUSE
17357 | HASELBURY PLUCKNETT | PETVINS COURT | W | Sewage Pumping Station | INUSE
17359 | ANSFORD | WAYSIDE FARM | W | Sewage Pumping Station | INUSE
17360 | BREAN | PONTINS SURFACE WATER | W | Sewage Pumping Station | INUSE
17361 | ANSFORD | THE ACERS STATION ROAD | W | Private Sewage Pumping Station | INUSE
17367 | COKERS FROME | . | S | Sewage Pumping Station | INUSE
17368 | POOLE | PINECLIFFE ROAD PUBLIC TOILETS | S | Private Sewage Pumping Station | INUSE
17369 | POOLE | BRANKSOME BEACH RESTAURANT | S | Private Sewage Pumping Station | INUSE
17370 | TAUNTON | WILTON ORCHARD CAR PARK | W | Combined Sewer Overflow | INUSE
17371 | HOLT | SPRINGFIELDS | S | Sewage Pumping Station | INUSE
17372 | HOLT | BUSSONS CORNER | S | Sewage Pumping Station | INUSE
17373 | HOLT | HOLT VALE FARM | S | Sewage Pumping Station | INUSE
17374 | HOLT | MARCH FARM | S | Sewage Pumping Station | INUSE
17378 | STOGURSEY | CHURCH ST NR 5-7 | W | Combined Sewer Overflow | INUSE
17380 | WESTON-SUPER-MARE | LOCKING ROAD JNC BIRCHWOOD AVE | W | Combined Sewer Overflow | INUSE
17383 | TAUNTON | STOKE ROAD O/S 15 | W | Combined Sewer Overflow | INUSE
17384 | BRISTOL | DEVONSHIRE ROAD O/S 75 | N | Combined Sewer Overflow | INUSE
17385 | BRISTOL | LINDEN ROAD JNC HOWARD ROAD | N | Combined Sewer Overflow | INUSE
17386 | BRISTOL | HOLLYGUEST ROAD JNC GREENBANK ROAD | N | Combined Sewer Overflow | INUSE
17388 | BRISTOL | HOLLYGUEST ROAD R/O 21 | N | Combined Sewer Overflow | INUSE
17389 | BRISTOL | HOLLYGUEST ROAD O/S 16 | N | Combined Sewer Overflow | INUSE
17390 | FRESHFORD | FIELDS OFF ROSEMARY LANE | N | Combined Sewer Overflow | INUSE
17391 | WEYMOUTH | RYLANDS LANE TUNNEL | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17392 | RADSTOCK | WALEGRAVE TERRACE OPP 9 | N | Combined Sewer Overflow | INUSE
17394 | WARMINSTER | WEYMOUTH STREET R/O 23 | N | Combined Sewer Overflow | INUSE
17396 | BRIDPORT | WEST BAY ROAD REAR GARDEN OF 13A | S | Combined Sewer Overflow | INUSE
17402 | TAUNTON | MONMOUTH COURT | W | Private Sewage Pumping Station | INUSE
17405 | FERNDOWN | GLADELANDS | S | Sewage Pumping Station | INUSE
17413 | BRADFORD ON TONE | GREYTHORPE | W | Single Property Pumping Station | INUSE
17414 | CALNE | GOATACRE HOUSE | N | Private Sewage Pumping Station | INUSE
17415 | PORLOCK | CARAVAN SITE | W | Sewage Pumping Station | INUSE
17417 | WEST LULWORTH | OLD BOAT HOUSE CAFE | S | Single Property Pumping Station | INUSE
17418 | BRISTOL | THE AVENUE | N | Private Sewage Pumping Station | INUSE
17419 | BRISTOL | THE GARDENS | N | S105A Sewage Pumping Station | INUSE
17422 | LEIGH WOODS | LEIGHWOODS HOUSE CHURCH ROAD | W | S105A Sewage Pumping Station | INUSE
17423 | LEIGH WOODS | ARDMORE VICARAGE ROAD | W | S105A Sewage Pumping Station | INUSE
17424 | OLDBURY | ANCHOR INN | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17428 | MINEHEAD | BUTLINS SOUTHWEST WORLD | W | Private Sewage Pumping Station | INUSE
17431 | CHALBURY | TOWER CLOSE | S | Sewage Pumping Station | INUSE
17435 | WESTON-SUPER-MARE | CASTLE ROAD | W | S105A Sewage Pumping Station | INUSE
17436 | STAVERTON | MARINA STORAGE TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17438 | GAUNTS COMMON | HILL FARM | S | Sewage Pumping Station | INUSE
17439 | GAUNTS COMMON | HORSESHOES | S | Sewage Pumping Station | INUSE
17440 | COMPTON BASSETT | STREET FARM | N | Combined Sewer Overflow | INUSE
17444 | BRENT KNOLL | SANDERS GARDEN CENTRE | W | Private Sewage Pumping Station | INUSE
17445 | BRENT KNOLL | FOX AND GOOSE INN | W | Private Sewage Pumping Station | INUSE
17447 | BRISTOL | CAIRNS ROAD O/S 42 | N | Combined Sewer Overflow | INUSE
17448 | WORLE | QUEENSWAY | W | Private Sewage Pumping Station | INUSE
17449 | WESTON-SUPER-MARE | PADDOCK PARK HOMES | W | Private Sewage Pumping Station | INUSE
17450 | BRISTOL | ELLESMERE ROAD R/O 15 AND 16 | N | Combined Sewer Overflow | INUSE
17454 | BOURTON | BRIDGE | S | Sewage Pumping Station | INUSE
17456 | CHICKERELL | 15 AUSTRALIA ROAD | S | Single Property Pumping Station | INUSE
17462 | LANGPORT | HUISH LEA | W | Sewage Pumping Station | INUSE
17463 | BRIDGWATER | BROADWAY | W | Private Sewage Pumping Station | INUSE
17471 | LUCKINGTON | POLAR GARDENS | N | S105A Sewage Pumping Station | INUSE
17472 | STREET | HOUNDWOOD | W | Sewage Pumping Station | INUSE
17473 | PORTISHEAD | SANDELING PLACE | W | Sewage Pumping Station | INUSE
17474 | POOLE | FLORENCE ROAD PUMPED ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17475 | ORCHESTON | STONEHENGE PARK | S | Sewage Pumping Station | INUSE
17476 | ORCHESTON | . | S | Sewage Pumping Station | INUSE
17479 | CLUTTON | CLUTTON DEPOT | N | Private Sewage Pumping Station | INUSE
17483 | CLEVEDON | NO 2 HIGHDALE ROAD SINGLE PROPERTY | W | Private Sewage Pumping Station | INUSE
17484 | CHICKERELL | PUTTON LANE SURFACE WATER | S | Private Sewage Pumping Station | INUSE
17485 | CHRISTIAN MALFORD | CHURCH ROAD | N | Single Property Pumping Station | INUSE
17487 | WINCANTON | BAYFORD COURT | W | S105A Sewage Pumping Station | INUSE
17488 | CASTLE CARY | CROWN PET FOODS | W | Sewage Pumping Station | INUSE
17489 | LONGHAM | HIGH MEAD LANE | S | Sewage Pumping Station | INUSE
17490 | LONGHAM | HAM LANE | S | Sewage Pumping Station | INUSE
17493 | OLDBURY | OLDBURY HOUSE | N | Private Sewage Pumping Station | INUSE
17495 | GLASTONBURY | PORCH CLOSE | W | S105A Sewage Pumping Station | INUSE
17498 | HUISH EPISCOPI | THE HILL STORM STORAGE TANK (PUMPED) | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17499 | BRISTOL | ALBANY ROAD STORM STORAGE TANK (PUMPED) | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17501 | BRISTOL | CRANBROOK ROAD O/S NO 2 | N | Combined Sewer Overflow | INUSE
17502 | BRISTOL | CRANBROOK ROAD O/S NO 192 | N | Combined Sewer Overflow | INUSE
17504 | STREET | FORD STREAM ROAD | W | Combined Sewer Overflow | INUSE
17510 | BATH | BRASSMILL LANE O/S NO 62 | N | Combined Sewer Overflow | INUSE
17511 | BATH | NEWBRIDGE ROAD R/O NO 131 | N | Combined Sewer Overflow | INUSE
17512 | BATH | LOCKSBROOK ROAD R/O NO 10 | N | Combined Sewer Overflow | INUSE
17513 | BATH | LANSDOWN LANE / HIGH STREET JUNCTION WESTON | N | Combined Sewer Overflow | INUSE
17514 | BATH | SOUTHLANDS RO NO 125 | N | Combined Sewer Overflow | INUSE
17515 | BATH | WESTON VILLAGE SEWER | N | Combined Sewer Overflow | INUSE
17517 | BATH | WINDSOR COURT | N | Combined Sewer Overflow | INUSE
17524 | BATH | LUCKLANDS ROAD O/S LAWN COTTAGE | N | Combined Sewer Overflow | INUSE
17526 | BATH | UPPER BRISTOL ROAD ADJ MARLBOROUGH LANE | N | Combined Sewer Overflow | INUSE
17531 | BATH | GREEN PARK SYPHON INLET RIVER TOWPATH | N | Combined Sewer Overflow | INUSE
17532 | BATH | AVON STREET O/S BATH TECHNICAL COLLEGE | N | Combined Sewer Overflow | INUSE
17533 | BATH | BROAD QUAY / WESTGATE STREET JUNCTION | N | Combined Sewer Overflow | INUSE
17534 | BATH | SOUTHGATE (NORTH END) ADJ LITTLEWOODS | N | Combined Sewer Overflow | INUSE
17536 | BATH | RAILWAY PLACE O/S ROYAL HOTEL | N | Combined Sewer Overflow | INUSE
17537 | BATH | FAIRFIELD AVENUE R/O NO 30 | N | Combined Sewer Overflow | INUSE
17538 | BATH | BAYTREE ROAD ALLOTMENTS R/O NO 28 | N | Combined Sewer Overflow | INUSE
17541 | BATH | LARKHALL TERRACE FIELD TO REAR | N | Combined Sewer Overflow | INUSE
17542 | BATH | CAR PARK ADJ J HUGHES COTTAGE | N | Combined Sewer Overflow | INUSE
17543 | BATH | LAMBRIDGE RUGBY GROUND CARPARK | N | Combined Sewer Overflow | INUSE
17544 | MILBORNE PORT | ANGEL COURT | W | S105A Sewage Pumping Station | INUSE
17545 | HORTON | HORTON MILL | N | Single Property Pumping Station | INUSE
17546 | HORTON | STEVENS COTTAGE | N | Single Property Pumping Station | INUSE
17547 | WESTCOMBE | LANDFILL SITE NEAR SOMERTON | W | Private Sewage Pumping Station | INUSE
17548 | ABBOTS LEIGH | . | W | Sewage Pumping Station | INUSE
17550 | BRIDGEYATE | LONDON ROAD | N | Sewage Pumping Station | INUSE
17551 | CONGRESBURY | WELL PARK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17552 | WESTON-SUPER-MARE | GREENFIELD PLACE O/S 15 | W | Combined Sewer Overflow | INUSE
17553 | CHRISTIAN MALFORD | THE GREEN STREET | N | Sewage Pumping Station | INUSE
17554 | BRISTOL | ALLOTMENT GARDENS REAR OF 186 CRANBROOK ROAD | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17556 | WIMBORNE | COBBS ROAD | S | Sewage Pumping Station | INUSE
17557 | MIDSOMER NORTON | ST CHADS SURGERY GULLOCK TYNING | N | Private Sewage Pumping Station | INUSE
17558 | MIDSOMER NORTON | HALL GULLOCK TYNING | N | Private Sewage Pumping Station | INUSE
17559 | WINTERBOURNE EARLS | BLACK HORSE LANE | S | Single Property Pumping Station | INUSE
17560 | IDMISTON | CHURCH LANE | S | Single Property Pumping Station | INUSE
17561 | WILTON | WYLYE LODGE | S | Single Property Pumping Station | INUSE
17562 | BRIDGWATER | STOCKMOOR VILLAGE | W | Sewage Pumping Station | INUSE
17563 | SALTFORD | MARINA | N | Private Sewage Pumping Station | INUSE
17564 | POOLE | MARSHES END | S | Sewage Pumping Station | INUSE
17568 | CANNINGTON | BLACKMORE LANE | W | Sewage Pumping Station | INUSE
17569 | THROOP | . | S | Sewage Pumping Station | INUSE
17570 | POOLE | BLANDFORD ROAD FIRE STATION HAMWORTHY | S | Single Property Pumping Station | INUSE
17571 | BLANDFORD | GURKHA ROAD | S | Sewage Pumping Station | INUSE
17572 | POUNDBURY | PARKWAY FARM | S | S105A Sewage Pumping Station | INUSE
17573 | WOOL | EAST BURTON ROAD | S | Sewage Pumping Station | INUSE
17574 | POOLE | 101 LILLIPUT ROAD | S | S105A Sewage Pumping Station | INUSE
17577 | BRISTOL | HOWARD RD JNC FALLODON WY/HALSBURY RD | N | Combined Sewer Overflow | INUSE
17582 | BRISTOL | 122 HAMPTON ROAD | N | Private Sewage Pumping Station | INUSE
17583 | BAGLEY | SNAKE LANE | W | Sewage Pumping Station | INUSE
17584 | STOGURSEY | PADDONS FARM | W | Sewage Pumping Station | INUSE
17585 | PYMORE | THREAD MILL LANE | S | Sewage Pumping Station | INUSE
17587 | BRISTOL | 36A DOWNS PARK WEST | N | Single Property Pumping Station | INUSE
17588 | WEST WICK | WOLVERS HILL ROAD | W | Sewage Pumping Station | INUSE
17589 | BATH | DARTMOUTH AVE NR ENTRANCE TO LINEAR PARK | N | Combined Sewer Overflow | INUSE
17590 | WEYMOUTH | BEACH COURT MELCOMBE AVENUE | S | Private Sewage Pumping Station | INUSE
17592 | BRIDGWATER | CASTLEFIELDS SW | W | Private Sewage Pumping Station | INUSE
17597 | TAUNTON | SOMERSET CRICKET CLUB WEST STAND | W | Private Sewage Pumping Station | INUSE
17598 | WESTON-SUPER-MARE | WINDWHISTLE ROAD JNC BRIDGWATER ROAD | W | Combined Sewer Overflow | Standby
17603 | STREET | HOUNDWOOD CLOSE | W | S105A Sewage Pumping Station | INUSE
17604 | HORTON | KINGSBURY COTTAGE | W | Private Sewage Pumping Station | INUSE
17611 | BRISTOL | SOUTH LIBERTY LANE | N | Private Sewage Pumping Station | INUSE
17612 | HULLAVINGTON | ROYAL FIELD CLOSE | N | S105A Sewage Pumping Station | INUSE
17613 | MALMESBURY | COWBRIDGE NEW | N | Sewage Pumping Station | INUSE
17614 | BRISTOL | ST NICHOLAS ROAD STORM STORAGE TANK (PUMPED) | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17620 | MINEHEAD | QUEENS HALL | W | Sewage Pumping Station | INUSE
17625 | CHELSTON | WEST PARK | W | Sewage Pumping Station | INUSE
17627 | HIGHBRIDGE | VARDY COURT | W | Private Sewage Pumping Station | INUSE
17628 | POOLE | BEECHES BROOK | S | Private Sewage Pumping Station | INUSE
17629 | TEMPLECOMBE | BLACKMORE VALE CLOSE | W | S105A Sewage Pumping Station | INUSE
17631 | CLEVEDON | COLEHOUSE FARM CARAVAN PARK | W | Private Sewage Pumping Station | INUSE
17632 | PORTLAND | EASTON SQUARE | S | Sewage Pumping Station | INUSE
17633 | BOURNEMOUTH | QUEENS PARK AVENUE | S | Sewage Pumping Station | INUSE
17634 | MINEHEAD | PARKS LANE NO 11 (PUMPED NRV) | W | Single Property Pumping Station | INUSE
17635 | SHEPTON MALLET | BOWLISH NO 6 (PUMPED NRV) | W | Single Property Pumping Station | INUSE
17636 | CHIPPENHAM | WOODSIDE | N | S105A Sewage Pumping Station | INUSE
17637 | PIDDLETRENTHIDE | ACROSS RIVER FROM RIVENDELL (CSO4) | S | Combined Sewer Overflow | INUSE
17638 | PIDDLETRENTHIDE | R/O TRENT HOUSE (CSO6) | S | Combined Sewer Overflow | INUSE
17646 | HAMBROOK | HOLIDAY INN FILTON ROAD | N | Private Sewage Pumping Station | INUSE
17647 | WARMINSTER | HAYGROVE FARM MEWS | N | S105A Sewage Pumping Station | INUSE
17648 | CALNE | CHURCH VIEW | N | S105A Sewage Pumping Station | INUSE
17649 | BRISTOL | GRANGE COURT ROAD | N | S105A Sewage Pumping Station | INUSE
17650 | TETBURY | O/S 29 SPRINGFIELDS | N | S105A Sewage Pumping Station | INUSE
17651 | NORTON FITZWARREN | GREAT WESTERN WAY NO. 2 | W | Sewage Pumping Station | INUSE
17675 | HIGHBRIDGE | DUNBAR CLOSE | W | S105A Sewage Pumping Station | INUSE
17676 | DOWNEND | FOURACRE CRESCENT | N | S105A Sewage Pumping Station | INUSE
17680 | FERNDOWN | 22 RINGWOOD ROAD | S | Single Property Pumping Station | INUSE
17681 | FERNDOWN | GREENACRES | S | Single Property Pumping Station | INUSE
17682 | FERNDOWN | 165 RINGWOOD ROAD | S | Single Property Pumping Station | INUSE
17683 | WARMINSTER | 70 HIGHBURY PARK SINGLE PROPERTY | N | Private Sewage Pumping Station | INUSE
17684 | WILLSBRIDGE | . | N | Combined Sewer Overflow | INUSE
17685 | CHELSTON | BUSINESS PARK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
17688 | GREAT RIDGEWAY | SWALLETT GATE | N | Combined Sewer Overflow | INUSE
17689 | RINGWOOD | CROW ARCH LANE | S | Private Sewage Pumping Station | INUSE
17691 | CHIPPENHAM | PLANTATION ROAD | N | Private Sewage Pumping Station | INUSE
17692 | BRISTOL | CAVE CLOSE | N | S105A Sewage Pumping Station | INUSE
17698 | TROWBRIDGE | WOODLANDS EDGE | N | S105A Sewage Pumping Station | INUSE
17699 | HANHAM GREEN | ELM TREE PH | N | Private Sewage Pumping Station | INUSE
17700 | NORTH PETHERTON | REGIONAL RURAL BUSINESS CENTRE | W | Private Sewage Pumping Station | INUSE
17701 | PAULTON | BLOOMFIELD RISE FOUL AND SURFACE | N | S105A Sewage Pumping Station | INUSE
17710 | DURRINGTON | AVON LODGE | S | Private Sewage Pumping Station | INUSE
17711 | WINTERBOURNE | LIBRARY FLAXPITS LANE | N | Private Sewage Pumping Station | INUSE
17712 | HURN | HURN COURT LANE | S | S105A Sewage Pumping Station | INUSE
17713 | HIGH LITTLETON | AUMERY GARDENS | N | S105A Sewage Pumping Station | INUSE
17714 | PATCHWAY | GLOUCESTER ROAD | N | Private Sewage Pumping Station | INUSE
17715 | BATH | BAILBROOK LANE | N | Sewage Pumping Station | INUSE
17718 | CHICKERELL | LOWER PUTTON LANE | S | S105A Sewage Pumping Station | INUSE
17719 | FROME | KNIGHTS MALTINGS | W | Sewage Pumping Station | INUSE
17723 | WARMINSTER | VIRGINIA DRIVE | N | S105A Sewage Pumping Station | INUSE
17724 | DEVIZES | QUAKERS WALK | N | Sewage Pumping Station | INUSE
17725 | BATH | WESTON PARK EAST | N | Private Sewage Pumping Station | INUSE
17726 | BATH | HANSFORD MEWS | N | S105A Sewage Pumping Station | INUSE
17727 | WARMINSTER | BOREHAM CLOSE | N | S105A Sewage Pumping Station | INUSE
17728 | BRADFORD-ON-AVON | ST. MARGARETS STREET | N | S105A Sewage Pumping Station | INUSE
17729 | BRADFORD-ON-AVON | REAR OF SWIMMING POOL ST. MARGARETS STREET | N | S105A Sewage Pumping Station | INUSE
17730 | BRADFORD-ON-AVON | HEALTH CENTRE | N | Private Sewage Pumping Station | INUSE
17731 | BRADFORD-ON-AVON | ORCHARD GARDENS | N | S105A Sewage Pumping Station | INUSE
17732 | BURTON BRADSTOCK | MILL STREET | S | S105A Sewage Pumping Station | INUSE
17733 | SEAVINGTON | BAKERS PLACE | S | Private Sewage Pumping Station | INUSE
17734 | MINEHEAD | STEPHENSON ROAD | W | Sewage Pumping Station | INUSE
17735 | LANGFORD | MEDICAL CENTRE FOUL | W | Private Sewage Pumping Station | INUSE
17736 | TAUNTON | CASTLE STREET | W | Private Sewage Pumping Station | INUSE
17737 | WEST HUNTSPILL | SLOWAY LANE 2 | W | Private Sewage Pumping Station | INUSE
17738 | BISHOPS LYDEARD | BRENDONS | W | S105A Sewage Pumping Station | INUSE
17739 | BISHOPS LYDEARD | WEST STREET | W | S105A Sewage Pumping Station | INUSE
17740 | NYNEHEAD | 7 BLACKDOWN VIEW | W | Private Sewage Pumping Station | INUSE
17744 | WESTBURY SUB MENDIP | FARM CLOSE | W | S105A Sewage Pumping Station | INUSE
17746 | NORTON FITZWARREN | STATION ROAD | W | Private Sewage Pumping Station | INUSE
17747 | SHAFTESBURY | SPRINGFIELD HOUSE HIGHER BLANDFORD ROAD | S | S105A Sewage Pumping Station | INUSE
17748 | GILLINGHAM | BARNABY MEAD | S | Private Sewage Pumping Station | INUSE
17749 | BOURTON | SILTON ROAD | S | S105A Sewage Pumping Station | INUSE
17750 | BOURNEMOUTH | COLUMBIA ROAD | S | S105A Sewage Pumping Station | INUSE
17751 | POOLE | SHERWOOD AVENUE 1 | S | Private Sewage Pumping Station | INUSE
17752 | BRIDGWATER | CRANLEIGH GARDENS | W | Private Sewage Pumping Station | INUSE
17753 | POOLE | SHERWOOD AVENUE 2 | S | Private Sewage Pumping Station | INUSE
17754 | POOLE | ARLEY ROAD 1 | S | Private Sewage Pumping Station | INUSE
17755 | POOLE | ARLEY ROAD 2 | S | Private Sewage Pumping Station | INUSE
17756 | REDHILL | HOLIDAY INN | W | Private Sewage Pumping Station | INUSE
17757 | GLASTONBURY | ROMAN WAY | W | Private Sewage Pumping Station | INUSE
17759 | YATE | 55 SOUTH WALK | N | Private Sewage Pumping Station | INUSE
17760 | YATE | 8/22 SOUTH WALK | N | Private Sewage Pumping Station | INUSE
17761 | HIGH LITTLETON | GREYFIELD COMMON | N | S105A Sewage Pumping Station | INUSE
17762 | OSMINGTON MILLS | WEYMOUTH | S | Combined Sewer Overflow | INUSE
17763 | ERLESTOKE | THE PARK | N | S105A Sewage Pumping Station | INUSE
17765 | POOLE | 107 LILLIPUT ROAD | S | Sewage Pumping Station | INUSE
17767 | MONKTON HEATHFIELD | SIDBROOK ORCHARD | W | S105A Sewage Pumping Station | INUSE
17770 | GLASTONBURY | ABBEY MOOR STADIUM | W | Private Sewage Pumping Station | INUSE
17771 | BOWERHILL | MELKSHAM OAK | N | Sewage Pumping Station | INUSE
17773 | BOURNEMOUTH | COLUMBIA GARDENS SURFACE WATER | S | S105A Sewage Pumping Station | INUSE
17774 | WOOKEY | HALES CLOSE | W | S105A Sewage Pumping Station | INUSE
17775 | IDMISTON | HALE BARN COURT | S | Sewage Pumping Station | INUSE
17778 | MONKTON COMBE | DUNDAS WHARF | N | Private Sewage Pumping Station | INUSE
17779 | YATE | BRIMSHAM GREEN SCHOOL FW | N | S105A Sewage Pumping Station | INUSE
17780 | YATE | BRIMSHAM GREEN SCHOOL SW | N | Private Sewage Pumping Station | INUSE
17781 | YATE | 2 X PS WITHIN TECHNICAL SERVICES UNIT S GLOUCESTERSHIRE COUNCIL | N | Private Sewage Pumping Station | INUSE
17786 | LOWER HILL FARM | BATH ROAD BLAGDON | W | Private Sewage Pumping Station | INUSE
17787 | MONTPELIER | BROOK ROAD | N | Private Sewage Pumping Station | INUSE
17788 | HAZELBURY BRYAN | PIDNEY GREEN | S | S105A Sewage Pumping Station | INUSE
17789 | KINGSBURY EPISCOPI | THREADNEEDLE CLOSE | W | S105A Sewage Pumping Station | INUSE
17790 | OAKHILL | ALL SAINTS CHURCH SINGLE PROPERTY | W | Private Sewage Pumping Station | INUSE
17794 | FRAMPTON COTTERELL | BEESMOOR ROAD | N | Sewage Pumping Station | INUSE
17797 | PILNING | TESCO CDC SPS | N | Private Sewage Pumping Station | INUSE
17798 | POOLE | 14 WESTERN ROAD | S | Private Sewage Pumping Station | INUSE
17799 | CHIPPING SODBURY | BOWLING ROAD HIGHWAY DRAINAGE | N | Private Sewage Pumping Station | INUSE
17800 | BATH | KELSTON VIEW O/S 38 | N | Combined Sewer Overflow | INUSE
17801 | MARTOCK | LYNDHURST COAT ROAD | W | S105A Sewage Pumping Station | INUSE
17802 | LONG ASHTON | BIRDWELL SCHOOL | W | Private Sewage Pumping Station | INUSE
17803 | SHERBORNE | HONEYCOMBE LENTHAY ROAD | S | Private Sewage Pumping Station | INUSE
17804 | WIVELISCOMBE | CASE AND SONS ABATTOIR SANDYS MOOR | W | Private Sewage Pumping Station | INUSE
17805 | RODE | CHURCHFIELDS | W | S105A Sewage Pumping Station | INUSE
17806 | GILLINGHAM | HAWTHORN AVENUE | S | S105A Sewage Pumping Station | INUSE
17807 | BURTON | WHITEHAYES ROAD | S | Sewage Pumping Station | INUSE
17808 | STREET | GRANGE AVENUE | W | Private Sewage Pumping Station | INUSE
17809 | THORNBURY | NEW SIBLANDS SCHOOL SINGLE PROPERTY | N | Private Sewage Pumping Station | INUSE
17812 | FOVANT | THE MILL HOUSE | S | Private Sewage Pumping Station | INUSE
17814 | YATE | MAGISTRATES COURT | N | Private Sewage Pumping Station | INUSE
17815 | WINTERBOURNE | ACCADEMY FOUL | N | Private Sewage Pumping Station | INUSE
17816 | WINTERBOURNE | ACCADEMY SURFACE WATER | N | Private Sewage Pumping Station | INUSE
17821 | BRISTOL | LINDEN COURT NO 1 | N | S105A Sewage Pumping Station | INUSE
17822 | BRISTOL | LINDEN COURT NO 2 | N | Private Sewage Pumping Station | INUSE
17824 | BRATTON | MILL LANE | W | S105A Sewage Pumping Station | INUSE
17826 | WELLINGTON | LOWMOOR TRADING ESTATE 2 | W | Private Sewage Pumping Station | INUSE
17828 | ALMONDSBURY | AZTEC WEST SURFACE WATER | N | Private Sewage Pumping Station | INUSE
17829 | ALMONDSBURY | HEMPTON LANE | N | S105A Sewage Pumping Station | INUSE
17832 | FOVANT | THE MILL HOUSE SURFACE WATER | S | Private Sewage Pumping Station | INUSE
17833 | TAUNTON | MILL RISE | W | Sewage Pumping Station | INUSE
17834 | MARTOCK | THE MEADOWS | W | S105A Sewage Pumping Station | INUSE
17835 | WESTBURY-ON-TRYM | WELLESLEY MEWS | N | S105A Sewage Pumping Station | INUSE
17837 | WASHFORD | ST MARYS CHURCH SINGLE PROPERTY | W | Private Sewage Pumping Station | INUSE
17838 | LONGWELL GREEN | 67-73 BATH ROAD | N | Private Sewage Pumping Station | INUSE
17839 | WINTERBOURNE | FLAXPITS LANE | N | Private Sewage Pumping Station | INUSE
17840 | SHAFTESBURY | THE MALTINGS | S | S105A Sewage Pumping Station | INUSE
17842 | WOODFORD | DAMERY LANE | N | Private Sewage Pumping Station | INUSE
17845 | BITTON | BATH ROAD SURFACE WATER | N | Private Sewage Pumping Station | INUSE
17847 | BRISTOL | ALBION DOCKS BOATYARD | N | Private Sewage Pumping Station | INUSE
17849 | FILTON | WEST WAY | N | Private Sewage Pumping Station | INUSE
17851 | PRIORSWOOD | CROWN INDUSTRIAL ESTATE SURFACE WATER | W | Private Sewage Pumping Station | INUSE
17852 | SHEPTON MALLET | JASMINE CLOSE | W | S105A Sewage Pumping Station | INUSE
17853 | GLASTONBURY | THE MOUND SURFACE WATER | W | Private Sewage Pumping Station | INUSE
17854 | MARTOCK | NEWTOWN COAT ROAD | W | Private Sewage Pumping Station | INUSE
17855 | CHEDDAR | LABOURHAM FARM | W | Private Sewage Pumping Station | INUSE
17856 | WEYMOUTH | CUSTOM HOUSE QUAY HIGHWAY DRAINAGE | S | Private Sewage Pumping Station | INUSE
17860 | WIMBORNE | HANHAM ROAD HIGHWAY DRAINAGE | S | Private Sewage Pumping Station | INUSE
17862 | THROOP | GLEBE COTTAGE | S | Private Sewage Pumping Station | INUSE
17864 | AMESBURY | MILLS WAY | S | Sewage Pumping Station | INUSE
17865 | WILTON | SOUTH STREET HIGHWAY DRAINAGE | S | Private Sewage Pumping Station | INUSE
17866 | BOURNEMOUTH | WELLINGTON ROAD HIGHWAY DRAINAGE | S | Private Sewage Pumping Station | INUSE
17867 | WINFRITH NEWBURGH | PROCESS WASTE | S | Private Sewage Pumping Station | INUSE
17868 | WOTTON-UNDER-EDGE | TORTWORTH COURT HOTEL | N | Private Sewage Pumping Station | INUSE
17869 | WEST QUANTOXHEAD | ST. AUDRIES PARK | W | Private Sewage Pumping Station | INUSE
17870 | BOURNEMOUTH | AFC BOURNEMOUTH FOOTBALL STADIUM | S | Private Sewage Pumping Station | INUSE
17871 | BOURNEMOUTH | CARRINGTON HOUSE HOTEL | S | Private Sewage Pumping Station | INUSE
17872 | BOURNEMOUTH | 9 CAMBRIDGE ROAD | S | Private Sewage Pumping Station | INUSE
17873 | BOURNEMOUTH | 89 SOUTHBOURNE ROAD | S | Private Sewage Pumping Station | INUSE
17874 | BOURNEMOUTH | BOSCOMBE LIBRARY AND FLATS | S | Private Sewage Pumping Station | INUSE
17875 | HIGHBRIDGE | MORLAND HALL | W | Private Sewage Pumping Station | INUSE
17876 | BRISTOL | 42 BELVOIR ROAD | N | Private Sewage Pumping Station | INUSE
17878 | WARMINSTER | ATYEO PLACE | N | S105A Sewage Pumping Station | INUSE
17879 | BUSHTON | BUSHTON ESTATES YARD | N | Private Sewage Pumping Station | INUSE
17880 | THORNCOMBE | GRIBB VIEW | W | Private Sewage Pumping Station | INUSE
17881 | YEOVIL | FANCY GARDENS | W | S105A Sewage Pumping Station | INUSE
17882 | HOLT | 46A LEIGH ROAD | N | Private Sewage Pumping Station | INUSE
17883 | SOUTH STOKE | THE OLD COACH HOUSE | N | Private Sewage Pumping Station | INUSE
17884 | TETBURY | LONDON ROAD | N | Private Sewage Pumping Station | INUSE
17885 | VERWOOD | 33 WISTERIA DRIVE | S | S105A Sewage Pumping Station | INUSE
17886 | LEIGH UPON MENDIP | ACORN HOUSE | N | Private Sewage Pumping Station | INUSE
17889 | KEYNSHAM | BROADMEAD LANE | N | Private Sewage Pumping Station | INUSE
17891 | HAM | O/S THE DAIRY | W | Sewage Pumping Station | INUSE
17892 | TIMSBURY | RADFORD HILL | N | Combined Sewer Overflow | INUSE
17902 | HIGHBRIDGE | BASON BRIDGE FACTORY LANE | W | Private Sewage Pumping Station | INUSE
17903 | BAGBOROUGH | HILLVIEW INDUSTRIAL ESTATE | W | Private Sewage Pumping Station | INUSE
17906 | MISTERTON | 1 MILL LANE | W | Private Sewage Pumping Station | INUSE
17907 | MISTERTON | 2 MILL LANE | W | Private Sewage Pumping Station | INUSE
17908 | MISTERTON | 3 MILL LANE | W | Private Sewage Pumping Station | INUSE
17909 | MISTERTON | 4 MILL LANE | W | Private Sewage Pumping Station | INUSE
17910 | NEWTON ST. LOE | BATH SPA UNIVERSITY | N | Private Sewage Pumping Station | INUSE
17918 | MERE | TOWNSEND CLOSE | S | S105A Sewage Pumping Station | INUSE
17920 | CHIPPENHAM | THE TURNPIKE | N | S105A Sewage Pumping Station | INUSE
17921 | BRISTOL | REDWOOD HOUSE | N | Single Property Pumping Station | INUSE
17922 | TAUNTON | GREAT WESTERN WAY NO. 1 | W | Sewage Pumping Station | INUSE
17923 | BURLEY | BURBUSH FARM | S | Private Sewage Pumping Station | INUSE
17924 | URCHFONT | CUCKOO FARM YARD | N | S105A Sewage Pumping Station | INUSE
17926 | POOLE | CIVIC CENTRE | S | Private Sewage Pumping Station | INUSE
17927 | POOLE | CYNTHIA CLOSE | S | Private Sewage Pumping Station | INUSE
17928 | POOLE | TRINIDAD HOUSE | S | Private Sewage Pumping Station | INUSE
17929 | POOLE | SALTERNS MARINA | S | Private Sewage Pumping Station | INUSE
17930 | RODE | 2-3 THE SPORTSMAN | W | S105A Sewage Pumping Station | INUSE
17931 | RODE | 4 THE SPORTSMAN | W | S105A Sewage Pumping Station | INUSE
17932 | POOLE | ROCKLEY POINT BOAT YARD | S | Private Sewage Pumping Station | INUSE
17933 | POOLE | ASDA SINGLE PROPERTY | S | Private Sewage Pumping Station | INUSE
17934 | POOLE | UPTON HOUSE | S | Private Sewage Pumping Station | INUSE
17935 | POOLE | MARINES CAMP | S | Private Sewage Pumping Station | INUSE
17936 | POOLE | ROCKLEY SANDS 1 | S | Private Sewage Pumping Station | INUSE
17937 | POOLE | ROCKLEY SANDS 2 | S | Private Sewage Pumping Station | INUSE
17938 | BOSCOMBE | MARINA CLOSE | S | Private Sewage Pumping Station | INUSE
17939 | CHRISTCHURCH | WATERSIDE | S | S105A Sewage Pumping Station | INUSE
17940 | CHRISTCHURCH | THE MERIDIANS | S | Private Sewage Pumping Station | INUSE
17941 | CHRISTCHURCH | PRIORY QUAY | S | S105A Sewage Pumping Station | INUSE
17942 | WAREHAM | REDCLIFFE CARAVAN PARK | S | Private Sewage Pumping Station | INUSE
17943 | WAREHAM | GRANGE ROAD | S | Private Sewage Pumping Station | INUSE
17945 | POOLE | MINTERN ROAD | S | Private Sewage Pumping Station | INUSE
17946 | POOLE | CRICHEL MOUNT ROAD | S | Sewage Pumping Station | INUSE
17947 | POOLE | HAMWORTHY SSC | S | Private Sewage Pumping Station | INUSE
17948 | POOLE | POOLE ROAD | S | Private Sewage Pumping Station | INUSE
17949 | LYTCHETT MATRAVERS | CHARBOROUGH CLOSE | S | S105A Sewage Pumping Station | INUSE
17950 | POOLE | LAKE PIER | S | Private Sewage Pumping Station | INUSE
17951 | POOLE | CANFORD CLIFFS | S | Private Sewage Pumping Station | INUSE
17952 | POOLE | TESCO SURFACE WATER | S | Private Sewage Pumping Station | INUSE
17953 | POOLE | CREMATORIUM | S | Private Sewage Pumping Station | INUSE
17957 | BOSCOMBE | HONEYCOMBE CHINE | S | Private Sewage Pumping Station | INUSE
17958 | BOURNEMOUTH | ST PETERS ROAD | S | Private Sewage Pumping Station | INUSE
17959 | UPTON | BEACH ROAD | S | Sewage Pumping Station | INUSE
17960 | POOLE | BRANKSOME DENE | S | Private Sewage Pumping Station | INUSE
17961 | POOLE | FOXHOLES ROAD | S | Sewage Pumping Station | INUSE
17963 | HOLTON HEATH | WAREHAM ROAD | S | Private Sewage Pumping Station | INUSE
17964 | YATTON KEYNELL | COOPERS MEADOW | N | S105A Sewage Pumping Station | INUSE
17965 | WAREHAM | MEADOW COTTAGE | S | S105A Sewage Pumping Station | INUSE
17967 | WEYMOUTH | NOTTINGTON LANE | S | S105A Sewage Pumping Station | INUSE
17971 | YEOVIL | GEORGE SMITH WAY | W | S105A Sewage Pumping Station | INUSE
17973 | SOUTHWICK | FROME ROAD | N | S105A Sewage Pumping Station | INUSE
17974 | POOLE | WESSEX GATE RETAIL PARK | S | Private Sewage Pumping Station | INUSE
17975 | LEIGH WOODS | NORTH ROAD | W | Sewage Pumping Station | INUSE
17976 | MINEHEAD | HAYFIELD CLOSE | W | Private Sewage Pumping Station | INUSE
17978 | NAILSEA | BUCKLANDS END | W | Single Property Pumping Station | INUSE
17979 | RINGWOOD | WINDMILL SERVICE STATION | S | Private Sewage Pumping Station | INUSE
17980 | VERWOOD | 25 SPRINGFIELD ROAD | S | Private Sewage Pumping Station | INUSE
17982 | MONKTON COMBE | MILL | N | Sewage Pumping Station | INUSE
17986 | TAUNTON | POPLAR ROAD | W | S105A Sewage Pumping Station | INUSE
17987 | CLUTTON | THE SIDINGS | N | Private Sewage Pumping Station | INUSE
17988 | WARMINSTER | QUEENS CHASE | N | S105A Sewage Pumping Station | INUSE
17990 | ALMONDSBURY | AZTEC WEST | N | S105A Sewage Pumping Station | INUSE
17995 | FRAMPTON COTTERELL | THE MEADS | N | Sewage Pumping Station | INUSE
17997 | WARMINSTER | STATION ROAD SURFACE WATER | N | Private Sewage Pumping Station | INUSE
17999 | WILSTOCK VILLAGE | CLOVER WAY | W | Sewage Pumping Station | INUSE
18000 | BRISTOL | 10 ELGIN PARK | N | Private Sewage Pumping Station | INUSE
18001 | CHRISTCHURCH | AIRFIELD WAY INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18002 | CHRISTCHURCH | ANCHOR CLOSE INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18003 | WEYMOUTH | KWIK FIT CAR PARK INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18004 | SALISBURY | CHURCHFIELDS IND EST OIL INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18005 | CHRISTCHURCH | CONIFER CLOSE OIL INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18012 | CHRISTCHURCH | PRIVATE RARDE OIL INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18015 | BOURNEMOUTH | COOPER DEAN DETENTION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18016 | WIMBORNE | SHEPPARDS FIELD INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18017 | CHRISTCHURCH | STEAMER POINT INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18018 | BOURNEMOUTH | TOWNSEND INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18019 | BRIDGWATER | WILLS ROAD INTERCEPTOR | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18021 | BOURNEMOUTH | ALUMHURST ROAD TANK 1 BETWEEN NO 52 AND WARREN ROAD | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18022 | BOURNEMOUTH | ALUMHURST ROAD TANK 2 BETWEEN MOUNTBATTEN AND EARL ROADS | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18023 | BOSCOMBE | ASHLEY ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18024 | BOURNEMOUTH | BORTHWICK ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18025 | BOURNEMOUTH | BEMISTER ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18026 | SOUTHBOURNE | BEAUFORT SCHOOL TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18027 | BOURNEMOUTH | BELMONT AVENUE TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18028 | BRISTOL | BELOE ROAD TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18029 | BOURNEMOUTH | BENNETT ROAD TANK 1 | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18030 | BOURNEMOUTH | BENNETT ROAD TANK 2 | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18031 | WELLINGTON | BIRCH ROAD TANK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18032 | BOURNEMOUTH | BRADPOLE ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18035 | BRISTOL | BROADWALK 2 | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18036 | BOURNEMOUTH | BROADWAY PARK TANK BOURNEMOUTH | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18038 | BOURNEMOUTH | CASTLE GATE CLOSE TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18039 | BRISTOL | CHAPLIN ROAD | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18040 | BOURNEMOUTH | CHARMINSTER ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18044 | BOSCOMBE | CHRISTCHURCH ROAD ATT TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18045 | SOUTHBOURNE | CHRISTCHURCH ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18048 | BOURNEMOUTH | COURT ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18049 | POOLE | CRANBROOK ROAD | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18051 | POOLE | DOLBERY ROAD NORTH | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18052 | BOURNEMOUTH | EAST WAY TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18053 | BRISTOL | EFFINGHAM ROAD | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18054 | BOURNEMOUTH | ELDON ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18055 | BRISTOL | FALLODON WAY | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18058 | RINGWOOD | FOREST LAKE INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18059 | BRISTOL | GRACE PARK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18061 | DORCHESTER | GROVE TRADING ESTATE | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18062 | BOURNEMOUTH | GROVENOR ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18063 | BOURNEMOUTH | HANKINSON ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18064 | BOURNEMOUTH | HAVERSTOCK ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18065 | RINGWOOD | HEADLANDS BUSINESS PARK INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18066 | BOURNEMOUTH | HERBERT ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18067 | BOURNEMOUTH | HOLDENHURST ROAD LOWER TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18068 | BOURNEMOUTH | HOLDENHURST ROAD UPPER TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18069 | BOURNEMOUTH | HOLDENHURST ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18070 | BRISTOL | HOMELEAZE | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18071 | POOLE | JUNCTION ROAD | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18072 | BOURNEMOUTH | KEEBLE ROAD LOWER TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18073 | BOURNEMOUTH | KEEBLE ROAD UPPER TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18075 | BRISTOL | KNOLE LANE | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18076 | WIVELISCOMBE | LION D'ANGERS TANK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18077 | WEYMOUTH | LODGE WAY TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18078 | BOURNEMOUTH | MALMESBURY PARK ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18079 | BOURNEMOUTH | EVELYN ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18080 | BOURNEMOUTH | MALVERN TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18081 | BOURNEMOUTH | MARLBOROUGH ROAD UPPER TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18082 | BOURNEMOUTH | MARLBOROUGH ROAD LOWER TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18083 | BRISTOL | MARSH LANE | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18084 | BOURNEMOUTH | MCKINLEY ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18085 | POOLE | MIDDLEBERE CRESCENT | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18087 | FORDINGBRIDGE | MULBERRY GARDENS INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18089 | BOSCOMBE | NORTH ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18090 | PEWSEY | BROOMCROFT ROAD | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18091 | SOUTHBOURNE | NORTHEY ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18092 | BOURNEMOUTH | OLD CHRISTCHURCH ROAD SW TUNNEL | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18094 | BOURNEMOUTH | PORTARLINGTON ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18095 | BOURNEMOUTH | PORTLAND ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18097 | WEYMOUTH | PRINCE OF WALES ROAD | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18098 | BRISTOL | PRIORY GARDENS HORFIELD | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18100 | WEYMOUTH | PURBECK CLOSE | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18101 | BOURNEMOUTH | REDHILL DRIVE | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18102 | BOURNEMOUTH | RL STEVENSON AVENUE TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18103 | HAZELBURY BRYAN | HEADLANDS | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18104 | STOKE BISHOP | SHAPLANDS | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18106 | BRIDPORT | SOUTH HOLME | S | S105A Sewage Pumping Station | INUSE
18107 | BOURNEMOUTH | ST MICHAELS ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18108 | HATCH BEAUCHAMP | STATION ROAD TANK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18109 | SOUTHBOURNE | CRANLEIGH ROAD | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18110 | BATHPOOL | SWINGBRIDGE TANK 1 | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18113 | BOURNEMOUTH | TALBOT ROSLIN (SPLIT TANK) | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18114 | BOURNEMOUTH | THE AVENUE TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18115 | DEVIZES | THE TUNNEL | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18117 | BOSCOMBE | VALE ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18118 | BOSCOMBE | VICTORIA GARDENS TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18119 | BOSCOMBE | WESSEX WAY TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18120 | DEVIZES | WICK LANE TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18121 | HATCH BEAUCHAMP | WILCOX FARM TANK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18123 | TAUNTON | WYNDHAM ROAD A TANK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18125 | BEAMINSTER | YARN BARTON INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18132 | NORTH CURRY | PORTMANS GREEN TANK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18140 | BOURNEMOUTH | SANDBOURNE ROAD TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18557 | BOURNEMOUTH | FIVE WAYS BY-PASS TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18704 | WEYMOUTH | KIMMERIDGE CLOSE | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18710 | BRISTOL | ROYAL EDWARD DOCK ST ANDREWS ROAD | N | Sewage Pumping Station | INUSE
18712 | CHAPMANSLADE | WEST | W | Sewage Pumping Station | INUSE
18715 | BUCKHORN WESTON | COURT COTTAGES | S | Sewage Pumping Station | INUSE
18716 | BUCKHORN WESTON | FILLEY BROOK KINGTON MAGNA RD | S | Sewage Pumping Station | INUSE
18718 | CHAPMANSLADE | DIVERS BRIDGE | W | Sewage Pumping Station | INUSE
18725 | ZEALS | TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18726 | LYNEHAM | C SITE (INTERCEPTOR A1) | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18727 | LYNEHAM | C SITE (INTERCEPTOR F1) | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
18728 | LYNEHAM | TECHNICAL SITE (PS 18) | N | Sewage Pumping Station | INUSE
18729 | LYNEHAM | TECHNICAL SITE (INTERCEPTOR Y) | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19030 | BRISTOL | MERLIN CLOSE VORTEX | N | Combined Sewer Overflow | INUSE
19035 | KINGSBURY EPISCOPI | . | W | Sewage Pumping Station | INUSE
19036 | BRISTOL | PENNY WELL ROAD SEMI SYPHONS | N | Sewage Pumping Station | INUSE
19047 | WIVELISCOMBE | NORDENS MEADOWS TAUNTON ROAD | W | Sewage Pumping Station | INUSE
19050 | CAM VALLEY | SPLOT FARM NR PEASEDOWN ST JOHN | N | Combined Sewer Overflow | INUSE
19052 | BOX | BOX RECREATION GROUND (ADJ TO) | N | Combined Sewer Overflow | INUSE
19053 | YEOVIL | ALVINGTON TRIANGLE | W | Sewage Pumping Station | INUSE
19054 | CLEVEDON | PEDDER ROAD | W | Sewage Pumping Station | INUSE
19056 | WEYMOUTH | CASTLE COVE OLD CASTLE ROAD WYKE REGIS | S | Sewage Pumping Station | INUSE
19057 | KINGTON MAGNA | FIVE BRIDGES | S | Sewage Pumping Station | INUSE
19058 | BRISTOL | ROBERTSON DRIVE BRISTOL | N | Sewage Pumping Station | INUSE
19062 | DOWNTON | BATTEN ROAD | S | Sewage Pumping Station | INUSE
19080 | PENSFORD | PENSFORD BRIDGE | N | Sewage Pumping Station | INUSE
19081 | WIMBORNE | CLAPGATE | S | Sewage Pumping Station | INUSE
19082 | WIMBORNE | FURZEHILL | S | Sewage Pumping Station | INUSE
19102 | BRISTOL | BIFIELD ROAD | N | Sewage Pumping Station | INUSE
19103 | YEOVIL | MARSH | W | Sewage Pumping Station | INUSE
19104 | CHILTON TRINITY | SQUARES ROAD | W | Sewage Pumping Station | INUSE
19106 | CONGRESBURY | STATION CLOSE WESTON ROAD | W | Sewage Pumping Station | INUSE
19121 | PORTISHEAD | SLADE ROAD O/S 47 | W | Combined Sewer Overflow | INUSE
19122 | PORTISHEAD | COOMBE/SLADE ROAD JUNCTION | W | Combined Sewer Overflow | INUSE
19123 | PORTISHEAD | BRAMPTON WAY | W | Combined Sewer Overflow | INUSE
19125 | RADSTOCK | CHAPEL LAWNS CLANDOWN | N | Sewage Pumping Station | INUSE
19129 | WESTON-SUPER-MARE | DIAMOND BATCH | W | Sewage Pumping Station | INUSE
19130 | BRISTOL | DALBY AVE | N | Sewage Pumping Station | INUSE
19148 | DEVIZES | HORTON AVE S/W DETENTION POND | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19151 | WEYMOUTH | CHICKERELL/CHAFFEYS ATTENUATION TANK RADIPOLE | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19152 | DEVIZES | CANNINGS LOCK ( LE MARCHANT: BARRACK) | N | Sewage Pumping Station | INUSE
19159 | WICKWAR | AMBERLEY WAY | N | Sewage Pumping Station | INUSE
19162 | BOURNEMOUTH | CIS PENSTOCK HOLDENHURST | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19168 | BISHOPS LYDEARD | RAILWAY STATION | W | Sewage Pumping Station | INUSE
19169 | BRADLEY STOKE | ELLAN HAY ROAD | N | Sewage Pumping Station | INUSE
19171 | FILTON | FILTON AVENUE R/G 699 | N | Combined Sewer Overflow | INUSE
19172 | FILTON | CLEEVE RD MORTUARY | N | Combined Sewer Overflow | INUSE
19173 | STOKE GIFFORD | NEW ROAD ALONG SIDE NO 177 | N | Combined Sewer Overflow | INUSE
19175 | ALDERBURY | FIRS ROAD | S | Sewage Pumping Station | INUSE
19177 | DINTON | TYNDALE MEADOWS | S | Sewage Pumping Station | INUSE
19178 | SOUTH PETHERTON | LAMPREYS LANE | W | Sewage Pumping Station | INUSE
19179 | NORTH PETHERTON | BAYMEAD LANE | W | Sewage Pumping Station | INUSE
19207 | SWANAGE | SHORE ROAD O/S NURSING HOME | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19252 | BRISTOL KINGSWOOD | DOWNLEAZE ROAD R/O 14 | N | Combined Sewer Overflow | INUSE
19254 | POULSHOT | SILLINGTON LANE | N | Sewage Pumping Station | INUSE
19257 | BRIDGWATER | HUNTWORTH BUSINESS PARK | W | Sewage Pumping Station | INUSE
19258 | BRISTOL | BATH ROAD/ FLOWERS HILL | N | Combined Sewer Overflow | INUSE
19260 | BRISTOL | AVONMOUTH WAY/ 1ST WAY | N | Combined Sewer Overflow | INUSE
19266 | BOURNEMOUTH | FISHERMANS WALK CIS | S | Combined Sewer Overflow | INUSE
19271 | MARK | GRANGE PADDOCK | W | Sewage Pumping Station | INUSE
19272 | ALHAMPTON | MAIN | W | Sewage Pumping Station | INUSE
19273 | ALHAMPTON | WAYSIDE COTTAGE | W | Sewage Pumping Station | INUSE
19274 | BRISTOL KINGSWOOD | NEW CHELTENHAM ROAD NEW STORAGE TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19275 | OLVESTON | GREEN FARM OPP LOWER LEAZE | N | Combined Sewer Overflow | INUSE
19276 | TOCKINGTON | MILL LODGE | N | Combined Sewer Overflow | INUSE
19279 | OAKE | SAXON CLOSE | W | Sewage Pumping Station | INUSE
19280 | BRISTOL | HENLEAZE ROAD JUNCTION WITH HENLEAZE PARK DRIVE | N | Combined Sewer Overflow | INUSE
19281 | BRISTOL | HENLEAZE PARK DRIVE JUNCTION OAKWOOD ROAD | N | Combined Sewer Overflow | INUSE
19283 | BALTONSBOROUGH | PERRYS LEAT MILL STREET | W | Sewage Pumping Station | INUSE
19284 | YATE | NIBLEY VILLAGE | N | Sewage Pumping Station | INUSE
19285 | YATE | BRIMSHAM PARK | N | Sewage Pumping Station | INUSE
19286 | LOWER WEARE | SPARROW HILL WAY | W | Sewage Pumping Station | INUSE
19287 | BLANDFORD ST MARY | STOUR PARK | S | Sewage Pumping Station | INUSE
19292 | CHARD | OLD STW BEECHING CL | W | Combined Sewer Overflow | INUSE
19293 | BRISTOL | GLOUCESTER ROAD/CAMBRIDGE ROAD | N | Combined Sewer Overflow | INUSE
19294 | MARTOCK | OAKLAND ROAD | W | Sewage Pumping Station | INUSE
19296 | CLEVEDON | KENN ROAD | W | Sewage Pumping Station | INUSE
19297 | WESTBURY | FROGMORE ROAD OPP 67 | N | Combined Sewer Overflow | INUSE
19299 | COLEFORD | CHURCH LANE | W | Sewage Pumping Station | INUSE
19300 | STAWELL | MOOR LANE | W | Sewage Pumping Station | INUSE
19301 | WESTON-SUPER-MARE | WORLEBURY HILL ROAD | W | Sewage Pumping Station | INUSE
19305 | BISHOPS CANNINGS | OAK CLOSE | N | Sewage Pumping Station | INUSE
19306 | BEER HACKETT | INDUSTRIAL ESTATE | S | Private Sewage Pumping Station | INUSE
19307 | BRISTOL KINGSWOOD | SOUTHEY PLAYING FIELDS (NEW CHELTENHAM ROAD ADJ NO 84) | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19308 | BRISTOL | GLENWOOD ROAD SIDE OF NO 2 WESTBURY ON TRYM | N | Combined Sewer Overflow | INUSE
19403 | COMPTON DUNDON | STREET ROAD | W | Sewage Pumping Station | INUSE
19404 | NAILSEA | PARISH BROOK ROAD (WATERY LANE KINGSHILL PARK) | W | Sewage Pumping Station | INUSE
19405 | VERWOOD | ALBION WAY (THE SYLVANS DEVELOPMENT) | S | Sewage Pumping Station | INUSE
19406 | FRAMPTON COTTERELL | PARK FARM BEESMOOR ROAD | N | Sewage Pumping Station | INUSE
19407 | ALTON BARNES | HONEY STREET | N | Sewage Pumping Station | INUSE
19408 | ALTON BARNES | . | N | Sewage Pumping Station | INUSE
19409 | WINTERBOURNE | FLAXPITS LANE (BURGHLEY COURT) | N | Sewage Pumping Station | INUSE
19453 | WESTON-SUPER-MARE | EBDON GROUNDS | W | Sewage Pumping Station | INUSE
19458 | FAILAND | BEGGAR BUSH LANE (REDWOOD LODGE HOTEL) | W | Sewage Pumping Station | INUSE
19459 | NORTON FITZWARREN | COTFORD ST LUKE NO.2 (TONE VALE INTERSTAGE) | W | Sewage Pumping Station | INUSE
19460 | WELLS | JOCELYN DRIVE | W | Sewage Pumping Station | INUSE
19466 | GLASTONBURY | MANOR HOUSE ROAD O/S TELEPHONE EXCHANGE | W | Combined Sewer Overflow | INUSE
19467 | WOOKEY | AXE ROAD O/S RIVERSIDE COTTAGE | W | Combined Sewer Overflow | INUSE
19468 | WEST PARLEY | ALDRIDGE ROAD | S | Combined Sewer Overflow | INUSE
19471 | YATTON | KENN MOOR ROAD | W | Sewage Pumping Station | INUSE
19487 | COTFORD ST. LUKE | COTFORD ST LUKE NO 1 | W | Sewage Pumping Station | INUSE
19504 | ILMINSTER | CANAL ROAD | W | Sewage Pumping Station | INUSE
19505 | LOCKING | RAF | W | Sewage Pumping Station | INUSE
19506 | SEVERN BEACH | WESTERN APPROACH | N | Sewage Pumping Station | INUSE
19510 | KINGSBURY EPISCOPI | STEMBRIDGE (NEW) | W | Sewage Pumping Station | INUSE
19524 | HENGISTBURY HEAD | ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19525 | ILCHESTER | BLACKTHORNE CLOSE | W | Sewage Pumping Station | INUSE
19529 | POOLE | POOLE PARK ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19530 | BOURNEMOUTH | PIER APPROACH ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19534 | WEYMOUTH | CHICKERELL ROAD O/S ALLOTMENTS NEAR THE ADMIRAL HARDY | S | Combined Sewer Overflow | INUSE
19535 | PORTISHEAD | QUAYS | W | Sewage Pumping Station | INUSE
19536 | NAILSEA | ELM FARM | W | Sewage Pumping Station | INUSE
19537 | PILL | HAM GREEN HOSPITAL NO.1 STATION | W | Sewage Pumping Station | INUSE
19538 | BATH | BATHEASTON BY-PASS | N | Combined Sewer Overflow | INUSE
19542 | AVONMOUTH | CABOT PARK NO.1 | N | Sewage Pumping Station | INUSE
19543 | AVONMOUTH | CABOT PARK NO.2 | N | Sewage Pumping Station | INUSE
19544 | AVONMOUTH | CABOT PARK NO.3 | N | Sewage Pumping Station | INUSE
19553 | BOURNEMOUTH | ASHLEY ROAD JNC WILSON ROAD | S | Combined Sewer Overflow | INUSE
19557 | WEYMOUTH | SPRING ROAD NR JUNC WITH MOUNT STREET | S | Combined Sewer Overflow | INUSE
19558 | CHEDDAR | DRAYCOTT ROAD | W | Sewage Pumping Station | INUSE
19560 | BRISTOL | STATION ROAD R/O 198 CHELTENHAM ROAD (CUTTERS MILLS CULVERT) | N | Combined Sewer Overflow | INUSE
19567 | BRISTOL | CRANBROOK ROAD O/S NO.67 | N | Combined Sewer Overflow | INUSE
19569 | MELKSHAM | FOREST ROAD | N | Sewage Pumping Station | INUSE
19570 | PEASEDOWN ST JOHN | WELLOW ROAD POND | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19571 | CHEDDAR | UNION ST JNC WITH CLIFF ST AND REDCLIFFE ST | W | Combined Sewer Overflow | INUSE
19572 | WIMBORNE | LEIGH ROAD 205 (PUMPED) | S | Combined Sewer Overflow | INUSE
19575 | MUDFORD | TRENT VIEW IN F/G (A359) | W | Combined Sewer Overflow | INUSE
19577 | SOUTH PETHERTON | WEST ST O/S 12 | W | Combined Sewer Overflow | INUSE
19578 | SOMERTON | NEW HILL NR 16 | W | Combined Sewer Overflow | INUSE
19582 | PORTISHEAD | HIGH STREET NR BUILDERS YARD | W | Combined Sewer Overflow | INUSE
19583 | CHILTON POLDEN | GOOSE LANE O/S COLLINGS | W | Combined Sewer Overflow | INUSE
19584 | POOLE | WOODLANDS AVE/HINCHLIFFE ROAD O/F | S | Combined Sewer Overflow | INUSE
19591 | WOOLAVINGTON | CRANCOMBE LANE DETENTION TANK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19592 | ROYAL WOOTTON BASSETT | GREEN PARK WESSEX OWNED SW POND | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19593 | ROYAL WOOTTON BASSETT | WESTBURY PARK LAGOON | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19612 | MILTON ABBAS | MILTON ROAD | S | Sewage Pumping Station | INUSE
19613 | MONTACUTE | NR OLD STW | W | Combined Sewer Overflow | INUSE
19615 | NORTH CURRY | BACKHAM COTTAGES | W | Sewage Pumping Station | INUSE
19629 | CHARLTON MUSGROVE | DIBBENS ROW | W | Sewage Pumping Station | INUSE
19635 | CUCKLINGTON | VALE VIEW | W | Sewage Pumping Station | INUSE
19641 | MUDFORD SOCK | COUNCIL HOUSES SEPTIC TANK | W | Sewage Pumping Station | INUSE
19652 | BEERCROCOMBE | BROADBRIDGE ROAD | W | Sewage Pumping Station | INUSE
19654 | KINGSBURY EPISCOPI | THE AVENUE | W | Sewage Pumping Station | INUSE
19655 | SOMERTON | ETSOME TERRACE | W | Sewage Pumping Station | INUSE
19663 | BLACKFORD | BLACKFORD MOOR LANE | W | Sewage Pumping Station | INUSE
19664 | BLACKFORD | OLD COURT FARM | W | Sewage Pumping Station | INUSE
19670 | BRISTOL | COOMBE BROOK TANK RIDGEWAY PLAYING FIELDS NR VERA ROAD | N | Combined Sewer Overflow | INUSE
19674 | TOCKINGTON | LOWER TOCKINGTON ROAD ADJ TO IVYWELL | N | Combined Sewer Overflow | INUSE
19675 | MUDEFORD | SANDBANK NO.1 | S | Sewage Pumping Station | INUSE
19676 | MUDEFORD | SANDBANK NO.2 | S | Sewage Pumping Station | INUSE
19677 | MUDEFORD | SANDBANK NO.3 | S | Sewage Pumping Station | INUSE
19678 | MUDEFORD | SANDBANK NO.4 | S | Sewage Pumping Station | INUSE
19687 | CROSS | CHARDET CLOSE | W | Sewage Pumping Station | INUSE
19694 | BOURNEMOUTH | HERBERTON ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19695 | BOURNEMOUTH | CLAREMONT AVENUE ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19697 | WATCHET | MARKET ST | W | Combined Sewer Overflow | INUSE
19698 | BRIDGWATER | UCB | W | Sewage Pumping Station | INUSE
19699 | BOVINGTON | LYTCHETT LANE | S | Sewage Pumping Station | INUSE
19700 | BATH | BATHWICK STREET ADJ NO. 31 | N | Combined Sewer Overflow | INUSE
19702 | BATH | WELLSWAY JNC MILTON AVE | N | Combined Sewer Overflow | INUSE
19703 | BATH | WELLSWAY NR 372 | N | Combined Sewer Overflow | INUSE
19704 | BATH | BELLOTTS ROAD | N | Combined Sewer Overflow | INUSE
19706 | KEYNSHAM | WELLSWAY | N | Sewage Pumping Station | INUSE
19708 | BOURNEMOUTH | EAST AVE ATT TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19709 | HILPERTON | CORNBRASH RISE | N | Sewage Pumping Station | INUSE
19710 | AVONMOUTH | GLOUCESTER ROAD | N | Sewage Pumping Station | INUSE
19712 | LITTON | . | W | Sewage Pumping Station | INUSE
19714 | ROYAL WOOTTON BASSETT | TEMPLARS FIRS | N | Sewage Pumping Station | INUSE
19717 | MELKSHAM | SEMINGTON ROAD O/S POLICE STATION | N | Combined Sewer Overflow | INUSE
19719 | WEYMOUTH | PRESTON ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19720 | TISBURY | THE MALLARDS ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19721 | VERWOOD | HAINAULT DRIVE ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19723 | WOOKEY HOLE | GLEN COTTAGE GLENCOTT LANE | W | Combined Sewer Overflow | INUSE
19724 | ALVESTON | COURVILLE CLOSE DETENTION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19725 | KIMMERIDGE | . | S | Sewage Pumping Station | INUSE
19726 | BRISTOL | TRENDLEWOOD PARK | N | S105A Sewage Pumping Station | INUSE
19727 | WEYMOUTH | KNIGHTSDALE ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19728 | THORNBURY | THORNBURY INDUSTRIAL PARK OFF-LINE DETENTION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19731 | HARMANS CROSS | TRANSFER STATION | S | Sewage Pumping Station | INUSE
19768 | STURMINSTER MARSHALL | PARKLEA | S | Sewage Pumping Station | INUSE
19769 | BRISTOL | CLEVE COURT FILTON | N | Combined Sewer Overflow | INUSE
19770 | BRISTOL KINGSWOOD | KINGSHOLME ROAD NO 86 | N | Combined Sewer Overflow | INUSE
19771 | HORTON | QUEENS COPSE (FORMERLY HOLTWOOD) | S | Sewage Pumping Station | INUSE
19772 | HORTON | STEVENS COTTAGE NEW (PUMPED) | N | Combined Sewer Overflow | INUSE
19773 | WEYMOUTH | DOUGLAS ROAD | S | Sewage Pumping Station | INUSE
19776 | WARMWELL | BOURNE LEISURE | S | Sewage Pumping Station | INUSE
19777 | BRISTOL | FOREST ROAD STORM RETENTION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19778 | BRISTOL | FISHPONDS STORM RETENTION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19779 | PORTISHEAD | WOODLANDS ROAD | W | Sewage Pumping Station | INUSE
19780 | BRISTOL | AMENITY LAND OPP NO.63 QUAKERS ROAD | N | Combined Sewer Overflow | INUSE
19781 | LYMPSHAM | BOAT LANE | W | Sewage Pumping Station | INUSE
19782 | BRISTOL | STAPLETON ROAD R/O BLACK SWAN (UNDER FLYOVER) | N | Combined Sewer Overflow | INUSE
19784 | WEYMOUTH | CORONATION CRES 0/S NO.3 | S | Combined Sewer Overflow | INUSE
19785 | BRUTON | TOLBURY MILL ATTENUATION TANK | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19786 | CORSTON | MILL LANE | N | Combined Sewer Overflow | INUSE
19787 | STOUR ROW | . | S | Sewage Pumping Station | INUSE
19789 | CORFE MULLEN | ADMIRALTY SOURCE | S | Sewage Pumping Station | INUSE
19790 | UPTON SCUDAMORE | WTW SPS | N | Sewage Pumping Station | INUSE
19791 | CHILD OKEFORD | BALANCING TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19792 | WEYMOUTH | SPA ROAD/ ROMAN ROAD AND QUEENS ROAD JCT. | S | Combined Sewer Overflow | INUSE
19793 | PILL | ROCK COTTAGES | W | Sewage Pumping Station | INUSE
19794 | FERNDOWN | NIMROD WAY | S | Sewage Pumping Station | INUSE
19816 | BANWELL | ELBOROUGH VILLAGE | W | Sewage Pumping Station | INUSE
19817 | SANDFORD ORCAS | . | S | Sewage Pumping Station | INUSE
19818 | BLAGDON HILL | . | W | Sewage Pumping Station | INUSE
19819 | BLAGDON HILL | HOWLEIGH LANE | W | Sewage Pumping Station | INUSE
19820 | PITMINSTER | QUEENS ARMS | W | Sewage Pumping Station | INUSE
19821 | PITMINSTER | WEIR | W | Sewage Pumping Station | INUSE
19822 | SHAFTESBURY | NEW ROAD/ WOODLANDS LANE | S | Combined Sewer Overflow | INUSE
19823 | LONGHAM | BRIDGE HOUSE | S | Sewage Pumping Station | INUSE
19824 | LONGHAM | GREEN LANE | S | Sewage Pumping Station | INUSE
19825 | TYTHERINGTON | NEW HOUSE FARM DUCK ST | N | Combined Sewer Overflow | INUSE
19827 | ST GEORGES | BRIMBLEWORTH FARM | W | Sewage Pumping Station | INUSE
19828 | PORTISHEAD | PORT MARINE | W | Sewage Pumping Station | INUSE
19829 | ST GEORGES | WILLOW CLOSE | W | Sewage Pumping Station | INUSE
19830 | WORLE | MOOR LANE | W | Sewage Pumping Station | INUSE
19831 | WEST PARLEY | CHINE WALK ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19832 | WEST PARLEY | GALLOWS DRIVE ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19833 | WEST WICK | BUSINESS PARK SURFACE WATER | W | Sewage Pumping Station | INUSE
19834 | STREET | STRAWBERRY HILL | W | Sewage Pumping Station | INUSE
19835 | CHARD | BALANCING POND | W | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19836 | BRIDGWATER | MEADS COURT | W | Sewage Pumping Station | INUSE
19838 | POOLE | WOKING ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19839 | POOLE | RICHMOND ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19840 | POOLE | CYNTHIA ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19841 | POOLE | GOOD ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19842 | POOLE | LANGLEY ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19843 | POOLE | LAYTON ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19844 | POOLE | PARK LAKE ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19845 | POOLE | ROCKLEY ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19846 | POOLE | KENNART ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19847 | POOLE | SANDBANKS PAVILION ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19848 | POOLE | BLANDFORD ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19861 | BURNHAM-ON-SEA | WALLACE WELLS ROAD | W | Sewage Pumping Station | INUSE
19862 | TAUNTON | CROWN IND ESTATE VENTURE WAY | W | Private Sewage Pumping Station | INUSE
19882 | GILLINGHAM | CHURCH VIEW | S | Sewage Pumping Station | INUSE
19883 | MALMESBURY | GLOUCESTER ROAD O/S 109 | N | Combined Sewer Overflow | INUSE
19885 | AVONMOUTH | LOWER HIGH STREET O/S NO. 27 | N | Combined Sewer Overflow | INUSE
19886 | GILLINGHAM | WINDSOR LANE PETROL INTERCEPTOR | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19903 | WICK | THE GREEN | N | Combined Sewer Overflow | INUSE
19904 | WICK | SAINSBURY MILL | N | Combined Sewer Overflow | INUSE
19905 | WINFRITH NEWBURGH | TECHNOLOGY CENTRE 1 | S | Sewage Pumping Station | INUSE
19921 | SHILLINGSTONE | SPENCER GARDENS BALANCING POND | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19924 | VERWOOD | STARLIGHT FARM CLOSE | S | Sewage Pumping Station | INUSE
19925 | WOODFALLS | ELMFIELD CLOSE | S | Sewage Pumping Station | INUSE
19926 | BRISTOL | MANOR WOOD OPEN SPACE RETENTION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19927 | BRISTOL | HEADLEY ROAD ALLOTMENTS RETENTION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19928 | BRISTOL | QUEENS HEAD PUB QUEENS ROAD RETENTION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19932 | HIGHBRIDGE | STATION WALK | W | Sewage Pumping Station | INUSE
19935 | BRADFORD-ON-AVON | GREENLAND MILLS | N | Sewage Pumping Station | INUSE
19936 | BOURNEMOUTH | SHEEPWASH BALANCING POND | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19937 | FERNDOWN | RINGWOOD ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19938 | CHRISTCHURCH | TILBURG ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19939 | CHRISTCHURCH | THE BUTTERY ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19940 | CHRISTCHURCH | HOLME ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19941 | CHRISTCHURCH | CHRISTCHURCH RECREATION GROUND ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19942 | FORDINGBRIDGE | THE OLD VINERIES ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19943 | SALISBURY | BISHOPDOWN BALANCING POND | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19944 | GILLINGHAM | THE OAKS 1 ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19945 | GILLINGHAM | THE OAKS 2 ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19946 | GILLINGHAM | THE OAKS 3 ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19947 | SWANAGE | HERSTON CROSS ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19948 | WARMLEY | POPLAR FARM ESTATE | N | Sewage Pumping Station | INUSE
19949 | WESTBURY | NORTHACRE INDUSTRIAL PARK | N | Sewage Pumping Station | INUSE
19950 | MALMESBURY | PARK ROAD | N | Sewage Pumping Station | INUSE
19951 | CALNE | DALGETY SITE QUEMERFORD | N | Sewage Pumping Station | INUSE
19952 | WESTBURY | THE HAM | N | Sewage Pumping Station | INUSE
19953 | BRISTOL | IMPERIAL GROUNDS BRISLINGTON | N | Sewage Pumping Station | INUSE
19954 | BRISTOL | WORDSWORTH ROAD ATTENUATION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19955 | ST LEONARDS | ROWAN CLOSE NEW | S | Combined Sewer Overflow | INUSE
19956 | BRISTOL | BADMINTON ROAD RETENTION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19957 | PORTISHEAD | CHARLECOMBE PARK | W | Sewage Pumping Station | INUSE
19958 | WEYMOUTH | BUXTON ROAD ATTENUATION TANK | S | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19959 | WIMBORNE | HENBEST CLOSE | S | Sewage Pumping Station | INUSE
19960 | BRISTOL | SHEPPARD ROAD INTERCEPTOR | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19962 | BRISTOL KINGSWOOD | ORCHARD VALE NEW O/S 42 | N | Combined Sewer Overflow | INUSE
19963 | BRISTOL KINGSWOOD | ORCHARD VALE RETENTION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19964 | BRISTOL HANHAM | BRITANNIA ROAD TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19965 | BRISTOL | OAKLEY ROAD / FILTON AVENUE NEW | N | Combined Sewer Overflow | INUSE
19975 | FILTON | STOKE BROOK | N | Combined Sewer Overflow | INUSE
19976 | ROYAL WOOTTON BASSETT | NEW ROAD ATTENUATION TANK | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE
19977 | BRISTOL | MULLER ROAD R/O HORFIELD UNITED REFORM CHURCH | N | Combined Sewer Overflow | INUSE
19978 | ROOKSBRIDGE | BRISTOL ROAD | W | Sewage Pumping Station | INUSE
19984 | WEST LAVINGTON | CHURCHILL ARMS NEW | N | Combined Sewer Overflow | INUSE
19985 | MIDSOMER NORTON | NORTHMEAD ROAD/ HAYES PARK ROAD | N | Combined Sewer Overflow | INUSE
19986 | WEYMOUTH | GREENHILL | S | Sewage Pumping Station | INUSE
19990 | CHILTON TRINITY | WESTERN WAY SURFACE WATER | W | Sewage Pumping Station | INUSE
19991 | BRIDGWATER | HUNTWORTH HOTEL | W | Sewage Pumping Station | INUSE
19992 | NORTH PETHERTON | PARKFIELD CLOSE | W | Sewage Pumping Station | INUSE
19994 | AMESBURY | MARRIED QUARTERS (BOSCOMBE DOWN) | S | Sewage Pumping Station | INUSE
19999 | WARMINSTER | GEORGE ST | N | Sewage Interceptor / Detention Tank / Storm Tanks | INUSE